## INFO
www.res4build.eu
Contact: Dr. George Kosmadakis
|  | E-mail: | gkosmad@ipta.demokritos.gr
Within the RES4BUILD project (H2020, 2019-2023), a pilot building at the National Center for Scientific Research "Demokritos" has been used for testing an innovative energy system for buildings.
The building is a single-floor office building with a surface area of 103 m2 (top view shown in the figure). It has been recently renovated with a 10-cm thermal insulation and double glazing.
Several sensors have been deployed, with representative measurements contained in the current spreadsheet with a time-step of 1 minute.
Two periods are selected of 1-week each, one in October 2022 without the use of any heating appliance, and another in December 2022 when the fan coils providing heating to the building.
There are 4 fan coils in the main rooms of the building, with each one having its own thermostat. All 4 follow the same time-schedule (hours in local time).
1. Day-time: From 08:00 until 21:00, room temperature allowed to fluctuate from 20.5 to 21 oC
2. Night-time: From 21:00 until 08:00, room temperature allowed to fluctuate from 18 to 19 oC
The first 7 days in October include no fan coils operation. The next 7 days in December include fan coils operation according to the above scheduling.
Measurements and units:
OUTDOOR_TEMP | Outdoor (ambient) temperature, in deg. Celsius
INDOOR_TEMP | Indoor temperature of the building, measured in one room near the center of the building, in deg. Celsius
SH_INLET | Inlet temperature to the fan coils from a buffer tank, in deg. Celsius
SH_RETURN | Return temperature from the fan coils, in deg. Celsius
PYRANOMETER | Total solar radiation on a tilted surface (31 deg.) facing south with the sensor placed on the rooftop, in W/m2
FLOW_FAN_COILS_INDOOR | Water flow rate to the fan coils (total), in m3/h
Main purpose: To assist research groups to validate and further develop their building models to predict the heating/cooling loads of buildings
This project has received funding from the European Union’s Horizon 2020 research and innovation programme under Grant Agreement No. 814865 (RES4BUILD). This output reflects only the author’s view. The European Climate, Infrastructure and Environment Executive Agency (CINEA) and the European Commission cannot be held responsible for any use that may be made of the information contained therein.

## 03-10-2022_NO HEAT
| Date&time_x | OUTDOOR_TEMP | INDOOR_TEMP | PYRANOMETER
0 | 2022-10-03 | 20.6 | 25.4 | 0
1 | 2022-10-03 00:01 | 20.2 | 25.3 | 0
2 | 2022-10-03 00:02 | 19.9 | 25.1 | 0
3 | 2022-10-03 00:03 | 19.9 | 24.9 | 0
4 | 2022-10-03 00:04 | 20.1 | 25.1 | 0
5 | 2022-10-03 00:05 | 20 | 25.1 | 0
6 | 2022-10-03 00:06 | 19.7 | 25 | 0
7 | 2022-10-03 00:07 | 19.4 | 24.9 | 0
8 | 2022-10-03 00:08 | 19.5 | 25.4 | 0
9 | 2022-10-03 00:09 | 19.3 | 24.5 | 0
10 | 2022-10-03 00:10 | 19.2 | 25.3 | 0
11 | 2022-10-03 00:11 | 19.8 | 24.7 | 0
12 | 2022-10-03 00:12 | 20.4 | 25.8 | 0
13 | 2022-10-03 00:13 | 21.1 | 24.6 | 0
14 | 2022-10-03 00:14 | 20.8 | 25.3 | 0
15 | 2022-10-03 00:15 | 20.5 | 25.1 | 0
16 | 2022-10-03 00:16 | 21.1 | 25.3 | 0
17 | 2022-10-03 00:17 | 21.3 | 25.1 | 0
18 | 2022-10-03 00:18 | 21.5 | 24.9 | 0
19 | 2022-10-03 00:19 | 21.6 | 25.1 | 0
20 | 2022-10-03 00:20 | 21.7 | 25.2 | 0
21 | 2022-10-03 00:21 | 21.9 | 24.3 | 0
22 | 2022-10-03 00:22 | 21.8 | 25 | 0
23 | 2022-10-03 00:23 | 22.1 | 24.8 | 0
24 | 2022-10-03 00:24 | 22.2 | 25 | 0
25 | 2022-10-03 00:25 | 21.9 | 25.2 | 0
26 | 2022-10-03 00:26 | 21.9 | 24.9 | 0
27 | 2022-10-03 00:27 | 22 | 24.8 | 0
28 | 2022-10-03 00:28 | 21.9 | 25.1 | 0
29 | 2022-10-03 00:29 | 21.8 | 24.9 | 0
30 | 2022-10-03 00:30 | 21.7 | 25.1 | 0
31 | 2022-10-03 00:31 | 21.8 | 24.8 | 0
32 | 2022-10-03 00:32 | 21.8 | 24.9 | 0
33 | 2022-10-03 00:33 | 21.7 | 24.9 | 0
34 | 2022-10-03 00:34 | 21.7 | 25.3 | 0
35 | 2022-10-03 00:35 | 21.7 | 25 | 0
36 | 2022-10-03 00:36 | 21.9 | 25.1 | 0
37 | 2022-10-03 00:37 | 21.6 | 24.8 | 0
38 | 2022-10-03 00:38 | 21.7 | 25.7 | 0
39 | 2022-10-03 00:39 | 21.8 | 25.2 | 0
40 | 2022-10-03 00:40 | 21.9 | 24.8 | 0
41 | 2022-10-03 00:41 | 21.7 | 25.1 | 0
42 | 2022-10-03 00:42 | 21.4 | 25 | 0
43 | 2022-10-03 00:43 | 21.5 | 25 | 0
44 | 2022-10-03 00:44 | 21.5 | 24.9 | 0
45 | 2022-10-03 00:45 | 21.6 | 24.8 | 0
46 | 2022-10-03 00:46 | 21.7 | 25.1 | 0
47 | 2022-10-03 00:47 | 21.8 | 24.6 | 0
48 | 2022-10-03 00:48 | 21.7 | 25.1 | 0
49 | 2022-10-03 00:49 | 21.6 | 25.1 | 0
50 | 2022-10-03 00:50 | 21.6 | 25.1 | 0
51 | 2022-10-03 00:51 | 21.6 | 25.1 | 0
52 | 2022-10-03 00:52 | 21.4 | 25 | 0
53 | 2022-10-03 00:53 | 21.3 | 24.9 | 0
54 | 2022-10-03 00:54 | 21.4 | 25 | 0
55 | 2022-10-03 00:55 | 21.6 | 25.1 | 0
56 | 2022-10-03 00:56 | 21.5 | 25 | 0
57 | 2022-10-03 00:57 | 21.5 | 25 | 0
58 | 2022-10-03 00:58 | 21.5 | 24.9 | 0
59 | 2022-10-03 00:59 | 21.6 | 25.4 | 0
60 | 2022-10-03 01:00 | 21.5 | 25.5 | 0
61 | 2022-10-03 01:01 | 21.4 | 25.2 | 0
62 | 2022-10-03 01:02 | 21.4 | 25 | 0
63 | 2022-10-03 01:03 | 21.5 | 25.1 | 0
64 | 2022-10-03 01:04 | 21.4 | 25.1 | 0
65 | 2022-10-03 01:05 | 21.4 | 25 | 0
66 | 2022-10-03 01:06 | 21.4 | 25 | 0
67 | 2022-10-03 01:07 | 21.2 | 24.9 | 0
68 | 2022-10-03 01:08 | 21.3 | 24.9 | 0
69 | 2022-10-03 01:09 | 21.3 | 24.9 | 0
70 | 2022-10-03 01:10 | 21.3 | 24.7 | 0
71 | 2022-10-03 01:11 | 21.2 | 25.2 | 0
72 | 2022-10-03 01:12 | 21.4 | 25 | 0
73 | 2022-10-03 01:13 | 21.5 | 25.2 | 0
74 | 2022-10-03 01:14 | 21.4 | 25.1 | 0
75 | 2022-10-03 01:15 | 21.1 | 24.3 | 0
76 | 2022-10-03 01:16 | 21 | 24.5 | 0
77 | 2022-10-03 01:17 | 21.1 | 25.1 | 0
78 | 2022-10-03 01:18 | 20.9 | 25.8 | 0
79 | 2022-10-03 01:19 | 20.9 | 24.6 | 0
80 | 2022-10-03 01:20 | 21.1 | 25.7 | 0
81 | 2022-10-03 01:21 | 20.9 | 25.3 | 0
82 | 2022-10-03 01:22 | 20.7 | 24.8 | 0
83 | 2022-10-03 01:23 | 20.8 | 25.2 | 0
84 | 2022-10-03 01:24 | 21.1 | 25.2 | 0
85 | 2022-10-03 01:25 | 21.1 | 24.8 | 0
86 | 2022-10-03 01:26 | 20.6 | 24.9 | 0
87 | 2022-10-03 01:27 | 20.6 | 24.9 | 0
88 | 2022-10-03 01:28 | 21 | 25 | 0
89 | 2022-10-03 01:29 | 20.8 | 24.5 | 0
90 | 2022-10-03 01:30 | 20.9 | 25.3 | 0
91 | 2022-10-03 01:31 | 20.5 | 25.3 | 0
92 | 2022-10-03 01:32 | 20.3 | 24.3 | 0
93 | 2022-10-03 01:33 | 20.1 | 25.7 | 0
94 | 2022-10-03 01:34 | 20.2 | 25.1 | 0
95 | 2022-10-03 01:35 | 20 | 25.4 | 0
96 | 2022-10-03 01:36 | 19.7 | 25.1 | 0
97 | 2022-10-03 01:37 | 19.7 | 24.8 | 0
98 | 2022-10-03 01:38 | 19.3 | 25 | 0
99 | 2022-10-03 01:39 | 19.3 | 25.2 | 0
100 | 2022-10-03 01:40 | 19.3 | 25.2 | 0
101 | 2022-10-03 01:41 | 19 | 25.2 | 0
102 | 2022-10-03 01:42 | 18.8 | 24.4 | 0
103 | 2022-10-03 01:43 | 18.7 | 25.1 | 0
104 | 2022-10-03 01:44 | 18.9 | 24.7 | 0
105 | 2022-10-03 01:45 | 19.1 | 24.7 | 0
106 | 2022-10-03 01:46 | 20.6 | 24.9 | 0
107 | 2022-10-03 01:47 | 20.5 | 25.2 | 0
108 | 2022-10-03 01:48 | 20.6 | 24.8 | 0
109 | 2022-10-03 01:49 | 20.8 | 24.7 | 0
110 | 2022-10-03 01:50 | 20.6 | 24.9 | 0
111 | 2022-10-03 01:51 | 20.3 | 25.5 | 0
112 | 2022-10-03 01:52 | 20.3 | 25.7 | 0
113 | 2022-10-03 01:53 | 19.7 | 25.1 | 0
114 | 2022-10-03 01:54 | 19.3 | 25.2 | 0
115 | 2022-10-03 01:55 | 19 | 25 | 0
116 | 2022-10-03 01:56 | 19 | 24.9 | 0
117 | 2022-10-03 01:57 | 19 | 24.7 | 0
118 | 2022-10-03 01:58 | 19.7 | 25.2 | 0
119 | 2022-10-03 01:59 | 19.9 | 24.9 | 0
120 | 2022-10-03 02:00 | 19.7 | 24.8 | 0
121 | 2022-10-03 02:01 | 19.2 | 24.9 | 0
122 | 2022-10-03 02:02 | 19 | 25 | 0
123 | 2022-10-03 02:03 | 19 | 24.9 | 0
124 | 2022-10-03 02:04 | 19.1 | 25 | 0
125 | 2022-10-03 02:05 | 18.9 | 24.8 | 0
126 | 2022-10-03 02:06 | 18.8 | 24.9 | 0
127 | 2022-10-03 02:07 | 18.9 | 24.7 | 0
128 | 2022-10-03 02:08 | 19.2 | 25.1 | 0
129 | 2022-10-03 02:09 | 19 | 24.8 | 0
130 | 2022-10-03 02:10 | 18.7 | 24 | 0
131 | 2022-10-03 02:11 | 18.6 | 24.4 | 0
132 | 2022-10-03 02:12 | 18.6 | 25 | 0
133 | 2022-10-03 02:13 | 19.5 | 24.6 | 0
134 | 2022-10-03 02:14 | 19.9 | 25.3 | 0
135 | 2022-10-03 02:15 | 19.5 | 24.9 | 0
136 | 2022-10-03 02:16 | 19.7 | 24.9 | 0
137 | 2022-10-03 02:17 | 20.1 | 24.9 | 0
138 | 2022-10-03 02:18 | 21 | 24.8 | 0
139 | 2022-10-03 02:19 | 20 | 25.3 | 0
140 | 2022-10-03 02:20 | 19.8 | 24.8 | 0
141 | 2022-10-03 02:21 | 19.3 | 25.1 | 0
142 | 2022-10-03 02:22 | 20.1 | 25.7 | 0
143 | 2022-10-03 02:23 | 20.1 | 25.6 | 0
144 | 2022-10-03 02:24 | 20.4 | 24.8 | 0
145 | 2022-10-03 02:25 | 20.1 | 25 | 0
146 | 2022-10-03 02:26 | 20.2 | 25 | 0
147 | 2022-10-03 02:27 | 20.4 | 25 | 0
148 | 2022-10-03 02:28 | 20.4 | 24.7 | 0
149 | 2022-10-03 02:29 | 20.3 | 25 | 0
150 | 2022-10-03 02:30 | 20.3 | 25 | 0
151 | 2022-10-03 02:31 | 20.5 | 24.5 | 0
152 | 2022-10-03 02:32 | 20.4 | 24.8 | 0
153 | 2022-10-03 02:33 | 20.6 | 25.3 | 0
154 | 2022-10-03 02:34 | 20.9 | 25.6 | 0
155 | 2022-10-03 02:35 | 21.2 | 24 | 0
156 | 2022-10-03 02:36 | 21 | 24.2 | 0
157 | 2022-10-03 02:37 | 21 | 24.6 | 0
158 | 2022-10-03 02:38 | 20.8 | 24.2 | 0
159 | 2022-10-03 02:39 | 20.6 | 25.5 | 0
160 | 2022-10-03 02:40 | 20.9 | 24.7 | 0
161 | 2022-10-03 02:41 | 21 | 24.6 | 0
162 | 2022-10-03 02:42 | 20.7 | 25 | 0
163 | 2022-10-03 02:43 | 20.8 | 25.1 | 0
164 | 2022-10-03 02:44 | 20.7 | 24.8 | 0
165 | 2022-10-03 02:45 | 20.7 | 24.8 | 0
166 | 2022-10-03 02:46 | 20.9 | 25 | 0
167 | 2022-10-03 02:47 | 20.9 | 24.7 | 0
168 | 2022-10-03 02:48 | 21.1 | 24.8 | 0
169 | 2022-10-03 02:49 | 20.8 | 24.7 | 0
170 | 2022-10-03 02:50 | 20.8 | 24.8 | 0
171 | 2022-10-03 02:51 | 21 | 24.8 | 0
172 | 2022-10-03 02:52 | 20.9 | 24.9 | 0
173 | 2022-10-03 02:53 | 20.8 | 24.8 | 0
174 | 2022-10-03 02:54 | 21.1 | 25.1 | 0
175 | 2022-10-03 02:55 | 20.9 | 24.8 | 0
176 | 2022-10-03 02:56 | 20.8 | 25.2 | 0
177 | 2022-10-03 02:57 | 20.8 | 25.3 | 0
178 | 2022-10-03 02:58 | 20.7 | 24.8 | 0
179 | 2022-10-03 02:59 | 20.8 | 24.6 | 0
180 | 2022-10-03 03:00 | 21 | 24.6 | 0
181 | 2022-10-03 03:01 | 21.3 | 24.8 | 0
182 | 2022-10-03 03:02 | 21.2 | 24.7 | 0
183 | 2022-10-03 03:03 | 21.1 | 24.6 | 0
184 | 2022-10-03 03:04 | 20.9 | 24.8 | 0
185 | 2022-10-03 03:05 | 20.7 | 24.6 | 0
186 | 2022-10-03 03:06 | 20.8 | 24.9 | 0
187 | 2022-10-03 03:07 | 21 | 25 | 0
188 | 2022-10-03 03:08 | 20.8 | 24.9 | 0
189 | 2022-10-03 03:09 | 20.9 | 25 | 0
190 | 2022-10-03 03:10 | 20.8 | 25.5 | 0
191 | 2022-10-03 03:11 | 20.8 | 25 | 0
192 | 2022-10-03 03:12 | 20.8 | 24.8 | 0
193 | 2022-10-03 03:13 | 20.9 | 25.3 | 0
194 | 2022-10-03 03:14 | 20.8 | 24.7 | 0
195 | 2022-10-03 03:15 | 20.9 | 25.5 | 0
196 | 2022-10-03 03:16 | 20.8 | 24.5 | 0
197 | 2022-10-03 03:17 | 20.9 | 24.4 | 0
198 | 2022-10-03 03:18 | 21 | 24.5 | 0
199 | 2022-10-03 03:19 | 21 | 25.6 | 0
200 | 2022-10-03 03:20 | 20.7 | 25.1 | 0
201 | 2022-10-03 03:21 | 20.7 | 25.1 | 0
202 | 2022-10-03 03:22 | 20.7 | 24.9 | 0
203 | 2022-10-03 03:23 | 20.6 | 24.8 | 0
204 | 2022-10-03 03:24 | 20.6 | 24.7 | 0
205 | 2022-10-03 03:25 | 20.2 | 25.2 | 0
206 | 2022-10-03 03:26 | 20.2 | 24.8 | 0
207 | 2022-10-03 03:27 | 20.1 | 24.4 | 0
208 | 2022-10-03 03:28 | 20.1 | 25.1 | 0
209 | 2022-10-03 03:29 | 20 | 24.5 | 0
210 | 2022-10-03 03:30 | 20.1 | 25.2 | 0
211 | 2022-10-03 03:31 | 20.3 | 25.3 | 0
212 | 2022-10-03 03:32 | 20.2 | 24.8 | 0
213 | 2022-10-03 03:33 | 20.1 | 24.9 | 0
214 | 2022-10-03 03:34 | 20.1 | 25 | 0
215 | 2022-10-03 03:35 | 19.9 | 24.6 | 0
216 | 2022-10-03 03:36 | 19.7 | 25.1 | 0
217 | 2022-10-03 03:37 | 19.5 | 24.9 | 0
218 | 2022-10-03 03:38 | 19.5 | 25 | 0
219 | 2022-10-03 03:39 | 19.2 | 24.7 | 0
220 | 2022-10-03 03:40 | 19.3 | 24.7 | 0
221 | 2022-10-03 03:41 | 18.9 | 24.4 | 0
222 | 2022-10-03 03:42 | 19.1 | 24.4 | 0
223 | 2022-10-03 03:43 | 18.7 | 24.4 | 0
224 | 2022-10-03 03:44 | 18.7 | 24.6 | 0
225 | 2022-10-03 03:45 | 18.6 | 24.8 | 0
226 | 2022-10-03 03:46 | 18.6 | 24.8 | 0
227 | 2022-10-03 03:47 | 18.8 | 24.7 | 0
228 | 2022-10-03 03:48 | 19.1 | 24.9 | 0
229 | 2022-10-03 03:49 | 19 | 24.9 | 0
230 | 2022-10-03 03:50 | 18.8 | 24.7 | 0
231 | 2022-10-03 03:51 | 18.7 | 25 | 0
232 | 2022-10-03 03:52 | 18.4 | 24.5 | 0
233 | 2022-10-03 03:53 | 18.4 | 24.7 | 0
234 | 2022-10-03 03:54 | 18.2 | 25 | 0
235 | 2022-10-03 03:55 | 18.2 | 24.9 | 0
236 | 2022-10-03 03:56 | 18.1 | 24.8 | 0
237 | 2022-10-03 03:57 | 18 | 24.9 | 0
238 | 2022-10-03 03:58 | 17.8 | 23.8 | 0
239 | 2022-10-03 03:59 | 17.7 | 23.9 | 0
240 | 2022-10-03 04:00 | 17.8 | 24.8 | 0
241 | 2022-10-03 04:01 | 17.8 | 24.7 | 0
242 | 2022-10-03 04:02 | 17.5 | 24.5 | 0
243 | 2022-10-03 04:03 | 17.4 | 24.6 | 0
244 | 2022-10-03 04:04 | 17.6 | 25 | 0
245 | 2022-10-03 04:05 | 17.5 | 24.6 | 0
246 | 2022-10-03 04:06 | 17.4 | 24.7 | 0
247 | 2022-10-03 04:07 | 17.2 | 24.8 | 0
248 | 2022-10-03 04:08 | 17.3 | 24.5 | 0
249 | 2022-10-03 04:09 | 17.3 | 25.2 | 0
250 | 2022-10-03 04:10 | 17.1 | 24.9 | 0
251 | 2022-10-03 04:11 | 17.2 | 24.4 | 0
252 | 2022-10-03 04:12 | 17 | 24.9 | 0
253 | 2022-10-03 04:13 | 17.1 | 24.5 | 0
254 | 2022-10-03 04:14 | 17.1 | 24.3 | 0
255 | 2022-10-03 04:15 | 17.1 | 24.1 | 0
256 | 2022-10-03 04:16 | 17.1 | 24.9 | 0
257 | 2022-10-03 04:17 | 16.9 | 25.7 | 0
258 | 2022-10-03 04:18 | 16.9 | 25.7 | 0
259 | 2022-10-03 04:19 | 16.8 | 25.3 | 0
260 | 2022-10-03 04:20 | 16.9 | 24.6 | 0
261 | 2022-10-03 04:21 | 17.2 | 24.4 | 0
262 | 2022-10-03 04:22 | 16.9 | 25.2 | 0
263 | 2022-10-03 04:23 | 17.2 | 25 | 0
264 | 2022-10-03 04:24 | 17.4 | 23.8 | 0
265 | 2022-10-03 04:25 | 17.4 | 23.9 | 0
266 | 2022-10-03 04:26 | 17.3 | 24.8 | 0
267 | 2022-10-03 04:27 | 17.2 | 24.6 | 0
268 | 2022-10-03 04:28 | 17.5 | 25.1 | 0
269 | 2022-10-03 04:29 | 17.7 | 25 | 0
270 | 2022-10-03 04:30 | 18.2 | 25.5 | 0
271 | 2022-10-03 04:31 | 18.7 | 25.1 | 0
272 | 2022-10-03 04:32 | 19.1 | 24.3 | 0
273 | 2022-10-03 04:33 | 19.1 | 24.4 | 0
274 | 2022-10-03 04:34 | 18.5 | 24.1 | 0
275 | 2022-10-03 04:35 | 17.8 | 24.1 | 0
276 | 2022-10-03 04:36 | 17.4 | 25.1 | 0
277 | 2022-10-03 04:37 | 17.2 | 24.2 | 0
278 | 2022-10-03 04:38 | 17.1 | 24.7 | 0
279 | 2022-10-03 04:39 | 17 | 24.8 | 0
280 | 2022-10-03 04:40 | 17.2 | 24.7 | 0
281 | 2022-10-03 04:41 | 17.1 | 24.8 | 0
282 | 2022-10-03 04:42 | 17.2 | 24.7 | 0
283 | 2022-10-03 04:43 | 17.2 | 25.4 | 0
284 | 2022-10-03 04:44 | 16.8 | 24.7 | 0
285 | 2022-10-03 04:45 | 16.7 | 24.8 | 0
286 | 2022-10-03 04:46 | 16.7 | 24.4 | 0
287 | 2022-10-03 04:47 | 16.8 | 24.9 | 0
288 | 2022-10-03 04:48 | 16.9 | 23.7 | 0
289 | 2022-10-03 04:49 | 16.7 | 24 | 0
290 | 2022-10-03 04:50 | 16.7 | 24.5 | 0
291 | 2022-10-03 04:51 | 16.6 | 24.1 | 0
292 | 2022-10-03 04:52 | 16.6 | 24.8 | 0
293 | 2022-10-03 04:53 | 16.6 | 24.2 | 0
294 | 2022-10-03 04:54 | 16.5 | 24.6 | 0
295 | 2022-10-03 04:55 | 16.4 | 23.8 | 0
296 | 2022-10-03 04:56 | 16.4 | 25.1 | 0
297 | 2022-10-03 04:57 | 17.4 | 24.5 | 0
298 | 2022-10-03 04:58 | 17.8 | 24.6 | 0
299 | 2022-10-03 04:59 | 17.5 | 24.7 | 0
300 | 2022-10-03 05:00 | 17.5 | 24.7 | 0
301 | 2022-10-03 05:01 | 17.2 | 24.4 | 0
302 | 2022-10-03 05:02 | 16.9 | 23.8 | 0
303 | 2022-10-03 05:03 | 17.9 | 25.3 | 0
304 | 2022-10-03 05:04 | 18.3 | 25.1 | 0
305 | 2022-10-03 05:05 | 18.5 | 24.9 | 0
306 | 2022-10-03 05:06 | 18.4 | 24.1 | 0
307 | 2022-10-03 05:07 | 18.1 | 24.7 | 0
308 | 2022-10-03 05:08 | 17.8 | 24.7 | 0
309 | 2022-10-03 05:09 | 17.5 | 25 | 0
310 | 2022-10-03 05:10 | 17.5 | 24.7 | 0
311 | 2022-10-03 05:11 | 17.6 | 24.6 | 0
312 | 2022-10-03 05:12 | 17.6 | 24.4 | 0
313 | 2022-10-03 05:13 | 17.8 | 25.4 | 0
314 | 2022-10-03 05:14 | 17.7 | 24.1 | 0
315 | 2022-10-03 05:15 | 17.2 | 24.9 | 0
316 | 2022-10-03 05:16 | 17.5 | 24.3 | 0
317 | 2022-10-03 05:17 | 17.6 | 24.4 | 0
318 | 2022-10-03 05:18 | 17.7 | 23.9 | 0
319 | 2022-10-03 05:19 | 17.3 | 24.7 | 0
320 | 2022-10-03 05:20 | 17.1 | 24.6 | 0
321 | 2022-10-03 05:21 | 17 | 24.4 | 0
322 | 2022-10-03 05:22 | 16.9 | 24.5 | 0
323 | 2022-10-03 05:23 | 16.8 | 25.2 | 0
324 | 2022-10-03 05:24 | 16.6 | 24.2 | 0
325 | 2022-10-03 05:25 | 16.5 | 24.2 | 0
326 | 2022-10-03 05:26 | 16.2 | 25.3 | 0
327 | 2022-10-03 05:27 | 16.2 | 25 | 0
328 | 2022-10-03 05:28 | 16.4 | 24.2 | 0
329 | 2022-10-03 05:29 | 16.5 | 24.4 | 0
330 | 2022-10-03 05:30 | 16.7 | 24.6 | 0
331 | 2022-10-03 05:31 | 16.9 | 25.4 | 0
332 | 2022-10-03 05:32 | 17.2 | 25.3 | 0
333 | 2022-10-03 05:33 | 17.4 | 24.6 | 0
334 | 2022-10-03 05:34 | 17.7 | 25.3 | 0
335 | 2022-10-03 05:35 | 18 | 24.6 | 0
336 | 2022-10-03 05:36 | 17.7 | 24.8 | 0
337 | 2022-10-03 05:37 | 18 | 24 | 0
338 | 2022-10-03 05:38 | 18.6 | 24.6 | 0
339 | 2022-10-03 05:39 | 19 | 25.1 | 0
340 | 2022-10-03 05:40 | 19.1 | 25.5 | 0
341 | 2022-10-03 05:41 | 18.8 | 24.7 | 0
342 | 2022-10-03 05:42 | 18.6 | 24.6 | 0
343 | 2022-10-03 05:43 | 18.7 | 24.4 | 0
344 | 2022-10-03 05:44 | 18.8 | 24.9 | 0
345 | 2022-10-03 05:45 | 18.3 | 24.4 | 0
346 | 2022-10-03 05:46 | 17.7 | 24 | 0
347 | 2022-10-03 05:47 | 17.7 | 24.9 | 0
348 | 2022-10-03 05:48 | 17.4 | 24.1 | 0
349 | 2022-10-03 05:49 | 18 | 24.6 | 0
350 | 2022-10-03 05:50 | 17.7 | 24.1 | 0
351 | 2022-10-03 05:51 | 17.8 | 24.3 | 0
352 | 2022-10-03 05:52 | 18 | 24.6 | 0
353 | 2022-10-03 05:53 | 17.9 | 24 | 0
354 | 2022-10-03 05:54 | 18.3 | 24.5 | 0
355 | 2022-10-03 05:55 | 18.4 | 25.4 | 0
356 | 2022-10-03 05:56 | 18.4 | 25.5 | 0
357 | 2022-10-03 05:57 | 18 | 24.5 | 0
358 | 2022-10-03 05:58 | 17.8 | 24.7 | 0
359 | 2022-10-03 05:59 | 17.7 | 24.3 | 0
360 | 2022-10-03 06:00 | 17.4 | 24.9 | 0
361 | 2022-10-03 06:01 | 17.2 | 24.7 | 0
362 | 2022-10-03 06:02 | 17.2 | 24.8 | 0
363 | 2022-10-03 06:03 | 17.1 | 24.6 | 0
364 | 2022-10-03 06:04 | 17.1 | 24.7 | 0
365 | 2022-10-03 06:05 | 17.1 | 24.5 | 0
366 | 2022-10-03 06:06 | 17 | 24.6 | 0
367 | 2022-10-03 06:07 | 16.9 | 24.6 | 0
368 | 2022-10-03 06:08 | 17 | 24.7 | 0
369 | 2022-10-03 06:09 | 17.1 | 24.6 | 0
370 | 2022-10-03 06:10 | 17.1 | 24.5 | 0
371 | 2022-10-03 06:11 | 17.4 | 24.4 | 0
372 | 2022-10-03 06:12 | 17.1 | 24.7 | 0
373 | 2022-10-03 06:13 | 16.8 | 24.6 | 0
374 | 2022-10-03 06:14 | 16.6 | 24.8 | 0
375 | 2022-10-03 06:15 | 16.9 | 24.8 | 0
376 | 2022-10-03 06:16 | 17.3 | 24.1 | 0
377 | 2022-10-03 06:17 | 17.2 | 23.6 | 0
378 | 2022-10-03 06:18 | 17 | 24 | 0
379 | 2022-10-03 06:19 | 16.7 | 24.7 | 0
380 | 2022-10-03 06:20 | 16.5 | 24.6 | 0
381 | 2022-10-03 06:21 | 16.6 | 24.5 | 0
382 | 2022-10-03 06:22 | 16.5 | 25.1 | 0
383 | 2022-10-03 06:23 | 16.3 | 24.4 | 0
384 | 2022-10-03 06:24 | 16.2 | 24.3 | 0
385 | 2022-10-03 06:25 | 16.4 | 24.6 | 0
386 | 2022-10-03 06:26 | 16.3 | 24.8 | 0
387 | 2022-10-03 06:27 | 16.2 | 24.3 | 0
388 | 2022-10-03 06:28 | 16.1 | 24.3 | 0
389 | 2022-10-03 06:29 | 16.2 | 24.9 | 0
390 | 2022-10-03 06:30 | 16.2 | 23.7 | 0
391 | 2022-10-03 06:31 | 16 | 24 | 0
392 | 2022-10-03 06:32 | 16 | 24.6 | 0
393 | 2022-10-03 06:33 | 16 | 24.7 | 0
394 | 2022-10-03 06:34 | 15.9 | 24.8 | 0
395 | 2022-10-03 06:35 | 16 | 24.9 | 0
396 | 2022-10-03 06:36 | 15.8 | 24.4 | 0
397 | 2022-10-03 06:37 | 15.8 | 24.7 | 0
398 | 2022-10-03 06:38 | 15.8 | 24.4 | 0
399 | 2022-10-03 06:39 | 15.8 | 24.6 | 0
400 | 2022-10-03 06:40 | 15.9 | 24.4 | 0
401 | 2022-10-03 06:41 | 16.1 | 24.3 | 0
402 | 2022-10-03 06:42 | 16 | 24.5 | 0
403 | 2022-10-03 06:43 | 16.2 | 24.8 | 0
404 | 2022-10-03 06:44 | 16.6 | 24.7 | 0
405 | 2022-10-03 06:45 | 16.8 | 24.3 | 0
406 | 2022-10-03 06:46 | 16.8 | 24.4 | 0
407 | 2022-10-03 06:47 | 16.7 | 24.4 | 0
408 | 2022-10-03 06:48 | 16.7 | 24.4 | 0
409 | 2022-10-03 06:49 | 16.5 | 23.6 | 0
410 | 2022-10-03 06:50 | 16.5 | 24.6 | 0
411 | 2022-10-03 06:51 | 16.4 | 24.4 | 0
412 | 2022-10-03 06:52 | 16.3 | 24.6 | 0
413 | 2022-10-03 06:53 | 16.5 | 24.2 | 0
414 | 2022-10-03 06:54 | 16.3 | 24.7 | 0
415 | 2022-10-03 06:55 | 16.3 | 24.7 | 0
416 | 2022-10-03 06:56 | 16.3 | 24.3 | 0
417 | 2022-10-03 06:57 | 16.3 | 24.4 | 0
418 | 2022-10-03 06:58 | 16.2 | 25 | 0
419 | 2022-10-03 06:59 | 16 | 24.4 | 0
420 | 2022-10-03 07:00 | 16.1 | 24.4 | 0
421 | 2022-10-03 07:01 | 16.1 | 24.5 | 0
422 | 2022-10-03 07:02 | 16.1 | 24.4 | 0
423 | 2022-10-03 07:03 | 16.1 | 24.5 | 0
424 | 2022-10-03 07:04 | 16 | 24.5 | 0
425 | 2022-10-03 07:05 | 16.1 | 24.6 | 0
426 | 2022-10-03 07:06 | 15.9 | 24.5 | 0
427 | 2022-10-03 07:07 | 16 | 24.6 | 0
428 | 2022-10-03 07:08 | 15.8 | 24.6 | 0
429 | 2022-10-03 07:09 | 15.8 | 24.5 | 0
430 | 2022-10-03 07:10 | 15.8 | 24.5 | 0
431 | 2022-10-03 07:11 | 15.7 | 24.3 | 0
432 | 2022-10-03 07:12 | 15.7 | 24.1 | 0
433 | 2022-10-03 07:13 | 15.6 | 24.4 | 0
434 | 2022-10-03 07:14 | 15.7 | 23.6 | 0
435 | 2022-10-03 07:15 | 15.9 | 24.5 | 0
436 | 2022-10-03 07:16 | 15.7 | 25.1 | 0
437 | 2022-10-03 07:17 | 15.8 | 23.9 | 0
438 | 2022-10-03 07:18 | 15.6 | 23.7 | 0
439 | 2022-10-03 07:19 | 15.4 | 24.7 | 0
440 | 2022-10-03 07:20 | 15.6 | 23.9 | 0
441 | 2022-10-03 07:21 | 15.5 | 24.2 | 1
442 | 2022-10-03 07:22 | 15.6 | 24.3 | 1
443 | 2022-10-03 07:23 | 15.5 | 24.7 | 1
444 | 2022-10-03 07:24 | 15.5 | 24.5 | 2
445 | 2022-10-03 07:25 | 15.2 | 24.5 | 2
446 | 2022-10-03 07:26 | 15.4 | 24.4 | 2
447 | 2022-10-03 07:27 | 15.3 | 24.6 | 3
448 | 2022-10-03 07:28 | 15.4 | 24.4 | 3
449 | 2022-10-03 07:29 | 15.3 | 24.2 | 4
450 | 2022-10-03 07:30 | 16.3 | 24.2 | 4
451 | 2022-10-03 07:31 | 16 | 24.6 | 5
452 | 2022-10-03 07:32 | 15.8 | 24.6 | 6
453 | 2022-10-03 07:33 | 15.7 | 24.2 | 6
454 | 2022-10-03 07:34 | 15.8 | 24.5 | 7
455 | 2022-10-03 07:35 | 16 | 24.2 | 7
456 | 2022-10-03 07:36 | 15.8 | 24.4 | 8
457 | 2022-10-03 07:37 | 16.3 | 24.4 | 9
458 | 2022-10-03 07:38 | 16.4 | 24.5 | 9
459 | 2022-10-03 07:39 | 16.4 | 24.4 | 10
460 | 2022-10-03 07:40 | 16.2 | 24.4 | 10
461 | 2022-10-03 07:41 | 16.4 | 24.4 | 11
462 | 2022-10-03 07:42 | 16.4 | 24.5 | 11
463 | 2022-10-03 07:43 | 16.2 | 24.5 | 12
464 | 2022-10-03 07:44 | 16.2 | 24.4 | 12
465 | 2022-10-03 07:45 | 16.3 | 24.5 | 13
466 | 2022-10-03 07:46 | 16.8 | 25.2 | 13
467 | 2022-10-03 07:47 | 17.2 | 25.3 | 14
468 | 2022-10-03 07:48 | 17 | 24.1 | 14
469 | 2022-10-03 07:49 | 17.3 | 24.6 | 15
470 | 2022-10-03 07:50 | 17.7 | 24.4 | 15
471 | 2022-10-03 07:51 | 17.8 | 24.4 | 16
472 | 2022-10-03 07:52 | 18.1 | 24.9 | 16
473 | 2022-10-03 07:53 | 18.3 | 24.7 | 17
474 | 2022-10-03 07:54 | 18.3 | 24.7 | 17
475 | 2022-10-03 07:55 | 18.5 | 24.3 | 18
476 | 2022-10-03 07:56 | 18.5 | 24.2 | 18
477 | 2022-10-03 07:57 | 18.7 | 24.9 | 19
478 | 2022-10-03 07:58 | 18.5 | 24.2 | 19
479 | 2022-10-03 07:59 | 18.5 | 24.1 | 19
480 | 2022-10-03 08:00 | 18.6 | 24.6 | 20
481 | 2022-10-03 08:01 | 18.6 | 24.1 | 20
482 | 2022-10-03 08:02 | 18.4 | 24.7 | 20
483 | 2022-10-03 08:03 | 18.3 | 24.3 | 20
484 | 2022-10-03 08:04 | 18.6 | 24.7 | 21
485 | 2022-10-03 08:05 | 18.7 | 25.2 | 21
486 | 2022-10-03 08:06 | 18.8 | 24.8 | 21
487 | 2022-10-03 08:07 | 18.8 | 24.3 | 22
488 | 2022-10-03 08:08 | 19.1 | 24.2 | 22
489 | 2022-10-03 08:09 | 18.9 | 24.6 | 22
490 | 2022-10-03 08:10 | 18.9 | 24.3 | 23
491 | 2022-10-03 08:11 | 18.9 | 24.4 | 23
492 | 2022-10-03 08:12 | 19 | 24.3 | 23
493 | 2022-10-03 08:13 | 19.2 | 24.3 | 24
494 | 2022-10-03 08:14 | 19.1 | 23.9 | 24
495 | 2022-10-03 08:15 | 19.2 | 24.4 | 24
496 | 2022-10-03 08:16 | 19 | 24.3 | 24
497 | 2022-10-03 08:17 | 18.9 | 24.2 | 25
498 | 2022-10-03 08:18 | 19.1 | 24.5 | 25
499 | 2022-10-03 08:19 | 19.1 | 24.4 | 25
500 | 2022-10-03 08:20 | 19.2 | 24.3 | 25
501 | 2022-10-03 08:21 | 19.2 | 24.3 | 26
502 | 2022-10-03 08:22 | 19.1 | 24.3 | 26
503 | 2022-10-03 08:23 | 19.1 | 24.4 | 27
504 | 2022-10-03 08:24 | 19.1 | 24.4 | 27
505 | 2022-10-03 08:25 | 19.1 | 24.5 | 27
506 | 2022-10-03 08:26 | 19.3 | 24.5 | 28
507 | 2022-10-03 08:27 | 19.2 | 24.3 | 28
508 | 2022-10-03 08:28 | 19.1 | 24.3 | 28
509 | 2022-10-03 08:29 | 19.1 | 24.7 | 29
510 | 2022-10-03 08:30 | 19.2 | 24.2 | 29
511 | 2022-10-03 08:31 | 19.3 | 24.1 | 36
512 | 2022-10-03 08:32 | 19.2 | 24.7 | 48
513 | 2022-10-03 08:33 | 19.2 | 24.4 | 43
514 | 2022-10-03 08:34 | 19.3 | 24.8 | 37
515 | 2022-10-03 08:35 | 19.5 | 25.1 | 40
516 | 2022-10-03 08:36 | 19.8 | 24.6 | 45
517 | 2022-10-03 08:37 | 19.7 | 24 | 84
518 | 2022-10-03 08:38 | 20 | 24.4 | 79
519 | 2022-10-03 08:39 | 20.1 | 24.1 | 69
520 | 2022-10-03 08:40 | 20 | 24.1 | 78
521 | 2022-10-03 08:41 | 20.3 | 24.2 | 153
522 | 2022-10-03 08:42 | 20.3 | 24 | 224
523 | 2022-10-03 08:43 | 20.5 | 24.3 | 181
524 | 2022-10-03 08:44 | 20.5 | 23.9 | 163
525 | 2022-10-03 08:45 | 20.7 | 24.2 | 218
526 | 2022-10-03 08:46 | 20.7 | 23.6 | 295
527 | 2022-10-03 08:47 | 20.8 | 23.8 | 307
528 | 2022-10-03 08:48 | 20.9 | 23.9 | 304
529 | 2022-10-03 08:49 | 21 | 24 | 315
530 | 2022-10-03 08:50 | 20.9 | 23.9 | 319
531 | 2022-10-03 08:51 | 21 | 24 | 324
532 | 2022-10-03 08:52 | 20.6 | 24 | 330
533 | 2022-10-03 08:53 | 20.6 | 24 | 334
534 | 2022-10-03 08:54 | 20.8 | 24 | 337
535 | 2022-10-03 08:55 | 20.9 | 23.9 | 342
536 | 2022-10-03 08:56 | 21.2 | 23.7 | 346
537 | 2022-10-03 08:57 | 21.4 | 23.8 | 352
538 | 2022-10-03 08:58 | 21.2 | 23.9 | 357
539 | 2022-10-03 08:59 | 21.5 | 23.3 | 361
540 | 2022-10-03 09:00 | 21.5 | 23.4 | 366
541 | 2022-10-03 09:01 | 21.4 | 23.3 | 370
542 | 2022-10-03 09:02 | 21.4 | 23.6 | 374
543 | 2022-10-03 09:03 | 21.1 | 23.1 | 378
544 | 2022-10-03 09:04 | 21.1 | 23.6 | 383
545 | 2022-10-03 09:05 | 21 | 23.4 | 387
546 | 2022-10-03 09:06 | 20.9 | 24.3 | 391
547 | 2022-10-03 09:07 | 21.1 | 23.2 | 396
548 | 2022-10-03 09:08 | 20.8 | 23.9 | 399
549 | 2022-10-03 09:09 | 20.9 | 23.8 | 403
550 | 2022-10-03 09:10 | 21.1 | 23.9 | 406
551 | 2022-10-03 09:11 | 21 | 23.8 | 410
552 | 2022-10-03 09:12 | 21.2 | 23.7 | 414
553 | 2022-10-03 09:13 | 21.1 | 22.8 | 419
554 | 2022-10-03 09:14 | 21.3 | 23.4 | 422
555 | 2022-10-03 09:15 | 21.3 | 23.8 | 426
556 | 2022-10-03 09:16 | 21.3 | 23.5 | 431
557 | 2022-10-03 09:17 | 21.6 | 23.5 | 437
558 | 2022-10-03 09:18 | 21.5 | 23.7 | 440
559 | 2022-10-03 09:19 | 21.4 | 23.3 | 445
560 | 2022-10-03 09:20 | 21.4 | 23.7 | 451
561 | 2022-10-03 09:21 | 21.4 | 23.7 | 455
562 | 2022-10-03 09:22 | 21.4 | 23.5 | 457
563 | 2022-10-03 09:23 | 21.6 | 23.7 | 462
564 | 2022-10-03 09:24 | 21.6 | 23 | 469
565 | 2022-10-03 09:25 | 22 | 23.5 | 473
566 | 2022-10-03 09:26 | 22 | 23.5 | 477
567 | 2022-10-03 09:27 | 22.2 | 23.6 | 482
568 | 2022-10-03 09:28 | 22.3 | 23.4 | 486
569 | 2022-10-03 09:29 | 22.6 | 23.4 | 488
570 | 2022-10-03 09:30 | 22.4 | 23.5 | 491
571 | 2022-10-03 09:31 | 22.7 | 23.6 | 494
572 | 2022-10-03 09:32 | 22.6 | 23.7 | 497
573 | 2022-10-03 09:33 | 22.5 | 23.7 | 502
574 | 2022-10-03 09:34 | 22.7 | 23.9 | 507
575 | 2022-10-03 09:35 | 22.6 | 23.6 | 510
576 | 2022-10-03 09:36 | 22.5 | 24.3 | 515
577 | 2022-10-03 09:37 | 22.5 | 23.5 | 518
578 | 2022-10-03 09:38 | 23.2 | 24.8 | 523
579 | 2022-10-03 09:39 | 23.3 | 24.5 | 528
580 | 2022-10-03 09:40 | 23.2 | 23.9 | 531
581 | 2022-10-03 09:41 | 23 | 24.4 | 536
582 | 2022-10-03 09:42 | 22.9 | 23.8 | 541
583 | 2022-10-03 09:43 | 23 | 24.8 | 545
584 | 2022-10-03 09:44 | 23.3 | 23.6 | 549
585 | 2022-10-03 09:45 | 23.9 | 23.9 | 553
586 | 2022-10-03 09:46 | 23.4 | 24.6 | 557
587 | 2022-10-03 09:47 | 23.4 | 23.1 | 561
588 | 2022-10-03 09:48 | 23.5 | 23.7 | 566
589 | 2022-10-03 09:49 | 23.7 | 22.9 | 570
590 | 2022-10-03 09:50 | 23.6 | 23.4 | 573
591 | 2022-10-03 09:51 | 24.1 | 23.7 | 578
592 | 2022-10-03 09:52 | 24.1 | 23.9 | 581
593 | 2022-10-03 09:53 | 24.5 | 23.6 | 585
594 | 2022-10-03 09:54 | 24.2 | 23.6 | 588
595 | 2022-10-03 09:55 | 24.5 | 23.6 | 592
596 | 2022-10-03 09:56 | 23.7 | 23.9 | 594
597 | 2022-10-03 09:57 | 24 | 23.8 | 598
598 | 2022-10-03 09:58 | 24 | 24.3 | 601
599 | 2022-10-03 09:59 | 24.4 | 24.3 | 607
600 | 2022-10-03 10:00 | 24.1 | 23.4 | 611
601 | 2022-10-03 10:01 | 23.8 | 24.1 | 615
602 | 2022-10-03 10:02 | 23.9 | 23.5 | 619
603 | 2022-10-03 10:03 | 23.9 | 23.6 | 623
604 | 2022-10-03 10:04 | 24.2 | 23.5 | 625
605 | 2022-10-03 10:05 | 24.5 | 23.2 | 628
606 | 2022-10-03 10:06 | 24.5 | 23.3 | 630
607 | 2022-10-03 10:07 | 24.7 | 23.4 | 634
608 | 2022-10-03 10:08 | 24.7 | 23.4 | 636
609 | 2022-10-03 10:09 | 24.8 | 24.7 | 640
610 | 2022-10-03 10:10 | 24.3 | 24.3 | 646
611 | 2022-10-03 10:11 | 24.4 | 24.1 | 651
612 | 2022-10-03 10:12 | 24.3 | 24.9 | 656
613 | 2022-10-03 10:13 | 25 | 24 | 660
614 | 2022-10-03 10:14 | 24.7 | 24.3 | 665
615 | 2022-10-03 10:15 | 24 | 24 | 670
616 | 2022-10-03 10:16 | 24 | 23.9 | 673
617 | 2022-10-03 10:17 | 24.2 | 24.4 | 677
618 | 2022-10-03 10:18 | 24.1 | 24.4 | 679
619 | 2022-10-03 10:19 | 24.2 | 24 | 683
620 | 2022-10-03 10:20 | 24.4 | 24.4 | 685
621 | 2022-10-03 10:21 | 24.6 | 24.3 | 690
622 | 2022-10-03 10:22 | 24.6 | 23.6 | 692
623 | 2022-10-03 10:23 | 25 | 24.4 | 695
624 | 2022-10-03 10:24 | 24.8 | 24 | 700
625 | 2022-10-03 10:25 | 25.3 | 24 | 702
626 | 2022-10-03 10:26 | 25.5 | 23.8 | 706
627 | 2022-10-03 10:27 | 25.3 | 24.2 | 711
628 | 2022-10-03 10:28 | 25.1 | 23.9 | 714
629 | 2022-10-03 10:29 | 25.2 | 24.1 | 717
630 | 2022-10-03 10:30 | 25.3 | 24.2 | 721
631 | 2022-10-03 10:31 | 25.3 | 23.9 | 724
632 | 2022-10-03 10:32 | 25 | 24.8 | 727
633 | 2022-10-03 10:33 | 25.3 | 24.3 | 731
634 | 2022-10-03 10:34 | 25.4 | 23.5 | 734
635 | 2022-10-03 10:35 | 24.7 | 23.5 | 738
636 | 2022-10-03 10:36 | 24.8 | 23.4 | 741
637 | 2022-10-03 10:37 | 24.9 | 24.1 | 744
638 | 2022-10-03 10:38 | 25.2 | 23.8 | 747
639 | 2022-10-03 10:39 | 25.4 | 24.4 | 750
640 | 2022-10-03 10:40 | 25.5 | 24 | 753
641 | 2022-10-03 10:41 | 25.3 | 23.9 | 757
642 | 2022-10-03 10:42 | 25.6 | 24 | 760
643 | 2022-10-03 10:43 | 25.9 | 24.2 | 762
644 | 2022-10-03 10:44 | 26 | 23.9 | 766
645 | 2022-10-03 10:45 | 26.5 | 24.2 | 768
646 | 2022-10-03 10:46 | 26.1 | 24.7 | 772
647 | 2022-10-03 10:47 | 26 | 24.3 | 775
648 | 2022-10-03 10:48 | 25.9 | 24.5 | 778
649 | 2022-10-03 10:49 | 25.9 | 23.6 | 781
650 | 2022-10-03 10:50 | 25.6 | 23.9 | 784
651 | 2022-10-03 10:51 | 25.3 | 23.9 | 787
652 | 2022-10-03 10:52 | 25.3 | 24.4 | 791
653 | 2022-10-03 10:53 | 25.4 | 24.7 | 792
654 | 2022-10-03 10:54 | 25.8 | 24.9 | 796
655 | 2022-10-03 10:55 | 25.8 | 24.4 | 800
656 | 2022-10-03 10:56 | 26.1 | 24.3 | 803
657 | 2022-10-03 10:57 | 25.8 | 23.7 | 805
658 | 2022-10-03 10:58 | 25.9 | 24.1 | 809
659 | 2022-10-03 10:59 | 25.5 | 24.4 | 811
660 | 2022-10-03 11:00 | 26 | 24.6 | 814
661 | 2022-10-03 11:01 | 25.6 | 24.2 | 818
662 | 2022-10-03 11:02 | 25.5 | 24 | 821
663 | 2022-10-03 11:03 | 25.1 | 24 | 824
664 | 2022-10-03 11:04 | 25.2 | 24.1 | 828
665 | 2022-10-03 11:05 | 25.4 | 24.1 | 831
666 | 2022-10-03 11:06 | 26.2 | 23.9 | 833
667 | 2022-10-03 11:07 | 26.4 | 24.2 | 834
668 | 2022-10-03 11:08 | 25.6 | 24.2 | 837
669 | 2022-10-03 11:09 | 25.6 | 25.1 | 841
670 | 2022-10-03 11:10 | 25.3 | 24.4 | 843
671 | 2022-10-03 11:11 | 25.9 | 24.5 | 844
672 | 2022-10-03 11:12 | 25.9 | 24.4 | 846
673 | 2022-10-03 11:13 | 26 | 24.5 | 847
674 | 2022-10-03 11:14 | 25.9 | 24.5 | 850
675 | 2022-10-03 11:15 | 26.4 | 24.3 | 854
676 | 2022-10-03 11:16 | 26 | 24.3 | 858
677 | 2022-10-03 11:17 | 26.2 | 24.1 | 861
678 | 2022-10-03 11:18 | 26.6 | 24.5 | 862
679 | 2022-10-03 11:19 | 26.9 | 24.6 | 864
680 | 2022-10-03 11:20 | 27.2 | 24.6 | 866
681 | 2022-10-03 11:21 | 26.8 | 24.5 | 869
682 | 2022-10-03 11:22 | 27 | 25.5 | 872
683 | 2022-10-03 11:23 | 26.6 | 25.2 | 875
684 | 2022-10-03 11:24 | 26.7 | 24.1 | 876
685 | 2022-10-03 11:25 | 25.9 | 25.3 | 878
686 | 2022-10-03 11:26 | 26.4 | 24.4 | 881
687 | 2022-10-03 11:27 | 26.6 | 25 | 883
688 | 2022-10-03 11:28 | 26.8 | 24.6 | 884
689 | 2022-10-03 11:29 | 26.2 | 24.6 | 888
690 | 2022-10-03 11:30 | 26 | 24 | 889
691 | 2022-10-03 11:31 | 26.6 | 24.2 | 892
692 | 2022-10-03 11:32 | 26.6 | 24.4 | 895
693 | 2022-10-03 11:33 | 26.6 | 24.3 | 897
694 | 2022-10-03 11:34 | 26.9 | 24.3 | 899
695 | 2022-10-03 11:35 | 27 | 24.8 | 897
696 | 2022-10-03 11:36 | 26.9 | 24.8 | 899
697 | 2022-10-03 11:37 | 26.9 | 24.5 | 902
698 | 2022-10-03 11:38 | 27.8 | 25.1 | 903
699 | 2022-10-03 11:39 | 27.4 | 25.4 | 906
700 | 2022-10-03 11:40 | 27.6 | 24.9 | 909
701 | 2022-10-03 11:41 | 27.4 | 24.8 | 912
702 | 2022-10-03 11:42 | 26.9 | 24.3 | 912
703 | 2022-10-03 11:43 | 26.2 | 24.7 | 916
704 | 2022-10-03 11:44 | 26.3 | 24.3 | 919
705 | 2022-10-03 11:45 | 26.8 | 24.5 | 921
706 | 2022-10-03 11:46 | 27.3 | 25 | 924
707 | 2022-10-03 11:47 | 26.9 | 25.1 | 926
708 | 2022-10-03 11:48 | 27.5 | 24.9 | 927
709 | 2022-10-03 11:49 | 27.9 | 24.5 | 929
710 | 2022-10-03 11:50 | 27.6 | 24.6 | 930
711 | 2022-10-03 11:51 | 27.4 | 25.3 | 932
712 | 2022-10-03 11:52 | 27.2 | 24.6 | 933
713 | 2022-10-03 11:53 | 26.9 | 24.8 | 933
714 | 2022-10-03 11:54 | 26.5 | 24.7 | 936
715 | 2022-10-03 11:55 | 26.6 | 24.8 | 938
716 | 2022-10-03 11:56 | 26.9 | 24.6 | 941
717 | 2022-10-03 11:57 | 26.8 | 24.5 | 944
718 | 2022-10-03 11:58 | 27.6 | 24.7 | 946
719 | 2022-10-03 11:59 | 27.2 | 25.3 | 948
720 | 2022-10-03 12:00 | 26.6 | 24.7 | 950
721 | 2022-10-03 12:01 | 26.7 | 25.1 | 952
722 | 2022-10-03 12:02 | 26.3 | 24.5 | 954
723 | 2022-10-03 12:03 | 26.1 | 24.5 | 955
724 | 2022-10-03 12:04 | 26.3 | 24.8 | 958
725 | 2022-10-03 12:05 | 26.2 | 25.2 | 959
726 | 2022-10-03 12:06 | 26.5 | 25 | 960
727 | 2022-10-03 12:07 | 26.6 | 23.9 | 962
728 | 2022-10-03 12:08 | 26.7 | 24.6 | 964
729 | 2022-10-03 12:09 | 26.5 | 24.7 | 967
730 | 2022-10-03 12:10 | 27.1 | 24.1 | 968
731 | 2022-10-03 12:11 | 26.6 | 25 | 972
732 | 2022-10-03 12:12 | 26.7 | 24.7 | 974
733 | 2022-10-03 12:13 | 27 | 24.4 | 974
734 | 2022-10-03 12:14 | 27 | 24.7 | 976
735 | 2022-10-03 12:15 | 26 | 23.8 | 977
736 | 2022-10-03 12:16 | 26.3 | 24.3 | 977
737 | 2022-10-03 12:17 | 26.4 | 24.7 | 979
738 | 2022-10-03 12:18 | 26.3 | 24.6 | 979
739 | 2022-10-03 12:19 | 26.2 | 24.9 | 979
740 | 2022-10-03 12:20 | 26.1 | 24.7 | 981
741 | 2022-10-03 12:21 | 26 | 25 | 983
742 | 2022-10-03 12:22 | 26.2 | 24.7 | 985
743 | 2022-10-03 12:23 | 26.1 | 24.3 | 987
744 | 2022-10-03 12:24 | 26.2 | 25.1 | 989
745 | 2022-10-03 12:25 | 26.2 | 25.7 | 991
746 | 2022-10-03 12:26 | 26.1 | 24.5 | 993
747 | 2022-10-03 12:27 | 26.3 | 25 | 992
748 | 2022-10-03 12:28 | 26.8 | 24.8 | 992
749 | 2022-10-03 12:29 | 27.5 | 24.8 | 993
750 | 2022-10-03 12:30 | 27.9 | 24.5 | 993
751 | 2022-10-03 12:31 | 27.7 | 25.1 | 994
752 | 2022-10-03 12:32 | 27.6 | 24.5 | 995
753 | 2022-10-03 12:33 | 26.8 | 25.1 | 995
754 | 2022-10-03 12:34 | 27.2 | 24.8 | 997
755 | 2022-10-03 12:35 | 26.7 | 24.7 | 1000
756 | 2022-10-03 12:36 | 27.1 | 25 | 1001
757 | 2022-10-03 12:37 | 27 | 24.6 | 1002
758 | 2022-10-03 12:38 | 26.4 | 25.5 | 1003
759 | 2022-10-03 12:39 | 26.7 | 25.8 | 1004
760 | 2022-10-03 12:40 | 27.1 | 25.3 | 1004
761 | 2022-10-03 12:41 | 27.5 | 25 | 1004
762 | 2022-10-03 12:42 | 27.6 | 24.9 | 1004
763 | 2022-10-03 12:43 | 26.9 | 24.6 | 1005
764 | 2022-10-03 12:44 | 27.4 | 24.9 | 1008
765 | 2022-10-03 12:45 | 27.7 | 25.6 | 1010
766 | 2022-10-03 12:46 | 27.6 | 25.3 | 1012
767 | 2022-10-03 12:47 | 27.1 | 25.5 | 1012
768 | 2022-10-03 12:48 | 26.9 | 25 | 1014
769 | 2022-10-03 12:49 | 26.7 | 25.1 | 1013
770 | 2022-10-03 12:50 | 26.6 | 24.4 | 1012
771 | 2022-10-03 12:51 | 26.9 | 25.1 | 1013
772 | 2022-10-03 12:52 | 27.3 | 24.1 | 1014
773 | 2022-10-03 12:53 | 27.7 | 24.8 | 1015
774 | 2022-10-03 12:54 | 27.2 | 24.1 | 1016
775 | 2022-10-03 12:55 | 27.7 | 24.1 | 1015
776 | 2022-10-03 12:56 | 28.2 | 24.9 | 1013
777 | 2022-10-03 12:57 | 28.3 | 24.7 | 1013
778 | 2022-10-03 12:58 | 27.6 | 24.9 | 1013
779 | 2022-10-03 12:59 | 27.3 | 25.2 | 1014
780 | 2022-10-03 13:00 | 27.5 | 25.2 | 1015
781 | 2022-10-03 13:01 | 27.1 | 24.9 | 1016
782 | 2022-10-03 13:02 | 27 | 25.4 | 1017
783 | 2022-10-03 13:03 | 26.8 | 25.4 | 1018
784 | 2022-10-03 13:04 | 26.7 | 25.1 | 1017
785 | 2022-10-03 13:05 | 26.6 | 25 | 1016
786 | 2022-10-03 13:06 | 26.8 | 25.7 | 1016
787 | 2022-10-03 13:07 | 27 | 25.7 | 1016
788 | 2022-10-03 13:08 | 27.7 | 25.5 | 1017
789 | 2022-10-03 13:09 | 28.1 | 26.2 | 1019
790 | 2022-10-03 13:10 | 27.8 | 24.8 | 1019
791 | 2022-10-03 13:11 | 27.8 | 25.3 | 1019
792 | 2022-10-03 13:12 | 27.7 | 25.6 | 1020
793 | 2022-10-03 13:13 | 27.9 | 25.5 | 1018
794 | 2022-10-03 13:14 | 27.7 | 25.1 | 1017
795 | 2022-10-03 13:15 | 28.4 | 25.9 | 1018
796 | 2022-10-03 13:16 | 28.4 | 25.6 | 1014
797 | 2022-10-03 13:17 | 28.3 | 24.6 | 1013
798 | 2022-10-03 13:18 | 28 | 25.4 | 1014
799 | 2022-10-03 13:19 | 27.7 | 25.5 | 1010
800 | 2022-10-03 13:20 | 27.5 | 25.3 | 1010
801 | 2022-10-03 13:21 | 28 | 25.8 | 1011
802 | 2022-10-03 13:22 | 27.9 | 25.9 | 1010
803 | 2022-10-03 13:23 | 27.8 | 25 | 1008
804 | 2022-10-03 13:24 | 27.3 | 25.7 | 1008
805 | 2022-10-03 13:25 | 27.3 | 25.3 | 1008
806 | 2022-10-03 13:26 | 27.8 | 25.5 | 1006
807 | 2022-10-03 13:27 | 28.1 | 26.4 | 1006
808 | 2022-10-03 13:28 | 28 | 26.1 | 1006
809 | 2022-10-03 13:29 | 27.5 | 24.9 | 1008
810 | 2022-10-03 13:30 | 28 | 25.8 | 1005
811 | 2022-10-03 13:31 | 27.6 | 25.7 | 1006
812 | 2022-10-03 13:32 | 27.7 | 25.7 | 1007
813 | 2022-10-03 13:33 | 27.8 | 24.8 | 1004
814 | 2022-10-03 13:34 | 27.7 | 25.2 | 1005
815 | 2022-10-03 13:35 | 28.3 | 25.8 | 1005
816 | 2022-10-03 13:36 | 28 | 25.4 | 1001
817 | 2022-10-03 13:37 | 27.6 | 26 | 1001
818 | 2022-10-03 13:38 | 27.5 | 25.3 | 1001
819 | 2022-10-03 13:39 | 28 | 25.6 | 1001
820 | 2022-10-03 13:40 | 27.7 | 26.5 | 1002
821 | 2022-10-03 13:41 | 27.4 | 25.4 | 1000
822 | 2022-10-03 13:42 | 27.3 | 26.3 | 1004
823 | 2022-10-03 13:43 | 27.3 | 25.4 | 1000
824 | 2022-10-03 13:44 | 27.4 | 25.9 | 998
825 | 2022-10-03 13:45 | 27.6 | 25.6 | 1000
826 | 2022-10-03 13:46 | 27.6 | 26 | 999
827 | 2022-10-03 13:47 | 27.7 | 25.4 | 998
828 | 2022-10-03 13:48 | 27.3 | 26.4 | 999
829 | 2022-10-03 13:49 | 27.9 | 25 | 999
830 | 2022-10-03 13:50 | 27.5 | 25.6 | 996
831 | 2022-10-03 13:51 | 27.7 | 26 | 995
832 | 2022-10-03 13:52 | 27.7 | 26 | 990
833 | 2022-10-03 13:53 | 27.3 | 26.4 | 992
834 | 2022-10-03 13:54 | 27.3 | 25.9 | 990
835 | 2022-10-03 13:55 | 26.8 | 25.4 | 990
836 | 2022-10-03 13:56 | 26.4 | 25.7 | 982
837 | 2022-10-03 13:57 | 26.9 | 25.8 | 987
838 | 2022-10-03 13:58 | 27 | 25.8 | 986
839 | 2022-10-03 13:59 | 27.2 | 25.8 | 985
840 | 2022-10-03 14:00 | 27.9 | 25.5 | 982
841 | 2022-10-03 14:01 | 28.4 | 25.3 | 982
842 | 2022-10-03 14:02 | 28.2 | 25.4 | 981
843 | 2022-10-03 14:03 | 28.9 | 26.7 | 981
844 | 2022-10-03 14:04 | 27.9 | 26.1 | 982
845 | 2022-10-03 14:05 | 27.4 | 25.6 | 978
846 | 2022-10-03 14:06 | 27.6 | 26.1 | 976
847 | 2022-10-03 14:07 | 27.7 | 24.8 | 974
848 | 2022-10-03 14:08 | 27.6 | 25.4 | 973
849 | 2022-10-03 14:09 | 28.4 | 25.6 | 970
850 | 2022-10-03 14:10 | 27.7 | 25.8 | 971
851 | 2022-10-03 14:11 | 27.8 | 25.1 | 971
852 | 2022-10-03 14:12 | 28.1 | 24.9 | 970
853 | 2022-10-03 14:13 | 27.6 | 25.8 | 973
854 | 2022-10-03 14:14 | 27.8 | 26 | 974
855 | 2022-10-03 14:15 | 28.5 | 25.8 | 971
856 | 2022-10-03 14:16 | 28.2 | 25.5 | 968
857 | 2022-10-03 14:17 | 27.3 | 25.7 | 965
858 | 2022-10-03 14:18 | 27.4 | 25.5 | 962
859 | 2022-10-03 14:19 | 28 | 26.4 | 962
860 | 2022-10-03 14:20 | 28.2 | 26.1 | 958
861 | 2022-10-03 14:21 | 28.5 | 25.6 | 959
862 | 2022-10-03 14:22 | 28.3 | 25.6 | 959
863 | 2022-10-03 14:23 | 27.9 | 26.5 | 958
864 | 2022-10-03 14:24 | 28.4 | 25.7 | 955
865 | 2022-10-03 14:25 | 28 | 26.5 | 953
866 | 2022-10-03 14:26 | 28 | 26.2 | 952
867 | 2022-10-03 14:27 | 27.6 | 25.7 | 950
868 | 2022-10-03 14:28 | 27.7 | 26.5 | 950
869 | 2022-10-03 14:29 | 27.7 | 25.8 | 943
870 | 2022-10-03 14:30 | 27.5 | 26.2 | 944
871 | 2022-10-03 14:31 | 27.5 | 26.3 | 945
872 | 2022-10-03 14:32 | 27.8 | 26.2 | 941
873 | 2022-10-03 14:33 | 27.6 | 26 | 940
874 | 2022-10-03 14:34 | 27.6 | 26.6 | 937
875 | 2022-10-03 14:35 | 27.7 | 26.4 | 938
876 | 2022-10-03 14:36 | 27.6 | 25.6 | 936
877 | 2022-10-03 14:37 | 27.4 | 25.7 | 935
878 | 2022-10-03 14:38 | 27.2 | 25.8 | 932
879 | 2022-10-03 14:39 | 27.6 | 25.8 | 930
880 | 2022-10-03 14:40 | 27.8 | 24.8 | 929
881 | 2022-10-03 14:41 | 27.3 | 25.7 | 924
882 | 2022-10-03 14:42 | 27.2 | 25.8 | 922
883 | 2022-10-03 14:43 | 27.5 | 26.3 | 920
884 | 2022-10-03 14:44 | 27.2 | 25.4 | 922
885 | 2022-10-03 14:45 | 26.9 | 25.8 | 921
886 | 2022-10-03 14:46 | 26.8 | 26.5 | 921
887 | 2022-10-03 14:47 | 26.9 | 26.2 | 920
888 | 2022-10-03 14:48 | 26.8 | 26 | 917
889 | 2022-10-03 14:49 | 27.5 | 25.3 | 915
890 | 2022-10-03 14:50 | 27.5 | 25.9 | 910
891 | 2022-10-03 14:51 | 27.1 | 25.6 | 908
892 | 2022-10-03 14:52 | 27.8 | 26.1 | 904
893 | 2022-10-03 14:53 | 27.9 | 25.7 | 900
894 | 2022-10-03 14:54 | 27.6 | 25.6 | 898
895 | 2022-10-03 14:55 | 27.7 | 25.7 | 897
896 | 2022-10-03 14:56 | 27.4 | 25.4 | 893
897 | 2022-10-03 14:57 | 27.4 | 25.5 | 892
898 | 2022-10-03 14:58 | 27.9 | 25.1 | 892
899 | 2022-10-03 14:59 | 28.2 | 25.4 | 889
900 | 2022-10-03 15:00 | 28.4 | 25.7 | 889
901 | 2022-10-03 15:01 | 28.6 | 25.9 | 886
902 | 2022-10-03 15:02 | 28.5 | 24.8 | 883
903 | 2022-10-03 15:03 | 28.5 | 25.6 | 883
904 | 2022-10-03 15:04 | 28.2 | 25.1 | 880
905 | 2022-10-03 15:05 | 28.6 | 25.6 | 876
906 | 2022-10-03 15:06 | 29.2 | 25.6 | 875
907 | 2022-10-03 15:07 | 28.9 | 26.1 | 872
908 | 2022-10-03 15:08 | 28.8 | 26.5 | 871
909 | 2022-10-03 15:09 | 28.7 | 25.5 | 868
910 | 2022-10-03 15:10 | 27.9 | 25.9 | 864
911 | 2022-10-03 15:11 | 28 | 25.8 | 857
912 | 2022-10-03 15:12 | 28.4 | 26.1 | 854
913 | 2022-10-03 15:13 | 28.3 | 25.5 | 854
914 | 2022-10-03 15:14 | 28.1 | 25.8 | 853
915 | 2022-10-03 15:15 | 28.1 | 26 | 853
916 | 2022-10-03 15:16 | 28.1 | 25.8 | 850
917 | 2022-10-03 15:17 | 27.9 | 25.4 | 849
918 | 2022-10-03 15:18 | 28.1 | 25.5 | 846
919 | 2022-10-03 15:19 | 27.7 | 24.8 | 844
920 | 2022-10-03 15:20 | 28.3 | 24.8 | 839
921 | 2022-10-03 15:21 | 28.6 | 25.5 | 838
922 | 2022-10-03 15:22 | 28.8 | 25.5 | 833
923 | 2022-10-03 15:23 | 29 | 26 | 830
924 | 2022-10-03 15:24 | 29 | 25.6 | 827
925 | 2022-10-03 15:25 | 28.7 | 26.1 | 823
926 | 2022-10-03 15:26 | 28.7 | 25.6 | 820
927 | 2022-10-03 15:27 | 28.9 | 26.6 | 818
928 | 2022-10-03 15:28 | 28.6 | 25.8 | 814
929 | 2022-10-03 15:29 | 29.4 | 25.4 | 811
930 | 2022-10-03 15:30 | 29.2 | 26.3 | 807
931 | 2022-10-03 15:31 | 29.3 | 24.9 | 805
932 | 2022-10-03 15:32 | 29.4 | 26.4 | 801
933 | 2022-10-03 15:33 | 29.3 | 25.8 | 798
934 | 2022-10-03 15:34 | 28.9 | 26.3 | 795
935 | 2022-10-03 15:35 | 28.5 | 25.7 | 792
936 | 2022-10-03 15:36 | 28.5 | 25.7 | 788
937 | 2022-10-03 15:37 | 28.3 | 25.6 | 788
938 | 2022-10-03 15:38 | 28.7 | 25.7 | 784
939 | 2022-10-03 15:39 | 28.1 | 26.7 | 781
940 | 2022-10-03 15:40 | 28.2 | 25.7 | 778
941 | 2022-10-03 15:41 | 28.1 | 25.7 | 774
942 | 2022-10-03 15:42 | 28.1 | 25.9 | 770
943 | 2022-10-03 15:43 | 28.3 | 25.9 | 767
944 | 2022-10-03 15:44 | 27.9 | 26.3 | 764
945 | 2022-10-03 15:45 | 28.3 | 26.8 | 762
946 | 2022-10-03 15:46 | 27.4 | 25.7 | 758
947 | 2022-10-03 15:47 | 26.8 | 25.6 | 754
948 | 2022-10-03 15:48 | 27.4 | 25.6 | 749
949 | 2022-10-03 15:49 | 27.8 | 25.9 | 745
950 | 2022-10-03 15:50 | 27.5 | 25.7 | 744
951 | 2022-10-03 15:51 | 27.4 | 25.7 | 741
952 | 2022-10-03 15:52 | 27.6 | 26 | 739
953 | 2022-10-03 15:53 | 27.8 | 25.9 | 736
954 | 2022-10-03 15:54 | 27.5 | 26 | 732
955 | 2022-10-03 15:55 | 27.6 | 26 | 730
956 | 2022-10-03 15:56 | 28 | 25.9 | 725
957 | 2022-10-03 15:57 | 28.4 | 25.9 | 721
958 | 2022-10-03 15:58 | 28.6 | 25.9 | 719
959 | 2022-10-03 15:59 | 27.8 | 26.1 | 716
960 | 2022-10-03 16:00 | 28.1 | 25.9 | 714
961 | 2022-10-03 16:01 | 27.3 | 26 | 711
962 | 2022-10-03 16:02 | 27.9 | 25.4 | 707
963 | 2022-10-03 16:03 | 27.8 | 26.5 | 702
964 | 2022-10-03 16:04 | 27.7 | 26.9 | 700
965 | 2022-10-03 16:05 | 27.4 | 25.8 | 697
966 | 2022-10-03 16:06 | 27.4 | 25.3 | 693
967 | 2022-10-03 16:07 | 28 | 26 | 688
968 | 2022-10-03 16:08 | 27.9 | 26.7 | 685
969 | 2022-10-03 16:09 | 28 | 26.3 | 680
970 | 2022-10-03 16:10 | 28.2 | 26 | 677
971 | 2022-10-03 16:11 | 28.2 | 25.8 | 672
972 | 2022-10-03 16:12 | 28 | 26 | 669
973 | 2022-10-03 16:13 | 27.5 | 26.3 | 666
974 | 2022-10-03 16:14 | 28 | 26.1 | 664
975 | 2022-10-03 16:15 | 27.3 | 26.1 | 661
976 | 2022-10-03 16:16 | 27.5 | 26 | 656
977 | 2022-10-03 16:17 | 27.6 | 25.7 | 652
978 | 2022-10-03 16:18 | 27.7 | 26.1 | 649
979 | 2022-10-03 16:19 | 27.8 | 25.8 | 646
980 | 2022-10-03 16:20 | 28 | 26.4 | 641
981 | 2022-10-03 16:21 | 27.7 | 26.3 | 637
982 | 2022-10-03 16:22 | 27.5 | 25.3 | 633
983 | 2022-10-03 16:23 | 27.7 | 25.4 | 629
984 | 2022-10-03 16:24 | 27.9 | 26.3 | 626
985 | 2022-10-03 16:25 | 27.9 | 26.6 | 622
986 | 2022-10-03 16:26 | 28 | 26 | 619
987 | 2022-10-03 16:27 | 28.5 | 26.1 | 615
988 | 2022-10-03 16:28 | 28.8 | 25.7 | 612
989 | 2022-10-03 16:29 | 27.7 | 25.8 | 608
990 | 2022-10-03 16:30 | 27.5 | 26 | 604
991 | 2022-10-03 16:31 | 27.8 | 26 | 600
992 | 2022-10-03 16:32 | 28.1 | 26.6 | 596
993 | 2022-10-03 16:33 | 27.8 | 26 | 593
994 | 2022-10-03 16:34 | 28 | 25.5 | 589
995 | 2022-10-03 16:35 | 28.3 | 26.1 | 585
996 | 2022-10-03 16:36 | 28.3 | 26 | 581
997 | 2022-10-03 16:37 | 28.2 | 25.9 | 577
998 | 2022-10-03 16:38 | 28 | 26.1 | 574
999 | 2022-10-03 16:39 | 27.7 | 25.7 | 570
1000 | 2022-10-03 16:40 | 27.9 | 26 | 566
1001 | 2022-10-03 16:41 | 27.9 | 25.7 | 563
1002 | 2022-10-03 16:42 | 27.7 | 26 | 559
1003 | 2022-10-03 16:43 | 27.7 | 25.8 | 554
1004 | 2022-10-03 16:44 | 27.5 | 25.4 | 551
1005 | 2022-10-03 16:45 | 27.4 | 26.2 | 547
1006 | 2022-10-03 16:46 | 27.4 | 26.2 | 543
1007 | 2022-10-03 16:47 | 27.2 | 26.3 | 538
1008 | 2022-10-03 16:48 | 27.3 | 26.2 | 534
1009 | 2022-10-03 16:49 | 27.5 | 25.7 | 530
1010 | 2022-10-03 16:50 | 27.8 | 26.3 | 526
1011 | 2022-10-03 16:51 | 27.6 | 26.1 | 521
1012 | 2022-10-03 16:52 | 27.7 | 25.2 | 518
1013 | 2022-10-03 16:53 | 27.5 | 25.7 | 513
1014 | 2022-10-03 16:54 | 27.4 | 26.8 | 510
1015 | 2022-10-03 16:55 | 27.2 | 25.8 | 505
1016 | 2022-10-03 16:56 | 27.1 | 26.4 | 501
1017 | 2022-10-03 16:57 | 26.7 | 25.8 | 497
1018 | 2022-10-03 16:58 | 26.6 | 25 | 486
1019 | 2022-10-03 16:59 | 26.8 | 25.9 | 486
1020 | 2022-10-03 17:00 | 26.9 | 25.8 | 481
1021 | 2022-10-03 17:01 | 27.3 | 26.1 | 476
1022 | 2022-10-03 17:02 | 27.7 | 25.9 | 472
1023 | 2022-10-03 17:03 | 27.4 | 26.1 | 470
1024 | 2022-10-03 17:04 | 27.4 | 25.9 | 463
1025 | 2022-10-03 17:05 | 27.5 | 25.8 | 460
1026 | 2022-10-03 17:06 | 26.7 | 25.9 | 451
1027 | 2022-10-03 17:07 | 26.8 | 25.7 | 450
1028 | 2022-10-03 17:08 | 26.6 | 26 | 446
1029 | 2022-10-03 17:09 | 26.6 | 25.9 | 440
1030 | 2022-10-03 17:10 | 27 | 26.3 | 437
1031 | 2022-10-03 17:11 | 26.7 | 25.9 | 434
1032 | 2022-10-03 17:12 | 26.3 | 25.8 | 428
1033 | 2022-10-03 17:13 | 26.6 | 26.1 | 424
1034 | 2022-10-03 17:14 | 26.6 | 26 | 420
1035 | 2022-10-03 17:15 | 26.8 | 25.5 | 414
1036 | 2022-10-03 17:16 | 26.7 | 25.8 | 411
1037 | 2022-10-03 17:17 | 26.6 | 25.6 | 368
1038 | 2022-10-03 17:18 | 26.6 | 25 | 404
1039 | 2022-10-03 17:19 | 26.2 | 26.2 | 385
1040 | 2022-10-03 17:20 | 26.2 | 26.1 | 386
1041 | 2022-10-03 17:21 | 26.1 | 25.5 | 392
1042 | 2022-10-03 17:22 | 26.5 | 26 | 342
1043 | 2022-10-03 17:23 | 26.4 | 25.6 | 368
1044 | 2022-10-03 17:24 | 26 | 25.9 | 374
1045 | 2022-10-03 17:25 | 25.6 | 25.7 | 376
1046 | 2022-10-03 17:26 | 26 | 25.8 | 371
1047 | 2022-10-03 17:27 | 25.9 | 26.1 | 366
1048 | 2022-10-03 17:28 | 25.8 | 25.6 | 361
1049 | 2022-10-03 17:29 | 25.9 | 25.8 | 356
1050 | 2022-10-03 17:30 | 25.7 | 25.8 | 351
1051 | 2022-10-03 17:31 | 25.8 | 25.5 | 348
1052 | 2022-10-03 17:32 | 25.9 | 26.2 | 343
1053 | 2022-10-03 17:33 | 25.7 | 26.6 | 339
1054 | 2022-10-03 17:34 | 25.7 | 26.2 | 335
1055 | 2022-10-03 17:35 | 25.8 | 26.2 | 332
1056 | 2022-10-03 17:36 | 26 | 26.3 | 312
1057 | 2022-10-03 17:37 | 25.9 | 25.8 | 271
1058 | 2022-10-03 17:38 | 25.9 | 26 | 320
1059 | 2022-10-03 17:39 | 25.7 | 25.7 | 311
1060 | 2022-10-03 17:40 | 25.5 | 25.9 | 305
1061 | 2022-10-03 17:41 | 25.6 | 25.8 | 301
1062 | 2022-10-03 17:42 | 25.9 | 26 | 297
1063 | 2022-10-03 17:43 | 25.7 | 25.9 | 292
1064 | 2022-10-03 17:44 | 25.8 | 25.9 | 276
1065 | 2022-10-03 17:45 | 25.8 | 25.9 | 244
1066 | 2022-10-03 17:46 | 25.7 | 25.7 | 239
1067 | 2022-10-03 17:47 | 25.9 | 25.5 | 212
1068 | 2022-10-03 17:48 | 25.9 | 25.9 | 255
1069 | 2022-10-03 17:49 | 25.4 | 25.9 | 269
1070 | 2022-10-03 17:50 | 25.6 | 26.3 | 240
1071 | 2022-10-03 17:51 | 25.5 | 26 | 257
1072 | 2022-10-03 17:52 | 25.5 | 26.8 | 251
1073 | 2022-10-03 17:53 | 25.3 | 25.9 | 246
1074 | 2022-10-03 17:54 | 25.1 | 25.4 | 243
1075 | 2022-10-03 17:55 | 24.9 | 25.6 | 200
1076 | 2022-10-03 17:56 | 25.1 | 25.9 | 234
1077 | 2022-10-03 17:57 | 25 | 26 | 230
1078 | 2022-10-03 17:58 | 25.2 | 25.6 | 226
1079 | 2022-10-03 17:59 | 25.3 | 26.1 | 222
1080 | 2022-10-03 18:00 | 25.2 | 25.7 | 217
1081 | 2022-10-03 18:01 | 25.3 | 26 | 211
1082 | 2022-10-03 18:02 | 25.2 | 25 | 209
1083 | 2022-10-03 18:03 | 25.1 | 25.9 | 205
1084 | 2022-10-03 18:04 | 25 | 25.8 | 188
1085 | 2022-10-03 18:05 | 24.9 | 25.7 | 166
1086 | 2022-10-03 18:06 | 24.9 | 25.8 | 192
1087 | 2022-10-03 18:07 | 25 | 26 | 186
1088 | 2022-10-03 18:08 | 25.2 | 25.8 | 181
1089 | 2022-10-03 18:09 | 25.2 | 25.9 | 177
1090 | 2022-10-03 18:10 | 24.8 | 25.7 | 167
1091 | 2022-10-03 18:11 | 24.7 | 26.9 | 168
1092 | 2022-10-03 18:12 | 24.8 | 25.8 | 163
1093 | 2022-10-03 18:13 | 24.7 | 25.9 | 158
1094 | 2022-10-03 18:14 | 24.6 | 25.8 | 154
1095 | 2022-10-03 18:15 | 24.7 | 25.6 | 149
1096 | 2022-10-03 18:16 | 24.6 | 25.8 | 144
1097 | 2022-10-03 18:17 | 24.3 | 25.4 | 142
1098 | 2022-10-03 18:18 | 24.2 | 26 | 103
1099 | 2022-10-03 18:19 | 24.1 | 25.9 | 127
1100 | 2022-10-03 18:20 | 24.1 | 25.9 | 128
1101 | 2022-10-03 18:21 | 24.2 | 25.8 | 124
1102 | 2022-10-03 18:22 | 24.4 | 25.7 | 106
1103 | 2022-10-03 18:23 | 24.4 | 25.8 | 81
1104 | 2022-10-03 18:24 | 24.3 | 25.9 | 108
1105 | 2022-10-03 18:25 | 24.2 | 25.9 | 101
1106 | 2022-10-03 18:26 | 24.1 | 26 | 104
1107 | 2022-10-03 18:27 | 24.2 | 26.2 | 101
1108 | 2022-10-03 18:28 | 24.2 | 26 | 84
1109 | 2022-10-03 18:29 | 23.8 | 25.9 | 89
1110 | 2022-10-03 18:30 | 23.8 | 25.9 | 89
1111 | 2022-10-03 18:31 | 23.8 | 26.1 | 84
1112 | 2022-10-03 18:32 | 23.9 | 25.9 | 80
1113 | 2022-10-03 18:33 | 23.6 | 26.1 | 47
1114 | 2022-10-03 18:34 | 23.6 | 25.2 | 31
1115 | 2022-10-03 18:35 | 23.6 | 25.7 | 27
1116 | 2022-10-03 18:36 | 23.6 | 26.2 | 23
1117 | 2022-10-03 18:37 | 23.3 | 26 | 19
1118 | 2022-10-03 18:38 | 23.4 | 26 | 18
1119 | 2022-10-03 18:39 | 23.2 | 25.8 | 17
1120 | 2022-10-03 18:40 | 23.1 | 25.8 | 16
1121 | 2022-10-03 18:41 | 23 | 25.9 | 15
1122 | 2022-10-03 18:42 | 23 | 25.9 | 14
1123 | 2022-10-03 18:43 | 22.8 | 25.8 | 14
1124 | 2022-10-03 18:44 | 22.8 | 25.8 | 13
1125 | 2022-10-03 18:45 | 22.7 | 25.8 | 13
1126 | 2022-10-03 18:46 | 22.6 | 25.8 | 12
1127 | 2022-10-03 18:47 | 22.6 | 25.9 | 11
1128 | 2022-10-03 18:48 | 22.4 | 26 | 9
1129 | 2022-10-03 18:49 | 22.5 | 25.9 | 8
1130 | 2022-10-03 18:50 | 22.4 | 25.9 | 6
1131 | 2022-10-03 18:51 | 22.4 | 25.9 | 5
1132 | 2022-10-03 18:52 | 22.2 | 25.6 | 4
1133 | 2022-10-03 18:53 | 22.2 | 25.7 | 3
1134 | 2022-10-03 18:54 | 22.1 | 25.9 | 3
1135 | 2022-10-03 18:55 | 22.1 | 25.7 | 2
1136 | 2022-10-03 18:56 | 22 | 25.6 | 2
1137 | 2022-10-03 18:57 | 21.9 | 25.5 | 1
1138 | 2022-10-03 18:58 | 22 | 25.1 | 1
1139 | 2022-10-03 18:59 | 21.8 | 25.8 | 0
1140 | 2022-10-03 19:00 | 21.5 | 25.6 | 0
1141 | 2022-10-03 19:01 | 21.6 | 25.7 | 0
1142 | 2022-10-03 19:02 | 21.6 | 25.8 | 0
1143 | 2022-10-03 19:03 | 21.7 | 25.7 | 0
1144 | 2022-10-03 19:04 | 21.5 | 25.7 | 0
1145 | 2022-10-03 19:05 | 21.3 | 25.7 | 0
1146 | 2022-10-03 19:06 | 21.2 | 25.7 | 0
1147 | 2022-10-03 19:07 | 21.1 | 25.7 | 0
1148 | 2022-10-03 19:08 | 21.1 | 25.5 | 0
1149 | 2022-10-03 19:09 | 20.8 | 25.3 | 0
1150 | 2022-10-03 19:10 | 20.7 | 25.5 | 0
1151 | 2022-10-03 19:11 | 20.8 | 25.4 | 0
1152 | 2022-10-03 19:12 | 20.8 | 26 | 0
1153 | 2022-10-03 19:13 | 20.6 | 25.1 | 0
1154 | 2022-10-03 19:14 | 20.6 | 25.9 | 0
1155 | 2022-10-03 19:15 | 20.5 | 24.8 | 0
1156 | 2022-10-03 19:16 | 20.4 | 25.2 | 0
1157 | 2022-10-03 19:17 | 20.3 | 25.6 | 0
1158 | 2022-10-03 19:18 | 20.1 | 26.3 | 0
1159 | 2022-10-03 19:19 | 20.3 | 26.1 | 0
1160 | 2022-10-03 19:20 | 20.2 | 25.8 | 0
1161 | 2022-10-03 19:21 | 20.2 | 25.1 | 0
1162 | 2022-10-03 19:22 | 20.3 | 25.7 | 0
1163 | 2022-10-03 19:23 | 20.2 | 25.6 | 0
1164 | 2022-10-03 19:24 | 20.2 | 25.6 | 0
1165 | 2022-10-03 19:25 | 20.1 | 25.6 | 0
1166 | 2022-10-03 19:26 | 19.9 | 25.6 | 0
1167 | 2022-10-03 19:27 | 19.9 | 25.7 | 0
1168 | 2022-10-03 19:28 | 19.9 | 25.6 | 0
1169 | 2022-10-03 19:29 | 19.7 | 25.3 | 0
1170 | 2022-10-03 19:30 | 19.7 | 25.6 | 0
1171 | 2022-10-03 19:31 | 19.8 | 26.2 | 0
1172 | 2022-10-03 19:32 | 19.9 | 26.1 | 0
1173 | 2022-10-03 19:33 | 19.8 | 24.8 | 0
1174 | 2022-10-03 19:34 | 19.7 | 26.1 | 0
1175 | 2022-10-03 19:35 | 19.8 | 25.6 | 0
1176 | 2022-10-03 19:36 | 19.8 | 25.6 | 0
1177 | 2022-10-03 19:37 | 19.7 | 25.6 | 0
1178 | 2022-10-03 19:38 | 19.8 | 25.6 | 0
1179 | 2022-10-03 19:39 | 19.6 | 25.4 | 0
1180 | 2022-10-03 19:40 | 19.8 | 25.6 | 0
1181 | 2022-10-03 19:41 | 19.9 | 25.6 | 0
1182 | 2022-10-03 19:42 | 19.6 | 25.6 | 0
1183 | 2022-10-03 19:43 | 19.6 | 25.8 | 0
1184 | 2022-10-03 19:44 | 19.6 | 25.5 | 0
1185 | 2022-10-03 19:45 | 19.6 | 25.8 | 0
1186 | 2022-10-03 19:46 | 19.7 | 25.6 | 0
1187 | 2022-10-03 19:47 | 19.8 | 25.6 | 0
1188 | 2022-10-03 19:48 | 20 | 25.6 | 0
1189 | 2022-10-03 19:49 | 20 | 25.6 | 0
1190 | 2022-10-03 19:50 | 20 | 25.6 | 0
1191 | 2022-10-03 19:51 | 19.9 | 25.5 | 0
1192 | 2022-10-03 19:52 | 20 | 25.6 | 0
1193 | 2022-10-03 19:53 | 19.9 | 25.6 | 0
1194 | 2022-10-03 19:54 | 19.9 | 25.6 | 0
1195 | 2022-10-03 19:55 | 19.9 | 25.6 | 0
1196 | 2022-10-03 19:56 | 20 | 25.6 | 0
1197 | 2022-10-03 19:57 | 20 | 25.5 | 0
1198 | 2022-10-03 19:58 | 19.9 | 25.6 | 0
1199 | 2022-10-03 19:59 | 19.8 | 25.6 | 0
1200 | 2022-10-03 20:00 | 19.7 | 25.8 | 0
1201 | 2022-10-03 20:01 | 19.7 | 25.9 | 0
1202 | 2022-10-03 20:02 | 19.8 | 25.5 | 0
1203 | 2022-10-03 20:03 | 19.9 | 25.5 | 0
1204 | 2022-10-03 20:04 | 19.8 | 25.7 | 0
1205 | 2022-10-03 20:05 | 19.7 | 25.1 | 0
1206 | 2022-10-03 20:06 | 19.8 | 26.2 | 0
1207 | 2022-10-03 20:07 | 19.5 | 25.8 | 0
1208 | 2022-10-03 20:08 | 19.4 | 25.3 | 0
1209 | 2022-10-03 20:09 | 19.5 | 25.8 | 0
1210 | 2022-10-03 20:10 | 19.6 | 25.3 | 0
1211 | 2022-10-03 20:11 | 19.3 | 25.5 | 0
1212 | 2022-10-03 20:12 | 19.3 | 24.7 | 0
1213 | 2022-10-03 20:13 | 19.4 | 25.2 | 0
1214 | 2022-10-03 20:14 | 19.3 | 24.8 | 0
1215 | 2022-10-03 20:15 | 19.2 | 24.8 | 0
1216 | 2022-10-03 20:16 | 19.4 | 26.1 | 0
1217 | 2022-10-03 20:17 | 19.3 | 26.3 | 0
1218 | 2022-10-03 20:18 | 19.2 | 25.8 | 0
1219 | 2022-10-03 20:19 | 19.2 | 24.8 | 0
1220 | 2022-10-03 20:20 | 19.3 | 24.6 | 0
1221 | 2022-10-03 20:21 | 19.1 | 25.3 | 0
1222 | 2022-10-03 20:22 | 19 | 25.4 | 0
1223 | 2022-10-03 20:23 | 19 | 25.7 | 0
1224 | 2022-10-03 20:24 | 19.1 | 24.9 | 0
1225 | 2022-10-03 20:25 | 19 | 25.9 | 0
1226 | 2022-10-03 20:26 | 18.9 | 25.4 | 0
1227 | 2022-10-03 20:27 | 19 | 25.9 | 0
1228 | 2022-10-03 20:28 | 18.9 | 26.4 | 0
1229 | 2022-10-03 20:29 | 18.8 | 26 | 0
1230 | 2022-10-03 20:30 | 18.7 | 25.8 | 0
1231 | 2022-10-03 20:31 | 18.5 | 25.4 | 0
1232 | 2022-10-03 20:32 | 18.8 | 25.6 | 0
1233 | 2022-10-03 20:33 | 18.6 | 26.3 | 0
1234 | 2022-10-03 20:34 | 18.5 | 25 | 0
1235 | 2022-10-03 20:35 | 18.6 | 25.6 | 0
1236 | 2022-10-03 20:36 | 18.5 | 25.4 | 0
1237 | 2022-10-03 20:37 | 18.4 | 25 | 0
1238 | 2022-10-03 20:38 | 18.5 | 25.8 | 0
1239 | 2022-10-03 20:39 | 18.6 | 26 | 0
1240 | 2022-10-03 20:40 | 18.6 | 24.9 | 0
1241 | 2022-10-03 20:41 | 18.3 | 25.5 | 0
1242 | 2022-10-03 20:42 | 18.4 | 24.8 | 0
1243 | 2022-10-03 20:43 | 18.7 | 25.2 | 0
1244 | 2022-10-03 20:44 | 18.6 | 25.8 | 0
1245 | 2022-10-03 20:45 | 18.4 | 25.8 | 0
1246 | 2022-10-03 20:46 | 18.4 | 25.3 | 0
1247 | 2022-10-03 20:47 | 18.3 | 25.4 | 0
1248 | 2022-10-03 20:48 | 18.2 | 25.5 | 0
1249 | 2022-10-03 20:49 | 18.1 | 25.3 | 0
1250 | 2022-10-03 20:50 | 18.1 | 25.4 | 0
1251 | 2022-10-03 20:51 | 18 | 25.6 | 0
1252 | 2022-10-03 20:52 | 18 | 25 | 0
1253 | 2022-10-03 20:53 | 18 | 25.5 | 0
1254 | 2022-10-03 20:54 | 18 | 25.3 | 0
1255 | 2022-10-03 20:55 | 18.1 | 25.4 | 0
1256 | 2022-10-03 20:56 | 18 | 25.3 | 0
1257 | 2022-10-03 20:57 | 17.9 | 25.4 | 0
1258 | 2022-10-03 20:58 | 18 | 25.4 | 0
1259 | 2022-10-03 20:59 | 17.9 | 25.2 | 0
1260 | 2022-10-03 21:00 | 17.9 | 25.6 | 0
1261 | 2022-10-03 21:01 | 17.9 | 25.7 | 0
1262 | 2022-10-03 21:02 | 17.7 | 25.6 | 0
1263 | 2022-10-03 21:03 | 17.7 | 25.4 | 0
1264 | 2022-10-03 21:04 | 17.7 | 25.4 | 0
1265 | 2022-10-03 21:05 | 17.8 | 25.1 | 0
1266 | 2022-10-03 21:06 | 17.8 | 24.9 | 0
1267 | 2022-10-03 21:07 | 17.8 | 25.8 | 0
1268 | 2022-10-03 21:08 | 17.7 | 26 | 0
1269 | 2022-10-03 21:09 | 17.7 | 25.7 | 0
1270 | 2022-10-03 21:10 | 17.7 | 25.4 | 0
1271 | 2022-10-03 21:11 | 17.7 | 25.3 | 0
1272 | 2022-10-03 21:12 | 17.7 | 25.6 | 0
1273 | 2022-10-03 21:13 | 17.6 | 25.6 | 0
1274 | 2022-10-03 21:14 | 17.9 | 25.2 | 0
1275 | 2022-10-03 21:15 | 18 | 25.2 | 0
1276 | 2022-10-03 21:16 | 17.9 | 25.4 | 0
1277 | 2022-10-03 21:17 | 18.1 | 26 | 0
1278 | 2022-10-03 21:18 | 18.2 | 25.8 | 0
1279 | 2022-10-03 21:19 | 18 | 25.2 | 0
1280 | 2022-10-03 21:20 | 18 | 25.8 | 0
1281 | 2022-10-03 21:21 | 18 | 24.6 | 0
1282 | 2022-10-03 21:22 | 18.1 | 24.9 | 0
1283 | 2022-10-03 21:23 | 18.4 | 25.7 | 0
1284 | 2022-10-03 21:24 | 18.6 | 25.6 | 0
1285 | 2022-10-03 21:25 | 18.3 | 25.2 | 0
1286 | 2022-10-03 21:26 | 18.6 | 25.4 | 0
1287 | 2022-10-03 21:27 | 18.9 | 25.2 | 0
1288 | 2022-10-03 21:28 | 18.8 | 25.3 | 0
1289 | 2022-10-03 21:29 | 18.9 | 25.2 | 0
1290 | 2022-10-03 21:30 | 18.7 | 25.3 | 0
1291 | 2022-10-03 21:31 | 18.6 | 26 | 0
1292 | 2022-10-03 21:32 | 18.4 | 25.8 | 0
1293 | 2022-10-03 21:33 | 18.3 | 26.1 | 0
1294 | 2022-10-03 21:34 | 18.5 | 26 | 0
1295 | 2022-10-03 21:35 | 18.7 | 25.4 | 0
1296 | 2022-10-03 21:36 | 18.5 | 24.9 | 0
1297 | 2022-10-03 21:37 | 18.7 | 25.8 | 0
1298 | 2022-10-03 21:38 | 18.8 | 25.3 | 0
1299 | 2022-10-03 21:39 | 18.6 | 25.2 | 0
1300 | 2022-10-03 21:40 | 18.6 | 25.2 | 0
1301 | 2022-10-03 21:41 | 18.6 | 25.3 | 0
1302 | 2022-10-03 21:42 | 18.4 | 25.4 | 0
1303 | 2022-10-03 21:43 | 18.7 | 25.4 | 0
1304 | 2022-10-03 21:44 | 18.7 | 25.5 | 0
1305 | 2022-10-03 21:45 | 18.6 | 25 | 0
1306 | 2022-10-03 21:46 | 18.6 | 25.4 | 0
1307 | 2022-10-03 21:47 | 18.4 | 25.6 | 0
1308 | 2022-10-03 21:48 | 18.5 | 25.4 | 0
1309 | 2022-10-03 21:49 | 18.5 | 25.1 | 0
1310 | 2022-10-03 21:50 | 18.4 | 25.7 | 0
1311 | 2022-10-03 21:51 | 18.4 | 25.4 | 0
1312 | 2022-10-03 21:52 | 18.4 | 25.4 | 0
1313 | 2022-10-03 21:53 | 18.3 | 25.4 | 0
1314 | 2022-10-03 21:54 | 18.1 | 25.2 | 0
1315 | 2022-10-03 21:55 | 18.1 | 25.2 | 0
1316 | 2022-10-03 21:56 | 18.2 | 25.2 | 0
1317 | 2022-10-03 21:57 | 18.2 | 25.2 | 0
1318 | 2022-10-03 21:58 | 18.1 | 25.3 | 0
1319 | 2022-10-03 21:59 | 18.1 | 25.4 | 0
1320 | 2022-10-03 22:00 | 18.2 | 25.1 | 0
1321 | 2022-10-03 22:01 | 18.3 | 25.3 | 0
1322 | 2022-10-03 22:02 | 18.3 | 25.4 | 0
1323 | 2022-10-03 22:03 | 18.3 | 25.3 | 0
1324 | 2022-10-03 22:04 | 18.3 | 25.3 | 0
1325 | 2022-10-03 22:05 | 18.5 | 25.2 | 0
1326 | 2022-10-03 22:06 | 18.3 | 25.4 | 0
1327 | 2022-10-03 22:07 | 18.4 | 25.3 | 0
1328 | 2022-10-03 22:08 | 18.3 | 25.3 | 0
1329 | 2022-10-03 22:09 | 18.2 | 25.3 | 0
1330 | 2022-10-03 22:10 | 18.4 | 25 | 0
1331 | 2022-10-03 22:11 | 18.4 | 25.2 | 0
1332 | 2022-10-03 22:12 | 18.5 | 25.3 | 0
1333 | 2022-10-03 22:13 | 18.5 | 26.2 | 0
1334 | 2022-10-03 22:14 | 18.3 | 25.3 | 0
1335 | 2022-10-03 22:15 | 18.5 | 25.4 | 0
1336 | 2022-10-03 22:16 | 18.4 | 25 | 0
1337 | 2022-10-03 22:17 | 18.5 | 24.8 | 0
1338 | 2022-10-03 22:18 | 18.8 | 25.6 | 0
1339 | 2022-10-03 22:19 | 18.9 | 24.9 | 0
1340 | 2022-10-03 22:20 | 19.2 | 25.3 | 0
1341 | 2022-10-03 22:21 | 19.3 | 24.9 | 0
1342 | 2022-10-03 22:22 | 19.1 | 25.4 | 0
1343 | 2022-10-03 22:23 | 18.8 | 25.4 | 0
1344 | 2022-10-03 22:24 | 18.6 | 25.4 | 0
1345 | 2022-10-03 22:25 | 18.7 | 25.2 | 0
1346 | 2022-10-03 22:26 | 18.4 | 25.3 | 0
1347 | 2022-10-03 22:27 | 18.3 | 25 | 0
1348 | 2022-10-03 22:28 | 18.4 | 25 | 0
1349 | 2022-10-03 22:29 | 18.5 | 25.2 | 0
1350 | 2022-10-03 22:30 | 18.5 | 25.2 | 0
1351 | 2022-10-03 22:31 | 18.3 | 25 | 0
1352 | 2022-10-03 22:32 | 18.3 | 24.8 | 0
1353 | 2022-10-03 22:33 | 18.1 | 25.4 | 0
1354 | 2022-10-03 22:34 | 18.2 | 25.1 | 0
1355 | 2022-10-03 22:35 | 18.2 | 25.2 | 0
1356 | 2022-10-03 22:36 | 18.2 | 25.1 | 0
1357 | 2022-10-03 22:37 | 17.9 | 25.1 | 0
1358 | 2022-10-03 22:38 | 17.9 | 25.3 | 0
1359 | 2022-10-03 22:39 | 17.8 | 25.2 | 0
1360 | 2022-10-03 22:40 | 17.8 | 25.2 | 0
1361 | 2022-10-03 22:41 | 17.9 | 25.3 | 0
1362 | 2022-10-03 22:42 | 17.8 | 25.1 | 0
1363 | 2022-10-03 22:43 | 17.7 | 25.2 | 0
1364 | 2022-10-03 22:44 | 17.8 | 25.1 | 0
1365 | 2022-10-03 22:45 | 17.6 | 25.1 | 0
1366 | 2022-10-03 22:46 | 17.7 | 25.1 | 0
1367 | 2022-10-03 22:47 | 17.6 | 25.6 | 0
1368 | 2022-10-03 22:48 | 17.7 | 25.2 | 0
1369 | 2022-10-03 22:49 | 17.5 | 25 | 0
1370 | 2022-10-03 22:50 | 17.5 | 25.4 | 0
1371 | 2022-10-03 22:51 | 17.5 | 25.1 | 0
1372 | 2022-10-03 22:52 | 17.6 | 25.2 | 0
1373 | 2022-10-03 22:53 | 17.5 | 25.1 | 0
1374 | 2022-10-03 22:54 | 17.6 | 25.3 | 0
1375 | 2022-10-03 22:55 | 17.6 | 25.3 | 0
1376 | 2022-10-03 22:56 | 17.5 | 25.1 | 0
1377 | 2022-10-03 22:57 | 17.4 | 24.9 | 0
1378 | 2022-10-03 22:58 | 17.5 | 25.1 | 0
1379 | 2022-10-03 22:59 | 17.4 | 25.4 | 0
1380 | 2022-10-03 23:00 | 17.4 | 25.1 | 0
1381 | 2022-10-03 23:01 | 17.4 | 25.2 | 0
1382 | 2022-10-03 23:02 | 17.4 | 25.2 | 0
1383 | 2022-10-03 23:03 | 17.3 | 25.3 | 0
1384 | 2022-10-03 23:04 | 17.2 | 25.2 | 0
1385 | 2022-10-03 23:05 | 17.1 | 25.1 | 0
1386 | 2022-10-03 23:06 | 17.1 | 25 | 0
1387 | 2022-10-03 23:07 | 17.2 | 25.4 | 0
1388 | 2022-10-03 23:08 | 17 | 25.2 | 0
1389 | 2022-10-03 23:09 | 17.1 | 25.2 | 0
1390 | 2022-10-03 23:10 | 17.2 | 25.2 | 0
1391 | 2022-10-03 23:11 | 17.2 | 24.8 | 0
1392 | 2022-10-03 23:12 | 17.1 | 24.5 | 0
1393 | 2022-10-03 23:13 | 17.1 | 24.5 | 0
1394 | 2022-10-03 23:14 | 17.1 | 25.3 | 0
1395 | 2022-10-03 23:15 | 17.1 | 25 | 0
1396 | 2022-10-03 23:16 | 17.1 | 25.2 | 0
1397 | 2022-10-03 23:17 | 17.3 | 25 | 0
1398 | 2022-10-03 23:18 | 17.3 | 25.1 | 0
1399 | 2022-10-03 23:19 | 17.2 | 25.2 | 0
1400 | 2022-10-03 23:20 | 17.3 | 25.2 | 0
1401 | 2022-10-03 23:21 | 17.5 | 24.7 | 0
1402 | 2022-10-03 23:22 | 17.6 | 25.4 | 0
1403 | 2022-10-03 23:23 | 17.5 | 25 | 0
1404 | 2022-10-03 23:24 | 17.5 | 25.1 | 0
1405 | 2022-10-03 23:25 | 17.3 | 24.9 | 0
1406 | 2022-10-03 23:26 | 17.3 | 25.2 | 0
1407 | 2022-10-03 23:27 | 17.1 | 25.2 | 0
1408 | 2022-10-03 23:28 | 17.1 | 25.1 | 0
1409 | 2022-10-03 23:29 | 17.3 | 25.3 | 0
1410 | 2022-10-03 23:30 | 17.4 | 25.3 | 0
1411 | 2022-10-03 23:31 | 17.2 | 25.1 | 0
1412 | 2022-10-03 23:32 | 17.3 | 24.4 | 0
1413 | 2022-10-03 23:33 | 17.2 | 25.5 | 0
1414 | 2022-10-03 23:34 | 17.2 | 25.7 | 0
1415 | 2022-10-03 23:35 | 17.1 | 24.8 | 0
1416 | 2022-10-03 23:36 | 17.1 | 24.9 | 0
1417 | 2022-10-03 23:37 | 16.9 | 25 | 0
1418 | 2022-10-03 23:38 | 17 | 25.3 | 0
1419 | 2022-10-03 23:39 | 17 | 25.2 | 0
1420 | 2022-10-03 23:40 | 16.9 | 24.9 | 0
1421 | 2022-10-03 23:41 | 16.8 | 25.1 | 0
1422 | 2022-10-03 23:42 | 17 | 25.2 | 0
1423 | 2022-10-03 23:43 | 17 | 25.3 | 0
1424 | 2022-10-03 23:44 | 16.9 | 25.2 | 0
1425 | 2022-10-03 23:45 | 17.1 | 25 | 0
1426 | 2022-10-03 23:46 | 16.8 | 24.5 | 0
1427 | 2022-10-03 23:47 | 16.9 | 25.6 | 0
1428 | 2022-10-03 23:48 | 16.8 | 25.3 | 0
1429 | 2022-10-03 23:49 | 16.9 | 24.8 | 0
1430 | 2022-10-03 23:50 | 16.9 | 25.1 | 0
1431 | 2022-10-03 23:51 | 16.9 | 25.6 | 0
1432 | 2022-10-03 23:52 | 16.8 | 25.5 | 0
1433 | 2022-10-03 23:53 | 16.7 | 24.8 | 0
1434 | 2022-10-03 23:54 | 16.7 | 25.2 | 0
1435 | 2022-10-03 23:55 | 16.8 | 25 | 0
1436 | 2022-10-03 23:56 | 16.6 | 25.2 | 0
1437 | 2022-10-03 23:57 | 16.7 | 24.9 | 0
1438 | 2022-10-03 23:58 | 16.8 | 25.3 | 0
1439 | 2022-10-03 23:59 | 16.7 | 25.3 | 0

## 04-10-2022_NO HEAT
| Date&time_x | OUTDOOR_TEMP | INDOOR_TEMP | PYRANOMETER
0 | 2022-10-04 | 16.9 | 25.2 | 0
1 | 2022-10-04 00:01 | 16.7 | 25.2 | 0
2 | 2022-10-04 00:02 | 16.6 | 25.2 | 0
3 | 2022-10-04 00:03 | 16.7 | 25 | 0
4 | 2022-10-04 00:04 | 16.6 | 25.2 | 0
5 | 2022-10-04 00:05 | 16.6 | 25.1 | 0
6 | 2022-10-04 00:06 | 16.7 | 25 | 0
7 | 2022-10-04 00:07 | 16.7 | 25.2 | 0
8 | 2022-10-04 00:08 | 16.7 | 24.9 | 0
9 | 2022-10-04 00:09 | 16.5 | 25 | 0
10 | 2022-10-04 00:10 | 16.5 | 24.8 | 0
11 | 2022-10-04 00:11 | 16.5 | 25.1 | 0
12 | 2022-10-04 00:12 | 16.9 | 24.8 | 0
13 | 2022-10-04 00:13 | 16.9 | 25.8 | 0
14 | 2022-10-04 00:14 | 16.9 | 24.6 | 0
15 | 2022-10-04 00:15 | 16.8 | 24.8 | 0
16 | 2022-10-04 00:16 | 16.9 | 24.7 | 0
17 | 2022-10-04 00:17 | 16.7 | 25.5 | 0
18 | 2022-10-04 00:18 | 16.8 | 24.9 | 0
19 | 2022-10-04 00:19 | 16.7 | 25.4 | 0
20 | 2022-10-04 00:20 | 16.7 | 25.9 | 0
21 | 2022-10-04 00:21 | 16.8 | 24.8 | 0
22 | 2022-10-04 00:22 | 16.6 | 25.2 | 0
23 | 2022-10-04 00:23 | 16.6 | 25 | 0
24 | 2022-10-04 00:24 | 16.6 | 25 | 0
25 | 2022-10-04 00:25 | 16.7 | 24.9 | 0
26 | 2022-10-04 00:26 | 16.7 | 24.9 | 0
27 | 2022-10-04 00:27 | 16.8 | 25 | 0
28 | 2022-10-04 00:28 | 16.7 | 25.2 | 0
29 | 2022-10-04 00:29 | 16.8 | 24.7 | 0
30 | 2022-10-04 00:30 | 16.6 | 24.9 | 0
31 | 2022-10-04 00:31 | 16.9 | 25.2 | 0
32 | 2022-10-04 00:32 | 16.7 | 24.4 | 0
33 | 2022-10-04 00:33 | 16.8 | 25 | 0
34 | 2022-10-04 00:34 | 16.9 | 24.1 | 0
35 | 2022-10-04 00:35 | 16.6 | 24.5 | 0
36 | 2022-10-04 00:36 | 16.6 | 24.8 | 0
37 | 2022-10-04 00:37 | 16.6 | 24.8 | 0
38 | 2022-10-04 00:38 | 16.5 | 25 | 0
39 | 2022-10-04 00:39 | 16.5 | 24.9 | 0
40 | 2022-10-04 00:40 | 16.7 | 24.8 | 0
41 | 2022-10-04 00:41 | 16.9 | 25 | 0
42 | 2022-10-04 00:42 | 17 | 25.1 | 0
43 | 2022-10-04 00:43 | 17.3 | 24.7 | 0
44 | 2022-10-04 00:44 | 18.4 | 25.1 | 0
45 | 2022-10-04 00:45 | 18.6 | 24.3 | 0
46 | 2022-10-04 00:46 | 17.9 | 24.9 | 0
47 | 2022-10-04 00:47 | 17.7 | 25.1 | 0
48 | 2022-10-04 00:48 | 17.5 | 24.1 | 0
49 | 2022-10-04 00:49 | 17.4 | 25.5 | 0
50 | 2022-10-04 00:50 | 17.5 | 25 | 0
51 | 2022-10-04 00:51 | 18.7 | 24.8 | 0
52 | 2022-10-04 00:52 | 18.4 | 24.4 | 0
53 | 2022-10-04 00:53 | 18.3 | 25.2 | 0
54 | 2022-10-04 00:54 | 18 | 24.8 | 0
55 | 2022-10-04 00:55 | 17.9 | 24.8 | 0
56 | 2022-10-04 00:56 | 18.1 | 25.4 | 0
57 | 2022-10-04 00:57 | 18.2 | 25.7 | 0
58 | 2022-10-04 00:58 | 18.3 | 24.4 | 0
59 | 2022-10-04 00:59 | 18.1 | 24.2 | 0
60 | 2022-10-04 01:00 | 17.9 | 24.7 | 0
61 | 2022-10-04 01:01 | 18.1 | 25.1 | 0
62 | 2022-10-04 01:02 | 18 | 24.9 | 0
63 | 2022-10-04 01:03 | 18.2 | 25 | 0
64 | 2022-10-04 01:04 | 18.7 | 24.9 | 0
65 | 2022-10-04 01:05 | 19 | 25 | 0
66 | 2022-10-04 01:06 | 19.5 | 24.9 | 0
67 | 2022-10-04 01:07 | 19.5 | 24.9 | 0
68 | 2022-10-04 01:08 | 19.7 | 24.9 | 0
69 | 2022-10-04 01:09 | 19.7 | 24.9 | 0
70 | 2022-10-04 01:10 | 19.6 | 25 | 0
71 | 2022-10-04 01:11 | 19.7 | 25 | 0
72 | 2022-10-04 01:12 | 19.8 | 24.9 | 0
73 | 2022-10-04 01:13 | 19.8 | 25 | 0
74 | 2022-10-04 01:14 | 19.6 | 24.9 | 0
75 | 2022-10-04 01:15 | 19.6 | 24.8 | 0
76 | 2022-10-04 01:16 | 19.6 | 25 | 0
77 | 2022-10-04 01:17 | 19.8 | 24.7 | 0
78 | 2022-10-04 01:18 | 19.5 | 24.8 | 0
79 | 2022-10-04 01:19 | 19.5 | 25.1 | 0
80 | 2022-10-04 01:20 | 19.3 | 25.2 | 0
81 | 2022-10-04 01:21 | 19.1 | 24.9 | 0
82 | 2022-10-04 01:22 | 18.8 | 24.9 | 0
83 | 2022-10-04 01:23 | 19 | 24.9 | 0
84 | 2022-10-04 01:24 | 19.4 | 24.6 | 0
85 | 2022-10-04 01:25 | 18.9 | 24.5 | 0
86 | 2022-10-04 01:26 | 18.9 | 25 | 0
87 | 2022-10-04 01:27 | 18.9 | 25 | 0
88 | 2022-10-04 01:28 | 19 | 25.1 | 0
89 | 2022-10-04 01:29 | 19.5 | 24.7 | 0
90 | 2022-10-04 01:30 | 19.5 | 25.4 | 0
91 | 2022-10-04 01:31 | 19.5 | 25 | 0
92 | 2022-10-04 01:32 | 19.6 | 25.6 | 0
93 | 2022-10-04 01:33 | 19.4 | 25.1 | 0
94 | 2022-10-04 01:34 | 19.1 | 25.1 | 0
95 | 2022-10-04 01:35 | 19 | 24.9 | 0
96 | 2022-10-04 01:36 | 19 | 24.3 | 0
97 | 2022-10-04 01:37 | 18.9 | 24.8 | 0
98 | 2022-10-04 01:38 | 19 | 24.8 | 0
99 | 2022-10-04 01:39 | 18.9 | 24.6 | 0
100 | 2022-10-04 01:40 | 19 | 25.2 | 0
101 | 2022-10-04 01:41 | 19.3 | 24.5 | 0
102 | 2022-10-04 01:42 | 19.4 | 25 | 0
103 | 2022-10-04 01:43 | 19.4 | 24.9 | 0
104 | 2022-10-04 01:44 | 19.3 | 25.6 | 0
105 | 2022-10-04 01:45 | 19 | 25.6 | 0
106 | 2022-10-04 01:46 | 18.9 | 25.4 | 0
107 | 2022-10-04 01:47 | 19.1 | 24.2 | 0
108 | 2022-10-04 01:48 | 19 | 24.1 | 0
109 | 2022-10-04 01:49 | 18.9 | 25.1 | 0
110 | 2022-10-04 01:50 | 18.6 | 25.6 | 0
111 | 2022-10-04 01:51 | 18.9 | 25 | 0
112 | 2022-10-04 01:52 | 18.9 | 24.6 | 0
113 | 2022-10-04 01:53 | 19.1 | 25.6 | 0
114 | 2022-10-04 01:54 | 18.9 | 24.5 | 0
115 | 2022-10-04 01:55 | 19.2 | 24.9 | 0
116 | 2022-10-04 01:56 | 19.3 | 24.6 | 0
117 | 2022-10-04 01:57 | 19 | 24.5 | 0
118 | 2022-10-04 01:58 | 19.3 | 24.6 | 0
119 | 2022-10-04 01:59 | 19.4 | 25.8 | 0
120 | 2022-10-04 02:00 | 19.3 | 25.3 | 0
121 | 2022-10-04 02:01 | 19.2 | 25 | 0
122 | 2022-10-04 02:02 | 19.1 | 24.8 | 0
123 | 2022-10-04 02:03 | 19.2 | 24.9 | 0
124 | 2022-10-04 02:04 | 19.2 | 24.8 | 0
125 | 2022-10-04 02:05 | 18.8 | 24.9 | 0
126 | 2022-10-04 02:06 | 18.7 | 24.8 | 0
127 | 2022-10-04 02:07 | 18.5 | 24.9 | 0
128 | 2022-10-04 02:08 | 18.2 | 24.8 | 0
129 | 2022-10-04 02:09 | 18.2 | 24.9 | 0
130 | 2022-10-04 02:10 | 18.6 | 24.8 | 0
131 | 2022-10-04 02:11 | 18.5 | 25 | 0
132 | 2022-10-04 02:12 | 18.7 | 25.1 | 0
133 | 2022-10-04 02:13 | 18.7 | 24.9 | 0
134 | 2022-10-04 02:14 | 18.6 | 25.1 | 0
135 | 2022-10-04 02:15 | 18.7 | 24.7 | 0
136 | 2022-10-04 02:16 | 18.7 | 25.1 | 0
137 | 2022-10-04 02:17 | 18.8 | 24.5 | 0
138 | 2022-10-04 02:18 | 18.8 | 24.2 | 0
139 | 2022-10-04 02:19 | 18.7 | 25.5 | 0
140 | 2022-10-04 02:20 | 18.9 | 24.7 | 0
141 | 2022-10-04 02:21 | 19 | 25.4 | 0
142 | 2022-10-04 02:22 | 19.2 | 25.4 | 0
143 | 2022-10-04 02:23 | 19 | 24.4 | 0
144 | 2022-10-04 02:24 | 19 | 24.2 | 0
145 | 2022-10-04 02:25 | 18.9 | 24.1 | 0
146 | 2022-10-04 02:26 | 19 | 24.7 | 0
147 | 2022-10-04 02:27 | 18.9 | 25.4 | 0
148 | 2022-10-04 02:28 | 18.9 | 24.6 | 0
149 | 2022-10-04 02:29 | 18.8 | 25.1 | 0
150 | 2022-10-04 02:30 | 18.9 | 24.7 | 0
151 | 2022-10-04 02:31 | 18.9 | 24.8 | 0
152 | 2022-10-04 02:32 | 18.9 | 24.5 | 0
153 | 2022-10-04 02:33 | 18.8 | 25.3 | 0
154 | 2022-10-04 02:34 | 18.5 | 25.2 | 0
155 | 2022-10-04 02:35 | 18.6 | 25.2 | 0
156 | 2022-10-04 02:36 | 18.4 | 25 | 0
157 | 2022-10-04 02:37 | 18.8 | 25.1 | 0
158 | 2022-10-04 02:38 | 18.9 | 24.9 | 0
159 | 2022-10-04 02:39 | 18.8 | 24.8 | 0
160 | 2022-10-04 02:40 | 18.8 | 25.1 | 0
161 | 2022-10-04 02:41 | 18.8 | 24.7 | 0
162 | 2022-10-04 02:42 | 18.9 | 25.1 | 0
163 | 2022-10-04 02:43 | 18.8 | 25.1 | 0
164 | 2022-10-04 02:44 | 18.6 | 25 | 0
165 | 2022-10-04 02:45 | 18.6 | 25.1 | 0
166 | 2022-10-04 02:46 | 18.7 | 24.3 | 0
167 | 2022-10-04 02:47 | 18.6 | 24.9 | 0
168 | 2022-10-04 02:48 | 18.6 | 24.9 | 0
169 | 2022-10-04 02:49 | 18.5 | 24.8 | 0
170 | 2022-10-04 02:50 | 18.5 | 24.8 | 0
171 | 2022-10-04 02:51 | 18.2 | 24.6 | 0
172 | 2022-10-04 02:52 | 18.3 | 24.7 | 0
173 | 2022-10-04 02:53 | 18.6 | 24.9 | 0
174 | 2022-10-04 02:54 | 18.3 | 24.8 | 0
175 | 2022-10-04 02:55 | 18.5 | 24.5 | 0
176 | 2022-10-04 02:56 | 18.5 | 25 | 0
177 | 2022-10-04 02:57 | 18.3 | 24.2 | 0
178 | 2022-10-04 02:58 | 18.5 | 25.1 | 0
179 | 2022-10-04 02:59 | 18.4 | 24.3 | 0
180 | 2022-10-04 03:00 | 18.5 | 25.1 | 0
181 | 2022-10-04 03:01 | 18.4 | 24.8 | 0
182 | 2022-10-04 03:02 | 18.4 | 24.9 | 0
183 | 2022-10-04 03:03 | 18.5 | 24.8 | 0
184 | 2022-10-04 03:04 | 18.5 | 24.7 | 0
185 | 2022-10-04 03:05 | 18.2 | 24.7 | 0
186 | 2022-10-04 03:06 | 18.2 | 24.9 | 0
187 | 2022-10-04 03:07 | 18.4 | 24.8 | 0
188 | 2022-10-04 03:08 | 18.3 | 25.5 | 0
189 | 2022-10-04 03:09 | 18.5 | 25.2 | 0
190 | 2022-10-04 03:10 | 18.7 | 23.9 | 0
191 | 2022-10-04 03:11 | 18.6 | 24.6 | 0
192 | 2022-10-04 03:12 | 18.6 | 23.9 | 0
193 | 2022-10-04 03:13 | 18.6 | 24 | 0
194 | 2022-10-04 03:14 | 18.5 | 24.6 | 0
195 | 2022-10-04 03:15 | 18.4 | 24.5 | 0
196 | 2022-10-04 03:16 | 18.5 | 25 | 0
197 | 2022-10-04 03:17 | 18.6 | 25.5 | 0
198 | 2022-10-04 03:18 | 18.8 | 25.5 | 0
199 | 2022-10-04 03:19 | 18.8 | 25.1 | 0
200 | 2022-10-04 03:20 | 18.8 | 24.6 | 0
201 | 2022-10-04 03:21 | 18.8 | 25 | 0
202 | 2022-10-04 03:22 | 18.8 | 25.2 | 0
203 | 2022-10-04 03:23 | 18.9 | 24.9 | 0
204 | 2022-10-04 03:24 | 18.8 | 24.8 | 0
205 | 2022-10-04 03:25 | 19 | 25.4 | 0
206 | 2022-10-04 03:26 | 18.9 | 25.2 | 0
207 | 2022-10-04 03:27 | 18.9 | 25.5 | 0
208 | 2022-10-04 03:28 | 18.9 | 25 | 0
209 | 2022-10-04 03:29 | 18.8 | 24.1 | 0
210 | 2022-10-04 03:30 | 19 | 24.2 | 0
211 | 2022-10-04 03:31 | 18.9 | 24.7 | 0
212 | 2022-10-04 03:32 | 19 | 24.8 | 0
213 | 2022-10-04 03:33 | 19 | 24.4 | 0
214 | 2022-10-04 03:34 | 19 | 24.6 | 0
215 | 2022-10-04 03:35 | 18.9 | 25 | 0
216 | 2022-10-04 03:36 | 18.9 | 24.9 | 0
217 | 2022-10-04 03:37 | 18.8 | 25 | 0
218 | 2022-10-04 03:38 | 18.9 | 24.8 | 0
219 | 2022-10-04 03:39 | 19 | 25.6 | 0
220 | 2022-10-04 03:40 | 19 | 25 | 0
221 | 2022-10-04 03:41 | 18.8 | 24.4 | 0
222 | 2022-10-04 03:42 | 18.9 | 24.9 | 0
223 | 2022-10-04 03:43 | 19 | 24.5 | 0
224 | 2022-10-04 03:44 | 18.9 | 24.6 | 0
225 | 2022-10-04 03:45 | 18.8 | 25 | 0
226 | 2022-10-04 03:46 | 18.9 | 24.4 | 0
227 | 2022-10-04 03:47 | 18.9 | 24.5 | 0
228 | 2022-10-04 03:48 | 18.9 | 24.8 | 0
229 | 2022-10-04 03:49 | 18.9 | 24.6 | 0
230 | 2022-10-04 03:50 | 18.9 | 24.7 | 0
231 | 2022-10-04 03:51 | 19.1 | 25.1 | 0
232 | 2022-10-04 03:52 | 19 | 25.3 | 0
233 | 2022-10-04 03:53 | 19 | 25.4 | 0
234 | 2022-10-04 03:54 | 18.9 | 24.6 | 0
235 | 2022-10-04 03:55 | 18.9 | 24.4 | 0
236 | 2022-10-04 03:56 | 18.9 | 25.3 | 0
237 | 2022-10-04 03:57 | 18.7 | 25.1 | 0
238 | 2022-10-04 03:58 | 18.7 | 24.6 | 0
239 | 2022-10-04 03:59 | 18.8 | 25 | 0
240 | 2022-10-04 04:00 | 18.8 | 24.7 | 0
241 | 2022-10-04 04:01 | 18.8 | 25.1 | 0
242 | 2022-10-04 04:02 | 18.9 | 24.7 | 0
243 | 2022-10-04 04:03 | 18.8 | 24.7 | 0
244 | 2022-10-04 04:04 | 18.8 | 24.8 | 0
245 | 2022-10-04 04:05 | 18.9 | 24.8 | 0
246 | 2022-10-04 04:06 | 18.8 | 24.4 | 0
247 | 2022-10-04 04:07 | 19 | 24.9 | 0
248 | 2022-10-04 04:08 | 18.8 | 24.9 | 0
249 | 2022-10-04 04:09 | 18.9 | 24.5 | 0
250 | 2022-10-04 04:10 | 18.8 | 25 | 0
251 | 2022-10-04 04:11 | 18.8 | 24.8 | 0
252 | 2022-10-04 04:12 | 18.8 | 24.4 | 0
253 | 2022-10-04 04:13 | 18.7 | 25.2 | 0
254 | 2022-10-04 04:14 | 18.7 | 24.2 | 0
255 | 2022-10-04 04:15 | 18.8 | 24.4 | 0
256 | 2022-10-04 04:16 | 18.8 | 23.9 | 0
257 | 2022-10-04 04:17 | 18.6 | 23.9 | 0
258 | 2022-10-04 04:18 | 18.6 | 24 | 0
259 | 2022-10-04 04:19 | 18.6 | 24 | 0
260 | 2022-10-04 04:20 | 18.6 | 24.8 | 0
261 | 2022-10-04 04:21 | 18.6 | 24.2 | 0
262 | 2022-10-04 04:22 | 18.8 | 24.6 | 0
263 | 2022-10-04 04:23 | 18.6 | 25 | 0
264 | 2022-10-04 04:24 | 18.8 | 24.2 | 0
265 | 2022-10-04 04:25 | 18.5 | 24.7 | 0
266 | 2022-10-04 04:26 | 18.6 | 24.2 | 0
267 | 2022-10-04 04:27 | 18.5 | 24.4 | 0
268 | 2022-10-04 04:28 | 18.5 | 23.9 | 0
269 | 2022-10-04 04:29 | 18.5 | 24 | 0
270 | 2022-10-04 04:30 | 18.5 | 24.8 | 0
271 | 2022-10-04 04:31 | 18.7 | 24.3 | 0
272 | 2022-10-04 04:32 | 18.6 | 25.3 | 0
273 | 2022-10-04 04:33 | 18.4 | 25.1 | 0
274 | 2022-10-04 04:34 | 18.5 | 24.7 | 0
275 | 2022-10-04 04:35 | 18.5 | 24.2 | 0
276 | 2022-10-04 04:36 | 18.3 | 25.1 | 0
277 | 2022-10-04 04:37 | 18.4 | 25.4 | 0
278 | 2022-10-04 04:38 | 18.5 | 25.4 | 0
279 | 2022-10-04 04:39 | 18.5 | 23.8 | 0
280 | 2022-10-04 04:40 | 18.3 | 24.4 | 0
281 | 2022-10-04 04:41 | 18.3 | 24.3 | 0
282 | 2022-10-04 04:42 | 18.3 | 24.9 | 0
283 | 2022-10-04 04:43 | 18.5 | 24 | 0
284 | 2022-10-04 04:44 | 18.5 | 24.5 | 0
285 | 2022-10-04 04:45 | 18.4 | 24.4 | 0
286 | 2022-10-04 04:46 | 18.3 | 24.8 | 0
287 | 2022-10-04 04:47 | 18.3 | 24.7 | 0
288 | 2022-10-04 04:48 | 18.5 | 24.3 | 0
289 | 2022-10-04 04:49 | 18.4 | 25 | 0
290 | 2022-10-04 04:50 | 18.4 | 24.3 | 0
291 | 2022-10-04 04:51 | 18.5 | 25.1 | 0
292 | 2022-10-04 04:52 | 18.6 | 25.3 | 0
293 | 2022-10-04 04:53 | 18.7 | 24.5 | 0
294 | 2022-10-04 04:54 | 18.7 | 23.7 | 0
295 | 2022-10-04 04:55 | 18.5 | 24.3 | 0
296 | 2022-10-04 04:56 | 18.5 | 25.3 | 0
297 | 2022-10-04 04:57 | 18.6 | 24.4 | 0
298 | 2022-10-04 04:58 | 18.5 | 23.8 | 0
299 | 2022-10-04 04:59 | 18.4 | 25 | 0
300 | 2022-10-04 05:00 | 18.4 | 24 | 0
301 | 2022-10-04 05:01 | 18.3 | 24.7 | 0
302 | 2022-10-04 05:02 | 18.4 | 24.8 | 0
303 | 2022-10-04 05:03 | 18.4 | 24.7 | 0
304 | 2022-10-04 05:04 | 18.4 | 24.7 | 0
305 | 2022-10-04 05:05 | 18.3 | 25.2 | 0
306 | 2022-10-04 05:06 | 18.5 | 25.1 | 0
307 | 2022-10-04 05:07 | 18.4 | 24.1 | 0
308 | 2022-10-04 05:08 | 18.6 | 23.9 | 0
309 | 2022-10-04 05:09 | 18.4 | 24.9 | 0
310 | 2022-10-04 05:10 | 18.4 | 25.5 | 0
311 | 2022-10-04 05:11 | 18.6 | 24.3 | 0
312 | 2022-10-04 05:12 | 18.4 | 24.1 | 0
313 | 2022-10-04 05:13 | 18.3 | 25.4 | 0
314 | 2022-10-04 05:14 | 18.4 | 25.3 | 0
315 | 2022-10-04 05:15 | 18.5 | 24.4 | 0
316 | 2022-10-04 05:16 | 18.3 | 24.4 | 0
317 | 2022-10-04 05:17 | 18.3 | 25.5 | 0
318 | 2022-10-04 05:18 | 18.2 | 24.5 | 0
319 | 2022-10-04 05:19 | 18.4 | 25.4 | 0
320 | 2022-10-04 05:20 | 18.3 | 24 | 0
321 | 2022-10-04 05:21 | 18.4 | 24.1 | 0
322 | 2022-10-04 05:22 | 18.2 | 24.4 | 0
323 | 2022-10-04 05:23 | 18.4 | 24.3 | 0
324 | 2022-10-04 05:24 | 18.2 | 25 | 0
325 | 2022-10-04 05:25 | 18.3 | 24.6 | 0
326 | 2022-10-04 05:26 | 18.3 | 24.8 | 0
327 | 2022-10-04 05:27 | 18.2 | 24.8 | 0
328 | 2022-10-04 05:28 | 18.2 | 25.4 | 0
329 | 2022-10-04 05:29 | 18.2 | 25.4 | 0
330 | 2022-10-04 05:30 | 18.3 | 24.1 | 0
331 | 2022-10-04 05:31 | 18.1 | 24.1 | 0
332 | 2022-10-04 05:32 | 18.2 | 24.7 | 0
333 | 2022-10-04 05:33 | 18.2 | 24.1 | 0
334 | 2022-10-04 05:34 | 18.2 | 25.3 | 0
335 | 2022-10-04 05:35 | 17.9 | 24.2 | 0
336 | 2022-10-04 05:36 | 18.1 | 23.8 | 0
337 | 2022-10-04 05:37 | 17.9 | 24.3 | 0
338 | 2022-10-04 05:38 | 17.9 | 24.5 | 0
339 | 2022-10-04 05:39 | 17.9 | 24.2 | 0
340 | 2022-10-04 05:40 | 17.9 | 24.1 | 0
341 | 2022-10-04 05:41 | 17.9 | 24.9 | 0
342 | 2022-10-04 05:42 | 18 | 24.1 | 0
343 | 2022-10-04 05:43 | 18 | 25.4 | 0
344 | 2022-10-04 05:44 | 18 | 25.6 | 0
345 | 2022-10-04 05:45 | 17.9 | 25.5 | 0
346 | 2022-10-04 05:46 | 17.8 | 24.1 | 0
347 | 2022-10-04 05:47 | 17.9 | 23.7 | 0
348 | 2022-10-04 05:48 | 17.9 | 24.7 | 0
349 | 2022-10-04 05:49 | 17.8 | 24.5 | 0
350 | 2022-10-04 05:50 | 17.8 | 25.2 | 0
351 | 2022-10-04 05:51 | 17.7 | 24.2 | 0
352 | 2022-10-04 05:52 | 17.7 | 24.7 | 0
353 | 2022-10-04 05:53 | 17.8 | 24.4 | 0
354 | 2022-10-04 05:54 | 17.7 | 24.5 | 0
355 | 2022-10-04 05:55 | 17.7 | 24.2 | 0
356 | 2022-10-04 05:56 | 17.7 | 24.5 | 0
357 | 2022-10-04 05:57 | 17.8 | 24.2 | 0
358 | 2022-10-04 05:58 | 17.7 | 24.6 | 0
359 | 2022-10-04 05:59 | 17.7 | 24.3 | 0
360 | 2022-10-04 06:00 | 17.6 | 24.6 | 0
361 | 2022-10-04 06:01 | 17.6 | 24.4 | 0
362 | 2022-10-04 06:02 | 17.6 | 24.2 | 0
363 | 2022-10-04 06:03 | 17.6 | 24.6 | 0
364 | 2022-10-04 06:04 | 17.6 | 24.6 | 0
365 | 2022-10-04 06:05 | 17.6 | 24.5 | 0
366 | 2022-10-04 06:06 | 17.6 | 24.6 | 0
367 | 2022-10-04 06:07 | 17.8 | 24.3 | 0
368 | 2022-10-04 06:08 | 17.6 | 24.6 | 0
369 | 2022-10-04 06:09 | 17.6 | 24.4 | 0
370 | 2022-10-04 06:10 | 17.7 | 24.5 | 0
371 | 2022-10-04 06:11 | 17.6 | 24.4 | 0
372 | 2022-10-04 06:12 | 17.7 | 24.4 | 0
373 | 2022-10-04 06:13 | 17.6 | 24.4 | 0
374 | 2022-10-04 06:14 | 17.6 | 24.6 | 0
375 | 2022-10-04 06:15 | 17.6 | 25.3 | 0
376 | 2022-10-04 06:16 | 17.5 | 24.7 | 0
377 | 2022-10-04 06:17 | 17.6 | 25.3 | 0
378 | 2022-10-04 06:18 | 17.4 | 24.4 | 0
379 | 2022-10-04 06:19 | 17.4 | 24.4 | 0
380 | 2022-10-04 06:20 | 17.3 | 24 | 0
381 | 2022-10-04 06:21 | 17.5 | 24.7 | 0
382 | 2022-10-04 06:22 | 17.6 | 24.4 | 0
383 | 2022-10-04 06:23 | 17.5 | 24.3 | 0
384 | 2022-10-04 06:24 | 17.4 | 24.6 | 0
385 | 2022-10-04 06:25 | 17.5 | 24.7 | 0
386 | 2022-10-04 06:26 | 17.4 | 24.3 | 0
387 | 2022-10-04 06:27 | 17.4 | 24.3 | 0
388 | 2022-10-04 06:28 | 17.6 | 25.3 | 0
389 | 2022-10-04 06:29 | 17.5 | 24.4 | 0
390 | 2022-10-04 06:30 | 17.5 | 24.3 | 0
391 | 2022-10-04 06:31 | 17.4 | 24.4 | 0
392 | 2022-10-04 06:32 | 17.3 | 24.2 | 0
393 | 2022-10-04 06:33 | 17.3 | 24.6 | 0
394 | 2022-10-04 06:34 | 17.4 | 24.9 | 0
395 | 2022-10-04 06:35 | 17.5 | 24.6 | 0
396 | 2022-10-04 06:36 | 17.3 | 23.9 | 0
397 | 2022-10-04 06:37 | 17.5 | 24.1 | 0
398 | 2022-10-04 06:38 | 17.4 | 24.2 | 0
399 | 2022-10-04 06:39 | 17.5 | 24.6 | 0
400 | 2022-10-04 06:40 | 17.3 | 24.3 | 0
401 | 2022-10-04 06:41 | 17.5 | 24.4 | 0
402 | 2022-10-04 06:42 | 17.3 | 24.2 | 0
403 | 2022-10-04 06:43 | 17.4 | 24.5 | 0
404 | 2022-10-04 06:44 | 17.4 | 24.3 | 0
405 | 2022-10-04 06:45 | 17.2 | 24.6 | 0
406 | 2022-10-04 06:46 | 17.3 | 24.3 | 0
407 | 2022-10-04 06:47 | 17.1 | 24.1 | 0
408 | 2022-10-04 06:48 | 17.1 | 24.7 | 0
409 | 2022-10-04 06:49 | 17.2 | 24.6 | 0
410 | 2022-10-04 06:50 | 17.2 | 23.6 | 0
411 | 2022-10-04 06:51 | 17 | 24.2 | 0
412 | 2022-10-04 06:52 | 17 | 24.5 | 0
413 | 2022-10-04 06:53 | 17 | 24.6 | 0
414 | 2022-10-04 06:54 | 17.1 | 24.5 | 0
415 | 2022-10-04 06:55 | 16.9 | 24.6 | 0
416 | 2022-10-04 06:56 | 16.9 | 24.3 | 0
417 | 2022-10-04 06:57 | 17.1 | 24.3 | 0
418 | 2022-10-04 06:58 | 17.1 | 23.6 | 0
419 | 2022-10-04 06:59 | 16.9 | 24.1 | 0
420 | 2022-10-04 07:00 | 16.8 | 24.4 | 0
421 | 2022-10-04 07:01 | 16.8 | 24.4 | 0
422 | 2022-10-04 07:02 | 16.8 | 24.4 | 0
423 | 2022-10-04 07:03 | 16.8 | 24.4 | 0
424 | 2022-10-04 07:04 | 16.8 | 24.5 | 0
425 | 2022-10-04 07:05 | 16.7 | 24.3 | 0
426 | 2022-10-04 07:06 | 16.8 | 24.6 | 0
427 | 2022-10-04 07:07 | 16.7 | 24.4 | 0
428 | 2022-10-04 07:08 | 16.8 | 24.7 | 0
429 | 2022-10-04 07:09 | 16.8 | 24.7 | 0
430 | 2022-10-04 07:10 | 16.7 | 24.2 | 0
431 | 2022-10-04 07:11 | 16.7 | 24.5 | 0
432 | 2022-10-04 07:12 | 16.8 | 24.3 | 0
433 | 2022-10-04 07:13 | 16.8 | 24.4 | 0
434 | 2022-10-04 07:14 | 16.7 | 24.5 | 0
435 | 2022-10-04 07:15 | 16.7 | 24.5 | 0
436 | 2022-10-04 07:16 | 16.7 | 24 | 0
437 | 2022-10-04 07:17 | 16.8 | 24.8 | 0
438 | 2022-10-04 07:18 | 16.7 | 23.8 | 0
439 | 2022-10-04 07:19 | 16.9 | 24.9 | 0
440 | 2022-10-04 07:20 | 16.9 | 23.6 | 0
441 | 2022-10-04 07:21 | 16.6 | 24.5 | 1
442 | 2022-10-04 07:22 | 16.6 | 24.4 | 1
443 | 2022-10-04 07:23 | 16.8 | 24.2 | 2
444 | 2022-10-04 07:24 | 16.8 | 24.1 | 2
445 | 2022-10-04 07:25 | 16.8 | 24.3 | 3
446 | 2022-10-04 07:26 | 16.8 | 24.2 | 3
447 | 2022-10-04 07:27 | 16.8 | 24.1 | 4
448 | 2022-10-04 07:28 | 16.8 | 24.7 | 5
449 | 2022-10-04 07:29 | 16.9 | 24.4 | 6
450 | 2022-10-04 07:30 | 16.8 | 24.7 | 7
451 | 2022-10-04 07:31 | 16.8 | 24.4 | 8
452 | 2022-10-04 07:32 | 17 | 24.9 | 8
453 | 2022-10-04 07:33 | 17 | 23.6 | 9
454 | 2022-10-04 07:34 | 16.9 | 24.8 | 9
455 | 2022-10-04 07:35 | 17 | 24.2 | 10
456 | 2022-10-04 07:36 | 16.8 | 24.3 | 10
457 | 2022-10-04 07:37 | 16.9 | 24.5 | 10
458 | 2022-10-04 07:38 | 16.8 | 24.7 | 10
459 | 2022-10-04 07:39 | 17 | 24.5 | 11
460 | 2022-10-04 07:40 | 17 | 24.4 | 12
461 | 2022-10-04 07:41 | 16.9 | 24.3 | 13
462 | 2022-10-04 07:42 | 16.9 | 24.2 | 13
463 | 2022-10-04 07:43 | 17 | 23.9 | 14
464 | 2022-10-04 07:44 | 17 | 24.5 | 13
465 | 2022-10-04 07:45 | 17.1 | 24.4 | 13
466 | 2022-10-04 07:46 | 17 | 24.7 | 14
467 | 2022-10-04 07:47 | 16.9 | 24.4 | 15
468 | 2022-10-04 07:48 | 16.9 | 23.9 | 17
469 | 2022-10-04 07:49 | 16.9 | 24.3 | 19
470 | 2022-10-04 07:50 | 17 | 24.3 | 18
471 | 2022-10-04 07:51 | 16.8 | 24.5 | 18
472 | 2022-10-04 07:52 | 16.8 | 24.3 | 20
473 | 2022-10-04 07:53 | 16.9 | 24.2 | 21
474 | 2022-10-04 07:54 | 17 | 24.7 | 21
475 | 2022-10-04 07:55 | 16.9 | 24.5 | 21
476 | 2022-10-04 07:56 | 16.9 | 24.4 | 21
477 | 2022-10-04 07:57 | 16.8 | 24 | 22
478 | 2022-10-04 07:58 | 16.8 | 24.4 | 22
479 | 2022-10-04 07:59 | 16.9 | 23.9 | 23
480 | 2022-10-04 08:00 | 17 | 24.3 | 23
481 | 2022-10-04 08:01 | 16.8 | 24.3 | 23
482 | 2022-10-04 08:02 | 16.9 | 24 | 24
483 | 2022-10-04 08:03 | 16.8 | 23.9 | 25
484 | 2022-10-04 08:04 | 17 | 24.1 | 26
485 | 2022-10-04 08:05 | 16.9 | 25 | 26
486 | 2022-10-04 08:06 | 16.9 | 24.5 | 27
487 | 2022-10-04 08:07 | 16.7 | 23.8 | 27
488 | 2022-10-04 08:08 | 16.8 | 23.3 | 27
489 | 2022-10-04 08:09 | 16.9 | 23.8 | 27
490 | 2022-10-04 08:10 | 16.9 | 25.1 | 28
491 | 2022-10-04 08:11 | 16.8 | 24.1 | 28
492 | 2022-10-04 08:12 | 17 | 24.4 | 29
493 | 2022-10-04 08:13 | 16.9 | 24.3 | 29
494 | 2022-10-04 08:14 | 16.8 | 23.8 | 30
495 | 2022-10-04 08:15 | 16.9 | 24.8 | 31
496 | 2022-10-04 08:16 | 17 | 24.5 | 31
497 | 2022-10-04 08:17 | 17 | 25 | 31
498 | 2022-10-04 08:18 | 16.8 | 24 | 32
499 | 2022-10-04 08:19 | 16.8 | 24.1 | 32
500 | 2022-10-04 08:20 | 17 | 24.3 | 33
501 | 2022-10-04 08:21 | 17 | 23.6 | 34
502 | 2022-10-04 08:22 | 17 | 24.3 | 34
503 | 2022-10-04 08:23 | 17 | 24.4 | 35
504 | 2022-10-04 08:24 | 17.1 | 23.9 | 35
505 | 2022-10-04 08:25 | 17 | 23.7 | 36
506 | 2022-10-04 08:26 | 17 | 24.1 | 37
507 | 2022-10-04 08:27 | 17 | 24.3 | 37
508 | 2022-10-04 08:28 | 17 | 23.8 | 37
509 | 2022-10-04 08:29 | 17.2 | 24.8 | 38
510 | 2022-10-04 08:30 | 17.1 | 23.5 | 38
511 | 2022-10-04 08:31 | 17 | 23.4 | 40
512 | 2022-10-04 08:32 | 17 | 23.8 | 45
513 | 2022-10-04 08:33 | 17.3 | 24.7 | 47
514 | 2022-10-04 08:34 | 17.3 | 23.3 | 45
515 | 2022-10-04 08:35 | 17.5 | 24 | 44
516 | 2022-10-04 08:36 | 17.7 | 24 | 56
517 | 2022-10-04 08:37 | 17.7 | 23.7 | 86
518 | 2022-10-04 08:38 | 17.9 | 24.4 | 86
519 | 2022-10-04 08:39 | 17.8 | 24 | 82
520 | 2022-10-04 08:40 | 17.7 | 23.8 | 89
521 | 2022-10-04 08:41 | 17.7 | 24.8 | 112
522 | 2022-10-04 08:42 | 17.9 | 24.4 | 113
523 | 2022-10-04 08:43 | 18.2 | 23.5 | 145
524 | 2022-10-04 08:44 | 18.1 | 24.3 | 202
525 | 2022-10-04 08:45 | 18.2 | 24 | 222
526 | 2022-10-04 08:46 | 18.3 | 23.5 | 273
527 | 2022-10-04 08:47 | 18.1 | 23.7 | 283
528 | 2022-10-04 08:48 | 18.1 | 25 | 289
529 | 2022-10-04 08:49 | 18.2 | 24 | 297
530 | 2022-10-04 08:50 | 18.1 | 23.3 | 299
531 | 2022-10-04 08:51 | 18.1 | 24.4 | 305
532 | 2022-10-04 08:52 | 18 | 24.1 | 304
533 | 2022-10-04 08:53 | 18.1 | 24.1 | 72
534 | 2022-10-04 08:54 | 17.8 | 24.2 | 303
535 | 2022-10-04 08:55 | 18 | 24.6 | 68
536 | 2022-10-04 08:56 | 17.9 | 24 | 74
537 | 2022-10-04 08:57 | 17.8 | 24 | 154
538 | 2022-10-04 08:58 | 17.7 | 24.7 | 75
539 | 2022-10-04 08:59 | 17.6 | 24.1 | 76
540 | 2022-10-04 09:00 | 17.8 | 23.9 | 344
541 | 2022-10-04 09:01 | 17.7 | 23.5 | 76
542 | 2022-10-04 09:02 | 17.6 | 24.7 | 66
543 | 2022-10-04 09:03 | 17.6 | 23.9 | 83
544 | 2022-10-04 09:04 | 17.6 | 24.5 | 123
545 | 2022-10-04 09:05 | 17.5 | 24.8 | 380
546 | 2022-10-04 09:06 | 17.7 | 23.7 | 361
547 | 2022-10-04 09:07 | 17.7 | 24.8 | 387
548 | 2022-10-04 09:08 | 17.7 | 23.9 | 384
549 | 2022-10-04 09:09 | 17.7 | 24.7 | 389
550 | 2022-10-04 09:10 | 17.9 | 24.6 | 133
551 | 2022-10-04 09:11 | 17.8 | 23.8 | 87
552 | 2022-10-04 09:12 | 18 | 23.8 | 360
553 | 2022-10-04 09:13 | 18 | 24.1 | 406
554 | 2022-10-04 09:14 | 18.1 | 24.1 | 315
555 | 2022-10-04 09:15 | 18.3 | 23.6 | 405
556 | 2022-10-04 09:16 | 18.1 | 23.9 | 173
557 | 2022-10-04 09:17 | 18.2 | 24.9 | 423
558 | 2022-10-04 09:18 | 18.2 | 24.8 | 104
559 | 2022-10-04 09:19 | 18.4 | 24.6 | 75
560 | 2022-10-04 09:20 | 18.3 | 24.3 | 308
561 | 2022-10-04 09:21 | 18.1 | 24 | 81
562 | 2022-10-04 09:22 | 18.3 | 23.8 | 84
563 | 2022-10-04 09:23 | 18.1 | 24.4 | 450
564 | 2022-10-04 09:24 | 18.2 | 24.1 | 244
565 | 2022-10-04 09:25 | 18.1 | 24.9 | 98
566 | 2022-10-04 09:26 | 17.9 | 24.4 | 79
567 | 2022-10-04 09:27 | 17.9 | 24.7 | 69
568 | 2022-10-04 09:28 | 17.7 | 23.7 | 65
569 | 2022-10-04 09:29 | 17.9 | 22.9 | 66
570 | 2022-10-04 09:30 | 17.7 | 21.9 | 67
571 | 2022-10-04 09:31 | 17.7 | 22.2 | 79
572 | 2022-10-04 09:32 | 17.6 | 22.1 | 486
573 | 2022-10-04 09:33 | 17.7 | 21.4 | 485
574 | 2022-10-04 09:34 | 18.3 | 21.7 | 500
575 | 2022-10-04 09:35 | 18.3 | 22.4 | 508
576 | 2022-10-04 09:36 | 18.6 | 20.9 | 524
577 | 2022-10-04 09:37 | 18.4 | 20.9 | 101
578 | 2022-10-04 09:38 | 18.2 | 21.5 | 536
579 | 2022-10-04 09:39 | 18.3 | 21 | 524
580 | 2022-10-04 09:40 | 18.7 | 21.7 | 516
581 | 2022-10-04 09:41 | 18.7 | 21.1 | 514
582 | 2022-10-04 09:42 | 18.8 | 21.8 | 512
583 | 2022-10-04 09:43 | 19.1 | 21.3 | 522
584 | 2022-10-04 09:44 | 18.9 | 21.4 | 526
585 | 2022-10-04 09:45 | 19.3 | 21.8 | 537
586 | 2022-10-04 09:46 | 19.5 | 22.3 | 547
587 | 2022-10-04 09:47 | 19.6 | 21.4 | 558
588 | 2022-10-04 09:48 | 19.8 | 21.6 | 564
589 | 2022-10-04 09:49 | 19.8 | 21.5 | 127
590 | 2022-10-04 09:50 | 19.9 | 21.7 | 556
591 | 2022-10-04 09:51 | 19.8 | 22.5 | 97
592 | 2022-10-04 09:52 | 19.5 | 22.6 | 126
593 | 2022-10-04 09:53 | 19.1 | 22 | 536
594 | 2022-10-04 09:54 | 19.2 | 21.8 | 599
595 | 2022-10-04 09:55 | 19.4 | 22.3 | 117
596 | 2022-10-04 09:56 | 19.5 | 22.1 | 133
597 | 2022-10-04 09:57 | 19.5 | 21.6 | 624
598 | 2022-10-04 09:58 | 19.5 | 21.5 | 591
599 | 2022-10-04 09:59 | 19.8 | 22.3 | 642
600 | 2022-10-04 10:00 | 19.8 | 22 | 648
601 | 2022-10-04 10:01 | 19.9 | 21.7 | 415
602 | 2022-10-04 10:02 | 19.8 | 21.4 | 642
603 | 2022-10-04 10:03 | 19.9 | 21.5 | 314
604 | 2022-10-04 10:04 | 19.8 | 21.5 | 665
605 | 2022-10-04 10:05 | 20.3 | 21.8 | 645
606 | 2022-10-04 10:06 | 20.5 | 21.8 | 192
607 | 2022-10-04 10:07 | 20.8 | 21.6 | 156
608 | 2022-10-04 10:08 | 20.2 | 21.7 | 685
609 | 2022-10-04 10:09 | 20 | 21.6 | 311
610 | 2022-10-04 10:10 | 20.1 | 21.7 | 173
611 | 2022-10-04 10:11 | 20.2 | 22.6 | 199
612 | 2022-10-04 10:12 | 20.2 | 22.2 | 203
613 | 2022-10-04 10:13 | 20 | 21.9 | 167
614 | 2022-10-04 10:14 | 19.9 | 22.1 | 128
615 | 2022-10-04 10:15 | 19.8 | 21.7 | 108
616 | 2022-10-04 10:16 | 19.7 | 21.3 | 93
617 | 2022-10-04 10:17 | 19.7 | 21.5 | 80
618 | 2022-10-04 10:18 | 19.7 | 21.7 | 71
619 | 2022-10-04 10:19 | 19.5 | 22.6 | 64
620 | 2022-10-04 10:20 | 19.3 | 22.4 | 63
621 | 2022-10-04 10:21 | 19.4 | 21.6 | 63
622 | 2022-10-04 10:22 | 19.2 | 21.7 | 64
623 | 2022-10-04 10:23 | 18.9 | 22.3 | 64
624 | 2022-10-04 10:24 | 18.9 | 21.9 | 65
625 | 2022-10-04 10:25 | 18.9 | 21.4 | 71
626 | 2022-10-04 10:26 | 19 | 21.4 | 70
627 | 2022-10-04 10:27 | 18.9 | 22 | 67
628 | 2022-10-04 10:28 | 19 | 22 | 65
629 | 2022-10-04 10:29 | 18.8 | 22.3 | 64
630 | 2022-10-04 10:30 | 19 | 21.8 | 62
631 | 2022-10-04 10:31 | 19 | 21.8 | 62
632 | 2022-10-04 10:32 | 19 | 21.4 | 59
633 | 2022-10-04 10:33 | 18.8 | 22.2 | 62
634 | 2022-10-04 10:34 | 18.6 | 21.6 | 62
635 | 2022-10-04 10:35 | 18.6 | 21.2 | 67
636 | 2022-10-04 10:36 | 18.6 | 20.8 | 77
637 | 2022-10-04 10:37 | 18.5 | 21.4 | 86
638 | 2022-10-04 10:38 | 18.5 | 21.8 | 102
639 | 2022-10-04 10:39 | 18.6 | 21.5 | 100
640 | 2022-10-04 10:40 | 18.6 | 21.1 | 93
641 | 2022-10-04 10:41 | 18.5 | 21.1 | 89
642 | 2022-10-04 10:42 | 18.6 | 20.9 | 104
643 | 2022-10-04 10:43 | 18.6 | 21.2 | 111
644 | 2022-10-04 10:44 | 18.6 | 20.9 | 104
645 | 2022-10-04 10:45 | 18.7 | 21.5 | 143
646 | 2022-10-04 10:46 | 18.7 | 21 | 152
647 | 2022-10-04 10:47 | 18.6 | 20.6 | 167
648 | 2022-10-04 10:48 | 18.5 | 21.5 | 145
649 | 2022-10-04 10:49 | 18.6 | 22 | 145
650 | 2022-10-04 10:50 | 18.5 | 21.6 | 144
651 | 2022-10-04 10:51 | 18.8 | 21.2 | 149
652 | 2022-10-04 10:52 | 18.6 | 21.5 | 188
653 | 2022-10-04 10:53 | 18.9 | 21.6 | 219
654 | 2022-10-04 10:54 | 18.7 | 21.7 | 227
655 | 2022-10-04 10:55 | 18.9 | 21.9 | 201
656 | 2022-10-04 10:56 | 18.9 | 21.6 | 173
657 | 2022-10-04 10:57 | 19 | 21.5 | 161
658 | 2022-10-04 10:58 | 18.9 | 21.5 | 153
659 | 2022-10-04 10:59 | 19 | 21.8 | 126
660 | 2022-10-04 11:00 | 19.2 | 21.9 | 109
661 | 2022-10-04 11:01 | 19.1 | 21.9 | 112
662 | 2022-10-04 11:02 | 19 | 21.6 | 130
663 | 2022-10-04 11:03 | 19 | 21.4 | 148
664 | 2022-10-04 11:04 | 19.1 | 21.2 | 164
665 | 2022-10-04 11:05 | 19.1 | 21.2 | 176
666 | 2022-10-04 11:06 | 19.1 | 21.2 | 199
667 | 2022-10-04 11:07 | 19.1 | 21.4 | 235
668 | 2022-10-04 11:08 | 18.9 | 21.2 | 623
669 | 2022-10-04 11:09 | 19.1 | 21.1 | 433
670 | 2022-10-04 11:10 | 19.2 | 21.5 | 634
671 | 2022-10-04 11:11 | 19.6 | 21.6 | 321
672 | 2022-10-04 11:12 | 19.8 | 21.6 | 331
673 | 2022-10-04 11:13 | 19.8 | 21.8 | 885
674 | 2022-10-04 11:14 | 20.2 | 22.9 | 255
675 | 2022-10-04 11:15 | 20.2 | 22.8 | 207
676 | 2022-10-04 11:16 | 20 | 22.7 | 180
677 | 2022-10-04 11:17 | 19.7 | 21.5 | 161
678 | 2022-10-04 11:18 | 19.7 | 22.4 | 146
679 | 2022-10-04 11:19 | 19.2 | 20.6 | 136
680 | 2022-10-04 11:20 | 19.2 | 21.4 | 131
681 | 2022-10-04 11:21 | 19.2 | 21.3 | 133
682 | 2022-10-04 11:22 | 19.3 | 22.5 | 144
683 | 2022-10-04 11:23 | 19.3 | 22.1 | 155
684 | 2022-10-04 11:24 | 18.9 | 21.4 | 167
685 | 2022-10-04 11:25 | 18.9 | 21.4 | 178
686 | 2022-10-04 11:26 | 19.1 | 21.3 | 186
687 | 2022-10-04 11:27 | 19 | 21.1 | 185
688 | 2022-10-04 11:28 | 19.2 | 21.6 | 162
689 | 2022-10-04 11:29 | 19.2 | 21.3 | 147
690 | 2022-10-04 11:30 | 19.2 | 21.5 | 140
691 | 2022-10-04 11:31 | 18.9 | 22.1 | 134
692 | 2022-10-04 11:32 | 18.9 | 21.4 | 131
693 | 2022-10-04 11:33 | 18.8 | 22.2 | 122
694 | 2022-10-04 11:34 | 18.7 | 21.9 | 121
695 | 2022-10-04 11:35 | 18.9 | 22 | 116
696 | 2022-10-04 11:36 | 18.6 | 21.1 | 115
697 | 2022-10-04 11:37 | 18.7 | 20.5 | 113
698 | 2022-10-04 11:38 | 18.6 | 21.3 | 139
699 | 2022-10-04 11:39 | 18.7 | 21.2 | 220
700 | 2022-10-04 11:40 | 18.7 | 20.8 | 248
701 | 2022-10-04 11:41 | 18.6 | 21.4 | 945
702 | 2022-10-04 11:42 | 19 | 21.4 | 950
703 | 2022-10-04 11:43 | 19.4 | 21.2 | 948
704 | 2022-10-04 11:44 | 19.7 | 20.9 | 950
705 | 2022-10-04 11:45 | 20 | 21.5 | 940
706 | 2022-10-04 11:46 | 20.3 | 22.2 | 934
707 | 2022-10-04 11:47 | 20.6 | 21.5 | 926
708 | 2022-10-04 11:48 | 20.7 | 21.1 | 930
709 | 2022-10-04 11:49 | 20.7 | 22.3 | 929
710 | 2022-10-04 11:50 | 20.8 | 22.6 | 935
711 | 2022-10-04 11:51 | 21.1 | 21.8 | 943
712 | 2022-10-04 11:52 | 20.6 | 21.8 | 948
713 | 2022-10-04 11:53 | 20.9 | 21.9 | 949
714 | 2022-10-04 11:54 | 21.1 | 21.7 | 949
715 | 2022-10-04 11:55 | 21.5 | 22.7 | 949
716 | 2022-10-04 11:56 | 21.3 | 21.1 | 952
717 | 2022-10-04 11:57 | 21.5 | 21.1 | 951
718 | 2022-10-04 11:58 | 20.8 | 21 | 948
719 | 2022-10-04 11:59 | 21.3 | 21.6 | 948
720 | 2022-10-04 12:00 | 21.2 | 21.7 | 949
721 | 2022-10-04 12:01 | 21.7 | 22 | 951
722 | 2022-10-04 12:02 | 21.7 | 22.1 | 955
723 | 2022-10-04 12:03 | 21.8 | 21.7 | 958
724 | 2022-10-04 12:04 | 22 | 21.9 | 958
725 | 2022-10-04 12:05 | 22.2 | 22.2 | 958
726 | 2022-10-04 12:06 | 22.4 | 22.1 | 959
727 | 2022-10-04 12:07 | 22.3 | 22.6 | 958
728 | 2022-10-04 12:08 | 22.4 | 22.4 | 957
729 | 2022-10-04 12:09 | 22.5 | 22.1 | 962
730 | 2022-10-04 12:10 | 22.5 | 22.3 | 965
731 | 2022-10-04 12:11 | 22.6 | 22.4 | 964
732 | 2022-10-04 12:12 | 22.3 | 22.4 | 967
733 | 2022-10-04 12:13 | 22.3 | 22.2 | 970
734 | 2022-10-04 12:14 | 22.6 | 22.5 | 972
735 | 2022-10-04 12:15 | 22.6 | 22.5 | 974
736 | 2022-10-04 12:16 | 22.6 | 21.7 | 976
737 | 2022-10-04 12:17 | 22.9 | 21.9 | 976
738 | 2022-10-04 12:18 | 23.1 | 22.6 | 980
739 | 2022-10-04 12:19 | 22.7 | 22.4 | 983
740 | 2022-10-04 12:20 | 22.8 | 22.7 | 987
741 | 2022-10-04 12:21 | 22.3 | 22.9 | 988
742 | 2022-10-04 12:22 | 21.8 | 22.3 | 986
743 | 2022-10-04 12:23 | 22.1 | 23.8 | 986
744 | 2022-10-04 12:24 | 22.6 | 23.2 | 989
745 | 2022-10-04 12:25 | 22.7 | 23.4 | 990
746 | 2022-10-04 12:26 | 23 | 23.4 | 989
747 | 2022-10-04 12:27 | 22.9 | 23.4 | 987
748 | 2022-10-04 12:28 | 22.8 | 23.8 | 988
749 | 2022-10-04 12:29 | 22.7 | 23.6 | 990
750 | 2022-10-04 12:30 | 22.7 | 23.8 | 991
751 | 2022-10-04 12:31 | 22.6 | 23.8 | 995
752 | 2022-10-04 12:32 | 23 | 24.5 | 997
753 | 2022-10-04 12:33 | 22.8 | 24 | 996
754 | 2022-10-04 12:34 | 22.9 | 23.7 | 996
755 | 2022-10-04 12:35 | 22.4 | 23.1 | 995
756 | 2022-10-04 12:36 | 22.9 | 23.7 | 996
757 | 2022-10-04 12:37 | 23.1 | 24.2 | 999
758 | 2022-10-04 12:38 | 23 | 23.7 | 1001
759 | 2022-10-04 12:39 | 22.8 | 23.9 | 1001
760 | 2022-10-04 12:40 | 23.4 | 23.8 | 1003
761 | 2022-10-04 12:41 | 23 | 23.7 | 1003
762 | 2022-10-04 12:42 | 23.1 | 24.1 | 1003
763 | 2022-10-04 12:43 | 23.3 | 23.7 | 1002
764 | 2022-10-04 12:44 | 23.3 | 23.9 | 1001
765 | 2022-10-04 12:45 | 23.2 | 24 | 1006
766 | 2022-10-04 12:46 | 22.6 | 23.5 | 1009
767 | 2022-10-04 12:47 | 22.3 | 24.5 | 1009
768 | 2022-10-04 12:48 | 22.6 | 23.7 | 1014
769 | 2022-10-04 12:49 | 23.1 | 24.7 | 1016
770 | 2022-10-04 12:50 | 23.3 | 23.2 | 1014
771 | 2022-10-04 12:51 | 23.2 | 24.8 | 1013
772 | 2022-10-04 12:52 | 23.4 | 24.2 | 1016
773 | 2022-10-04 12:53 | 23.5 | 24.6 | 1016
774 | 2022-10-04 12:54 | 23.5 | 25.1 | 1016
775 | 2022-10-04 12:55 | 23.6 | 24.6 | 1017
776 | 2022-10-04 12:56 | 23.4 | 24.3 | 1018
777 | 2022-10-04 12:57 | 23.6 | 24.3 | 1021
778 | 2022-10-04 12:58 | 23.6 | 24 | 1020
779 | 2022-10-04 12:59 | 23.5 | 23.9 | 1023
780 | 2022-10-04 13:00 | 23.8 | 24.1 | 1024
781 | 2022-10-04 13:01 | 23.5 | 24.4 | 1023
782 | 2022-10-04 13:02 | 23.2 | 24.3 | 1022
783 | 2022-10-04 13:03 | 23.2 | 25 | 1021
784 | 2022-10-04 13:04 | 22.8 | 24.3 | 1020
785 | 2022-10-04 13:05 | 23 | 24.3 | 1020
786 | 2022-10-04 13:06 | 23.3 | 24.1 | 1019
787 | 2022-10-04 13:07 | 23.8 | 24.4 | 1020
788 | 2022-10-04 13:08 | 23.7 | 24.3 | 1021
789 | 2022-10-04 13:09 | 23.6 | 24.2 | 1021
790 | 2022-10-04 13:10 | 23.8 | 24.2 | 1021
791 | 2022-10-04 13:11 | 23.8 | 24.1 | 1020
792 | 2022-10-04 13:12 | 23.6 | 24.3 | 1020
793 | 2022-10-04 13:13 | 23.7 | 23.5 | 1020
794 | 2022-10-04 13:14 | 23.6 | 24.3 | 1018
795 | 2022-10-04 13:15 | 23.7 | 23.9 | 1017
796 | 2022-10-04 13:16 | 23.8 | 24.1 | 1016
797 | 2022-10-04 13:17 | 24.2 | 24 | 1017
798 | 2022-10-04 13:18 | 24.5 | 24.1 | 1017
799 | 2022-10-04 13:19 | 23.8 | 24.3 | 1016
800 | 2022-10-04 13:20 | 23 | 24.4 | 1019
801 | 2022-10-04 13:21 | 23.8 | 24.3 | 1022
802 | 2022-10-04 13:22 | 23.9 | 24.2 | 1023
803 | 2022-10-04 13:23 | 23.9 | 24.6 | 1021
804 | 2022-10-04 13:24 | 23.9 | 24.2 | 1019
805 | 2022-10-04 13:25 | 24.3 | 24.3 | 1016
806 | 2022-10-04 13:26 | 23.6 | 24.1 | 1012
807 | 2022-10-04 13:27 | 24.1 | 24.1 | 1012
808 | 2022-10-04 13:28 | 24.4 | 23.9 | 1012
809 | 2022-10-04 13:29 | 23.9 | 24.1 | 1012
810 | 2022-10-04 13:30 | 23.9 | 24.3 | 1013
811 | 2022-10-04 13:31 | 24 | 24.5 | 1014
812 | 2022-10-04 13:32 | 23.2 | 24 | 1015
813 | 2022-10-04 13:33 | 23.5 | 24.3 | 1015
814 | 2022-10-04 13:34 | 23.5 | 24.4 | 1015
815 | 2022-10-04 13:35 | 23.7 | 24.1 | 1013
816 | 2022-10-04 13:36 | 23.9 | 24.6 | 1010
817 | 2022-10-04 13:37 | 24 | 24.1 | 1009
818 | 2022-10-04 13:38 | 23.8 | 24.6 | 1007
819 | 2022-10-04 13:39 | 23.4 | 24.2 | 1008
820 | 2022-10-04 13:40 | 23.2 | 23.8 | 1006
821 | 2022-10-04 13:41 | 23.3 | 24.5 | 1006
822 | 2022-10-04 13:42 | 23.4 | 23.2 | 1005
823 | 2022-10-04 13:43 | 24 | 23.6 | 1001
824 | 2022-10-04 13:44 | 24.3 | 23.2 | 1002
825 | 2022-10-04 13:45 | 23.7 | 23.2 | 1002
826 | 2022-10-04 13:46 | 23.6 | 23.4 | 1001
827 | 2022-10-04 13:47 | 23.6 | 23.8 | 1001
828 | 2022-10-04 13:48 | 23.7 | 23.5 | 992
829 | 2022-10-04 13:49 | 23.6 | 22.8 | 995
830 | 2022-10-04 13:50 | 23.4 | 22.7 | 1000
831 | 2022-10-04 13:51 | 23.3 | 22.7 | 1003
832 | 2022-10-04 13:52 | 23.5 | 22.8 | 1005
833 | 2022-10-04 13:53 | 23.4 | 23 | 1007
834 | 2022-10-04 13:54 | 23.8 | 22.8 | 1007
835 | 2022-10-04 13:55 | 24 | 22.8 | 1007
836 | 2022-10-04 13:56 | 24.2 | 22.8 | 1007
837 | 2022-10-04 13:57 | 24.1 | 22.9 | 1006
838 | 2022-10-04 13:58 | 23.9 | 22.6 | 1005
839 | 2022-10-04 13:59 | 24.4 | 22.9 | 1002
840 | 2022-10-04 14:00 | 24.6 | 23 | 1003
841 | 2022-10-04 14:01 | 24.1 | 23.5 | 1006
842 | 2022-10-04 14:02 | 24.1 | 22.1 | 1003
843 | 2022-10-04 14:03 | 24.3 | 22.9 | 1000
844 | 2022-10-04 14:04 | 24.2 | 22 | 995
845 | 2022-10-04 14:05 | 24.1 | 22.5 | 996
846 | 2022-10-04 14:06 | 24.1 | 22.5 | 999
847 | 2022-10-04 14:07 | 23.6 | 23.4 | 994
848 | 2022-10-04 14:08 | 23.6 | 22.5 | 993
849 | 2022-10-04 14:09 | 23.5 | 22.4 | 990
850 | 2022-10-04 14:10 | 23.4 | 23.5 | 988
851 | 2022-10-04 14:11 | 23.8 | 23.4 | 987
852 | 2022-10-04 14:12 | 23.6 | 22 | 982
853 | 2022-10-04 14:13 | 23.7 | 22.1 | 979
854 | 2022-10-04 14:14 | 23.6 | 22.1 | 973
855 | 2022-10-04 14:15 | 24 | 23.3 | 976
856 | 2022-10-04 14:16 | 24.4 | 23.7 | 972
857 | 2022-10-04 14:17 | 24 | 22.4 | 969
858 | 2022-10-04 14:18 | 23.8 | 23.2 | 968
859 | 2022-10-04 14:19 | 23.8 | 23.6 | 966
860 | 2022-10-04 14:20 | 23.8 | 23.4 | 965
861 | 2022-10-04 14:21 | 23.9 | 23 | 960
862 | 2022-10-04 14:22 | 24 | 23.4 | 952
863 | 2022-10-04 14:23 | 24.1 | 23 | 940
864 | 2022-10-04 14:24 | 24.1 | 23.1 | 953
865 | 2022-10-04 14:25 | 24.1 | 23 | 950
866 | 2022-10-04 14:26 | 24.2 | 23.4 | 891
867 | 2022-10-04 14:27 | 23.8 | 23.2 | 957
868 | 2022-10-04 14:28 | 23.7 | 22.5 | 734
869 | 2022-10-04 14:29 | 23.4 | 23.5 | 443
870 | 2022-10-04 14:30 | 23.2 | 22.5 | 983
871 | 2022-10-04 14:31 | 22.7 | 22.7 | 964
872 | 2022-10-04 14:32 | 22.9 | 22.5 | 981
873 | 2022-10-04 14:33 | 22.7 | 22.9 | 685
874 | 2022-10-04 14:34 | 22.8 | 23.3 | 237
875 | 2022-10-04 14:35 | 23 | 23.8 | 533
876 | 2022-10-04 14:36 | 23.2 | 22.9 | 947
877 | 2022-10-04 14:37 | 23.3 | 22.3 | 933
878 | 2022-10-04 14:38 | 23.8 | 22.5 | 945
879 | 2022-10-04 14:39 | 23.7 | 23.4 | 951
880 | 2022-10-04 14:40 | 23.8 | 23.5 | 929
881 | 2022-10-04 14:41 | 23.7 | 22.2 | 934
882 | 2022-10-04 14:42 | 23.8 | 22.9 | 927
883 | 2022-10-04 14:43 | 23.7 | 22.3 | 920
884 | 2022-10-04 14:44 | 23.7 | 22.6 | 923
885 | 2022-10-04 14:45 | 23.9 | 22.4 | 903
886 | 2022-10-04 14:46 | 23.9 | 23.1 | 892
887 | 2022-10-04 14:47 | 23.8 | 23 | 916
888 | 2022-10-04 14:48 | 23.8 | 22.9 | 912
889 | 2022-10-04 14:49 | 23.7 | 22.9 | 908
890 | 2022-10-04 14:50 | 23.5 | 23 | 907
891 | 2022-10-04 14:51 | 23.3 | 22.9 | 907
892 | 2022-10-04 14:52 | 23.2 | 22.8 | 914
893 | 2022-10-04 14:53 | 23.7 | 22.9 | 916
894 | 2022-10-04 14:54 | 24.1 | 22.9 | 898
895 | 2022-10-04 14:55 | 23.9 | 23.1 | 878
896 | 2022-10-04 14:56 | 23.9 | 23.1 | 887
897 | 2022-10-04 14:57 | 23.8 | 23.1 | 892
898 | 2022-10-04 14:58 | 23.7 | 23 | 882
899 | 2022-10-04 14:59 | 23.9 | 23.1 | 881
900 | 2022-10-04 15:00 | 24.1 | 22.9 | 878
901 | 2022-10-04 15:01 | 24 | 23 | 881
902 | 2022-10-04 15:02 | 23.6 | 22.9 | 887
903 | 2022-10-04 15:03 | 23.6 | 22.8 | 885
904 | 2022-10-04 15:04 | 23.5 | 22.4 | 878
905 | 2022-10-04 15:05 | 23.5 | 22.4 | 875
906 | 2022-10-04 15:06 | 23.7 | 22.9 | 868
907 | 2022-10-04 15:07 | 23.3 | 22.6 | 852
908 | 2022-10-04 15:08 | 23.4 | 22.9 | 850
909 | 2022-10-04 15:09 | 23.7 | 22.7 | 864
910 | 2022-10-04 15:10 | 24.1 | 23.4 | 526
911 | 2022-10-04 15:11 | 24 | 22.5 | 873
912 | 2022-10-04 15:12 | 24.3 | 22.9 | 869
913 | 2022-10-04 15:13 | 24.4 | 23.2 | 865
914 | 2022-10-04 15:14 | 24.4 | 23 | 873
915 | 2022-10-04 15:15 | 24.4 | 23.2 | 884
916 | 2022-10-04 15:16 | 24.4 | 23.9 | 887
917 | 2022-10-04 15:17 | 24.2 | 22.8 | 891
918 | 2022-10-04 15:18 | 24.2 | 23.3 | 891
919 | 2022-10-04 15:19 | 24.2 | 23.9 | 872
920 | 2022-10-04 15:20 | 24.2 | 23.1 | 859
921 | 2022-10-04 15:21 | 24.3 | 23.4 | 442
922 | 2022-10-04 15:22 | 24 | 22.9 | 528
923 | 2022-10-04 15:23 | 23.7 | 23.3 | 896
924 | 2022-10-04 15:24 | 23.3 | 23 | 473
925 | 2022-10-04 15:25 | 23.6 | 23.3 | 623
926 | 2022-10-04 15:26 | 24 | 23.4 | 236
927 | 2022-10-04 15:27 | 23.6 | 23.1 | 188
928 | 2022-10-04 15:28 | 23.3 | 23.1 | 851
929 | 2022-10-04 15:29 | 23.1 | 22.8 | 829
930 | 2022-10-04 15:30 | 23.4 | 22 | 826
931 | 2022-10-04 15:31 | 23.9 | 22.8 | 816
932 | 2022-10-04 15:32 | 23.3 | 23.5 | 809
933 | 2022-10-04 15:33 | 23.8 | 22.8 | 812
934 | 2022-10-04 15:34 | 23.8 | 23 | 808
935 | 2022-10-04 15:35 | 23.7 | 22.1 | 802
936 | 2022-10-04 15:36 | 23.6 | 22.8 | 804
937 | 2022-10-04 15:37 | 23.7 | 22.7 | 797
938 | 2022-10-04 15:38 | 23 | 22.5 | 792
939 | 2022-10-04 15:39 | 23.3 | 23 | 790
940 | 2022-10-04 15:40 | 23.1 | 23 | 791
941 | 2022-10-04 15:41 | 23.1 | 23.1 | 795
942 | 2022-10-04 15:42 | 23.5 | 22.9 | 799
943 | 2022-10-04 15:43 | 23.7 | 22.6 | 797
944 | 2022-10-04 15:44 | 23.2 | 22.7 | 792
945 | 2022-10-04 15:45 | 23.7 | 23 | 797
946 | 2022-10-04 15:46 | 23.4 | 23.4 | 795
947 | 2022-10-04 15:47 | 23.8 | 22.2 | 807
948 | 2022-10-04 15:48 | 24.2 | 22.1 | 811
949 | 2022-10-04 15:49 | 24.1 | 22.4 | 817
950 | 2022-10-04 15:50 | 24.2 | 22.6 | 796
951 | 2022-10-04 15:51 | 23.7 | 22.6 | 779
952 | 2022-10-04 15:52 | 23.9 | 22.9 | 772
953 | 2022-10-04 15:53 | 24.2 | 23.8 | 764
954 | 2022-10-04 15:54 | 23.9 | 23.4 | 756
955 | 2022-10-04 15:55 | 23.9 | 22.8 | 745
956 | 2022-10-04 15:56 | 23.1 | 23.8 | 736
957 | 2022-10-04 15:57 | 23.3 | 23 | 731
958 | 2022-10-04 15:58 | 23.6 | 23.2 | 728
959 | 2022-10-04 15:59 | 24 | 24 | 727
960 | 2022-10-04 16:00 | 23.9 | 23.2 | 722
961 | 2022-10-04 16:01 | 24.3 | 22.9 | 717
962 | 2022-10-04 16:02 | 24 | 23 | 710
963 | 2022-10-04 16:03 | 23.8 | 22.8 | 713
964 | 2022-10-04 16:04 | 23.6 | 23.2 | 709
965 | 2022-10-04 16:05 | 23.3 | 22.9 | 704
966 | 2022-10-04 16:06 | 23.4 | 21.9 | 700
967 | 2022-10-04 16:07 | 23.3 | 22.1 | 694
968 | 2022-10-04 16:08 | 23.5 | 22.8 | 691
969 | 2022-10-04 16:09 | 23.6 | 22.9 | 685
970 | 2022-10-04 16:10 | 24.1 | 22.4 | 681
971 | 2022-10-04 16:11 | 24.1 | 22.3 | 675
972 | 2022-10-04 16:12 | 24 | 23.4 | 674
973 | 2022-10-04 16:13 | 24.1 | 23.7 | 671
974 | 2022-10-04 16:14 | 23.3 | 22.5 | 671
975 | 2022-10-04 16:15 | 23.3 | 22.7 | 668
976 | 2022-10-04 16:16 | 23.6 | 22.5 | 663
977 | 2022-10-04 16:17 | 23.5 | 22.9 | 659
978 | 2022-10-04 16:18 | 23.4 | 22.9 | 653
979 | 2022-10-04 16:19 | 23.5 | 23.5 | 648
980 | 2022-10-04 16:20 | 23.3 | 22.9 | 647
981 | 2022-10-04 16:21 | 23.2 | 22.4 | 644
982 | 2022-10-04 16:22 | 23.1 | 23.1 | 638
983 | 2022-10-04 16:23 | 23.4 | 22.9 | 636
984 | 2022-10-04 16:24 | 23.4 | 22.5 | 633
985 | 2022-10-04 16:25 | 23.4 | 22.5 | 630
986 | 2022-10-04 16:26 | 23.4 | 22.5 | 627
987 | 2022-10-04 16:27 | 23.7 | 22.2 | 623
988 | 2022-10-04 16:28 | 23.7 | 22.3 | 617
989 | 2022-10-04 16:29 | 23.8 | 22.9 | 611
990 | 2022-10-04 16:30 | 23.6 | 22.8 | 605
991 | 2022-10-04 16:31 | 23.5 | 22.8 | 600
992 | 2022-10-04 16:32 | 23.2 | 23.7 | 594
993 | 2022-10-04 16:33 | 23.3 | 23.5 | 590
994 | 2022-10-04 16:34 | 23.1 | 23 | 589
995 | 2022-10-04 16:35 | 23.2 | 22.6 | 588
996 | 2022-10-04 16:36 | 23.2 | 22.3 | 584
997 | 2022-10-04 16:37 | 23.3 | 22.4 | 581
998 | 2022-10-04 16:38 | 23.4 | 22.6 | 578
999 | 2022-10-04 16:39 | 23 | 22.6 | 573
1000 | 2022-10-04 16:40 | 23.2 | 22.6 | 568
1001 | 2022-10-04 16:41 | 23.5 | 22.8 | 566
1002 | 2022-10-04 16:42 | 23.1 | 22.4 | 561
1003 | 2022-10-04 16:43 | 23.1 | 22.4 | 557
1004 | 2022-10-04 16:44 | 22.9 | 22.6 | 552
1005 | 2022-10-04 16:45 | 23.1 | 22.4 | 547
1006 | 2022-10-04 16:46 | 22.9 | 22.5 | 543
1007 | 2022-10-04 16:47 | 22.7 | 22.2 | 538
1008 | 2022-10-04 16:48 | 23 | 22.4 | 530
1009 | 2022-10-04 16:49 | 22.8 | 21.5 | 523
1010 | 2022-10-04 16:50 | 22.6 | 22.8 | 517
1011 | 2022-10-04 16:51 | 23 | 22.5 | 515
1012 | 2022-10-04 16:52 | 22.7 | 22.3 | 506
1013 | 2022-10-04 16:53 | 22.9 | 23.1 | 506
1014 | 2022-10-04 16:54 | 23 | 23.3 | 503
1015 | 2022-10-04 16:55 | 22.9 | 23.6 | 498
1016 | 2022-10-04 16:56 | 22.4 | 23.4 | 495
1017 | 2022-10-04 16:57 | 22.5 | 23.1 | 491
1018 | 2022-10-04 16:58 | 22.4 | 22.8 | 491
1019 | 2022-10-04 16:59 | 22.2 | 21.3 | 488
1020 | 2022-10-04 17:00 | 22.4 | 22.5 | 481
1021 | 2022-10-04 17:01 | 22.7 | 22.6 | 479
1022 | 2022-10-04 17:02 | 22.6 | 22.8 | 477
1023 | 2022-10-04 17:03 | 22.8 | 22.6 | 473
1024 | 2022-10-04 17:04 | 22.7 | 22.9 | 468
1025 | 2022-10-04 17:05 | 23.2 | 23.5 | 461
1026 | 2022-10-04 17:06 | 22.6 | 23.9 | 451
1027 | 2022-10-04 17:07 | 22.7 | 23.2 | 441
1028 | 2022-10-04 17:08 | 22.5 | 23.7 | 442
1029 | 2022-10-04 17:09 | 22.2 | 23.3 | 439
1030 | 2022-10-04 17:10 | 22 | 23.9 | 431
1031 | 2022-10-04 17:11 | 22.1 | 23.9 | 430
1032 | 2022-10-04 17:12 | 22.5 | 23.9 | 432
1033 | 2022-10-04 17:13 | 22.7 | 23.9 | 421
1034 | 2022-10-04 17:14 | 22.9 | 23.8 | 424
1035 | 2022-10-04 17:15 | 22.4 | 24.4 | 426
1036 | 2022-10-04 17:16 | 22.6 | 24.5 | 416
1037 | 2022-10-04 17:17 | 22.6 | 24 | 399
1038 | 2022-10-04 17:18 | 22.7 | 23.9 | 398
1039 | 2022-10-04 17:19 | 22.7 | 23.9 | 395
1040 | 2022-10-04 17:20 | 22.4 | 24 | 397
1041 | 2022-10-04 17:21 | 22.1 | 24 | 392
1042 | 2022-10-04 17:22 | 22.3 | 24 | 385
1043 | 2022-10-04 17:23 | 22.1 | 24.2 | 383
1044 | 2022-10-04 17:24 | 22.3 | 23.9 | 379
1045 | 2022-10-04 17:25 | 22.5 | 23.8 | 374
1046 | 2022-10-04 17:26 | 22.3 | 23.9 | 370
1047 | 2022-10-04 17:27 | 22.3 | 23.8 | 365
1048 | 2022-10-04 17:28 | 22.2 | 23.8 | 359
1049 | 2022-10-04 17:29 | 22.2 | 23.4 | 356
1050 | 2022-10-04 17:30 | 22.4 | 23.7 | 350
1051 | 2022-10-04 17:31 | 22.6 | 24.1 | 347
1052 | 2022-10-04 17:32 | 22.3 | 24.1 | 342
1053 | 2022-10-04 17:33 | 22.2 | 23.1 | 339
1054 | 2022-10-04 17:34 | 22.6 | 23.4 | 336
1055 | 2022-10-04 17:35 | 22.2 | 23.7 | 330
1056 | 2022-10-04 17:36 | 22.1 | 23.6 | 328
1057 | 2022-10-04 17:37 | 22.2 | 24 | 326
1058 | 2022-10-04 17:38 | 22.2 | 23.8 | 319
1059 | 2022-10-04 17:39 | 22.3 | 23.9 | 315
1060 | 2022-10-04 17:40 | 22.4 | 23.8 | 313
1061 | 2022-10-04 17:41 | 22.1 | 23.8 | 307
1062 | 2022-10-04 17:42 | 22.2 | 23.7 | 302
1063 | 2022-10-04 17:43 | 22.4 | 23.7 | 298
1064 | 2022-10-04 17:44 | 22.3 | 23.8 | 300
1065 | 2022-10-04 17:45 | 22.2 | 23.7 | 299
1066 | 2022-10-04 17:46 | 22 | 23.9 | 298
1067 | 2022-10-04 17:47 | 22 | 24.3 | 297
1068 | 2022-10-04 17:48 | 21.8 | 23.8 | 289
1069 | 2022-10-04 17:49 | 21.6 | 23.5 | 282
1070 | 2022-10-04 17:50 | 21.6 | 23.9 | 230
1071 | 2022-10-04 17:51 | 21.9 | 23.6 | 235
1072 | 2022-10-04 17:52 | 21.9 | 24 | 255
1073 | 2022-10-04 17:53 | 21.8 | 23.8 | 252
1074 | 2022-10-04 17:54 | 21.9 | 24 | 195
1075 | 2022-10-04 17:55 | 21.7 | 24 | 239
1076 | 2022-10-04 17:56 | 21.4 | 24.2 | 201
1077 | 2022-10-04 17:57 | 21.5 | 23.6 | 154
1078 | 2022-10-04 17:58 | 21.3 | 24.3 | 56
1079 | 2022-10-04 17:59 | 21.3 | 23.8 | 79
1080 | 2022-10-04 18:00 | 21.2 | 23.7 | 165
1081 | 2022-10-04 18:01 | 20.9 | 23.8 | 53
1082 | 2022-10-04 18:02 | 20.6 | 23.8 | 51
1083 | 2022-10-04 18:03 | 20.7 | 23.8 | 48
1084 | 2022-10-04 18:04 | 20.6 | 23.9 | 47
1085 | 2022-10-04 18:05 | 20.6 | 23.8 | 44
1086 | 2022-10-04 18:06 | 20.4 | 23.9 | 44
1087 | 2022-10-04 18:07 | 20.3 | 23.8 | 45
1088 | 2022-10-04 18:08 | 20.4 | 23.4 | 46
1089 | 2022-10-04 18:09 | 20.3 | 23.2 | 44
1090 | 2022-10-04 18:10 | 20.4 | 24.5 | 40
1091 | 2022-10-04 18:11 | 20.3 | 24.1 | 38
1092 | 2022-10-04 18:12 | 20.2 | 23.8 | 39
1093 | 2022-10-04 18:13 | 20.1 | 23.8 | 39
1094 | 2022-10-04 18:14 | 20 | 23.9 | 40
1095 | 2022-10-04 18:15 | 19.9 | 23.8 | 38
1096 | 2022-10-04 18:16 | 20.1 | 23.4 | 34
1097 | 2022-10-04 18:17 | 19.9 | 24.1 | 32
1098 | 2022-10-04 18:18 | 19.9 | 24.2 | 33
1099 | 2022-10-04 18:19 | 19.6 | 23.7 | 34
1100 | 2022-10-04 18:20 | 19.7 | 24.2 | 35
1101 | 2022-10-04 18:21 | 19.6 | 23.8 | 34
1102 | 2022-10-04 18:22 | 19.6 | 23.8 | 34
1103 | 2022-10-04 18:23 | 19.6 | 23.8 | 34
1104 | 2022-10-04 18:24 | 19.5 | 23.7 | 34
1105 | 2022-10-04 18:25 | 19.5 | 23.9 | 33
1106 | 2022-10-04 18:26 | 19.5 | 23.8 | 43
1107 | 2022-10-04 18:27 | 19.5 | 23.9 | 71
1108 | 2022-10-04 18:28 | 19.4 | 23.9 | 91
1109 | 2022-10-04 18:29 | 19.4 | 23.8 | 89
1110 | 2022-10-04 18:30 | 19.4 | 24 | 85
1111 | 2022-10-04 18:31 | 19.6 | 23.4 | 80
1112 | 2022-10-04 18:32 | 19.5 | 23.7 | 66
1113 | 2022-10-04 18:33 | 19.8 | 23.4 | 41
1114 | 2022-10-04 18:34 | 19.7 | 23.1 | 28
1115 | 2022-10-04 18:35 | 19.5 | 23.7 | 26
1116 | 2022-10-04 18:36 | 19.4 | 23.9 | 25
1117 | 2022-10-04 18:37 | 19.4 | 23.7 | 25
1118 | 2022-10-04 18:38 | 19.3 | 24 | 21
1119 | 2022-10-04 18:39 | 19.1 | 23.6 | 22
1120 | 2022-10-04 18:40 | 19.1 | 24.1 | 20
1121 | 2022-10-04 18:41 | 19 | 23.7 | 18
1122 | 2022-10-04 18:42 | 19 | 23.6 | 16
1123 | 2022-10-04 18:43 | 18.8 | 23.8 | 14
1124 | 2022-10-04 18:44 | 18.9 | 23.8 | 13
1125 | 2022-10-04 18:45 | 18.8 | 23.7 | 12
1126 | 2022-10-04 18:46 | 18.9 | 23.6 | 11
1127 | 2022-10-04 18:47 | 18.7 | 23.9 | 10
1128 | 2022-10-04 18:48 | 18.7 | 23.8 | 9
1129 | 2022-10-04 18:49 | 18.7 | 23.9 | 8
1130 | 2022-10-04 18:50 | 18.6 | 23.8 | 7
1131 | 2022-10-04 18:51 | 18.6 | 23.9 | 6
1132 | 2022-10-04 18:52 | 18.6 | 23.7 | 5
1133 | 2022-10-04 18:53 | 18.6 | 23.6 | 4
1134 | 2022-10-04 18:54 | 18.5 | 24 | 4
1135 | 2022-10-04 18:55 | 18.4 | 23.9 | 3
1136 | 2022-10-04 18:56 | 18.4 | 23.8 | 3
1137 | 2022-10-04 18:57 | 18.4 | 23.6 | 2
1138 | 2022-10-04 18:58 | 18.3 | 23.8 | 2
1139 | 2022-10-04 18:59 | 18.4 | 23.4 | 1
1140 | 2022-10-04 19:00 | 18.2 | 23.6 | 1
1141 | 2022-10-04 19:01 | 18.3 | 23.8 | 0
1142 | 2022-10-04 19:02 | 18.3 | 23.7 | 0
1143 | 2022-10-04 19:03 | 18.2 | 23.7 | 0
1144 | 2022-10-04 19:04 | 18.1 | 23.8 | 0
1145 | 2022-10-04 19:05 | 18.1 | 23.8 | 0
1146 | 2022-10-04 19:06 | 18 | 23.5 | 0
1147 | 2022-10-04 19:07 | 18 | 23.8 | 0
1148 | 2022-10-04 19:08 | 18 | 23.9 | 0
1149 | 2022-10-04 19:09 | 18.1 | 23.7 | 0
1150 | 2022-10-04 19:10 | 18 | 23.8 | 0
1151 | 2022-10-04 19:11 | 18.1 | 24.1 | 0
1152 | 2022-10-04 19:12 | 17.8 | 23.9 | 0
1153 | 2022-10-04 19:13 | 17.9 | 23.8 | 0
1154 | 2022-10-04 19:14 | 17.9 | 23.6 | 0
1155 | 2022-10-04 19:15 | 17.9 | 23.4 | 0
1156 | 2022-10-04 19:16 | 17.8 | 23.9 | 0
1157 | 2022-10-04 19:17 | 17.8 | 24.1 | 0
1158 | 2022-10-04 19:18 | 17.8 | 24.3 | 0
1159 | 2022-10-04 19:19 | 17.6 | 24 | 0
1160 | 2022-10-04 19:20 | 17.6 | 23.4 | 0
1161 | 2022-10-04 19:21 | 17.7 | 23.7 | 0
1162 | 2022-10-04 19:22 | 17.6 | 23.9 | 0
1163 | 2022-10-04 19:23 | 17.8 | 23.7 | 0
1164 | 2022-10-04 19:24 | 17.7 | 23.8 | 0
1165 | 2022-10-04 19:25 | 17.7 | 23.5 | 0
1166 | 2022-10-04 19:26 | 17.6 | 23.6 | 0
1167 | 2022-10-04 19:27 | 17.7 | 23.7 | 0
1168 | 2022-10-04 19:28 | 17.6 | 23.7 | 0
1169 | 2022-10-04 19:29 | 17.4 | 23.8 | 0
1170 | 2022-10-04 19:30 | 17.4 | 23.7 | 0
1171 | 2022-10-04 19:31 | 17.4 | 23.8 | 0
1172 | 2022-10-04 19:32 | 17.5 | 23.6 | 0
1173 | 2022-10-04 19:33 | 17.4 | 23.9 | 0
1174 | 2022-10-04 19:34 | 17.2 | 23.6 | 0
1175 | 2022-10-04 19:35 | 17.2 | 23.5 | 0
1176 | 2022-10-04 19:36 | 17.2 | 23.9 | 0
1177 | 2022-10-04 19:37 | 17.3 | 23.8 | 0
1178 | 2022-10-04 19:38 | 17.3 | 23.6 | 0
1179 | 2022-10-04 19:39 | 17.2 | 23.6 | 0
1180 | 2022-10-04 19:40 | 17.3 | 23.7 | 0
1181 | 2022-10-04 19:41 | 17.1 | 23.6 | 0
1182 | 2022-10-04 19:42 | 17.2 | 23.6 | 0
1183 | 2022-10-04 19:43 | 17 | 23.6 | 0
1184 | 2022-10-04 19:44 | 17.1 | 23.4 | 0
1185 | 2022-10-04 19:45 | 17 | 23.7 | 0
1186 | 2022-10-04 19:46 | 17 | 23.6 | 0
1187 | 2022-10-04 19:47 | 17.1 | 23.9 | 0
1188 | 2022-10-04 19:48 | 17 | 23.6 | 0
1189 | 2022-10-04 19:49 | 16.9 | 23.5 | 0
1190 | 2022-10-04 19:50 | 17.1 | 23.8 | 0
1191 | 2022-10-04 19:51 | 16.9 | 23.6 | 0
1192 | 2022-10-04 19:52 | 16.9 | 23.6 | 0
1193 | 2022-10-04 19:53 | 16.9 | 23.6 | 0
1194 | 2022-10-04 19:54 | 16.9 | 23.6 | 0
1195 | 2022-10-04 19:55 | 16.8 | 23.5 | 0
1196 | 2022-10-04 19:56 | 16.8 | 23.6 | 0
1197 | 2022-10-04 19:57 | 16.9 | 23.6 | 0
1198 | 2022-10-04 19:58 | 16.9 | 23.6 | 0
1199 | 2022-10-04 19:59 | 17 | 23.3 | 0
1200 | 2022-10-04 20:00 | 16.8 | 23.5 | 0
1201 | 2022-10-04 20:01 | 16.7 | 24.4 | 0
1202 | 2022-10-04 20:02 | 16.6 | 23.8 | 0
1203 | 2022-10-04 20:03 | 16.6 | 24.2 | 0
1204 | 2022-10-04 20:04 | 16.7 | 23.9 | 0
1205 | 2022-10-04 20:05 | 16.9 | 23.4 | 0
1206 | 2022-10-04 20:06 | 17 | 23 | 0
1207 | 2022-10-04 20:07 | 16.9 | 23.4 | 0
1208 | 2022-10-04 20:08 | 16.9 | 23.1 | 0
1209 | 2022-10-04 20:09 | 16.7 | 24 | 0
1210 | 2022-10-04 20:10 | 16.8 | 23.7 | 0
1211 | 2022-10-04 20:11 | 16.7 | 23.7 | 0
1212 | 2022-10-04 20:12 | 16.9 | 23.2 | 0
1213 | 2022-10-04 20:13 | 16.9 | 23.2 | 0
1214 | 2022-10-04 20:14 | 16.7 | 23.6 | 0
1215 | 2022-10-04 20:15 | 16.5 | 23.7 | 0
1216 | 2022-10-04 20:16 | 16.5 | 24.5 | 0
1217 | 2022-10-04 20:17 | 16.6 | 23.7 | 0
1218 | 2022-10-04 20:18 | 16.5 | 24.3 | 0
1219 | 2022-10-04 20:19 | 16.5 | 24.3 | 0
1220 | 2022-10-04 20:20 | 16.6 | 24.4 | 0
1221 | 2022-10-04 20:21 | 16.5 | 24.1 | 0
1222 | 2022-10-04 20:22 | 16.8 | 23.1 | 0
1223 | 2022-10-04 20:23 | 16.7 | 23.6 | 0
1224 | 2022-10-04 20:24 | 16.5 | 24 | 0
1225 | 2022-10-04 20:25 | 16.5 | 24.2 | 0
1226 | 2022-10-04 20:26 | 16.5 | 24.1 | 0
1227 | 2022-10-04 20:27 | 16.7 | 23.1 | 0
1228 | 2022-10-04 20:28 | 16.5 | 24.1 | 0
1229 | 2022-10-04 20:29 | 16.6 | 23.8 | 0
1230 | 2022-10-04 20:30 | 16.6 | 23 | 0
1231 | 2022-10-04 20:31 | 16.5 | 24.1 | 0
1232 | 2022-10-04 20:32 | 16.3 | 23.4 | 0
1233 | 2022-10-04 20:33 | 16.1 | 23.6 | 0
1234 | 2022-10-04 20:34 | 16.3 | 24.1 | 0
1235 | 2022-10-04 20:35 | 16.2 | 23.5 | 0
1236 | 2022-10-04 20:36 | 16.2 | 23.6 | 0
1237 | 2022-10-04 20:37 | 16.1 | 23.3 | 0
1238 | 2022-10-04 20:38 | 16 | 23.6 | 0
1239 | 2022-10-04 20:39 | 16.4 | 24.1 | 0
1240 | 2022-10-04 20:40 | 16.5 | 24.3 | 0
1241 | 2022-10-04 20:41 | 16.2 | 24.1 | 0
1242 | 2022-10-04 20:42 | 16.1 | 23.8 | 0
1243 | 2022-10-04 20:43 | 16 | 23.4 | 0
1244 | 2022-10-04 20:44 | 16.1 | 24 | 0
1245 | 2022-10-04 20:45 | 15.9 | 23.1 | 0
1246 | 2022-10-04 20:46 | 16 | 22.9 | 0
1247 | 2022-10-04 20:47 | 16.1 | 23.1 | 0
1248 | 2022-10-04 20:48 | 16 | 23.7 | 0
1249 | 2022-10-04 20:49 | 16 | 23.7 | 0
1250 | 2022-10-04 20:50 | 15.7 | 23.4 | 0
1251 | 2022-10-04 20:51 | 15.6 | 23.3 | 0
1252 | 2022-10-04 20:52 | 15.7 | 23.5 | 0
1253 | 2022-10-04 20:53 | 15.6 | 23.3 | 0
1254 | 2022-10-04 20:54 | 15.8 | 23.9 | 0
1255 | 2022-10-04 20:55 | 15.6 | 23.4 | 0
1256 | 2022-10-04 20:56 | 15.5 | 23.6 | 0
1257 | 2022-10-04 20:57 | 15.6 | 24 | 0
1258 | 2022-10-04 20:58 | 15.8 | 23.3 | 0
1259 | 2022-10-04 20:59 | 15.7 | 23.3 | 0
1260 | 2022-10-04 21:00 | 15.6 | 23.8 | 0
1261 | 2022-10-04 21:01 | 15.7 | 23.3 | 0
1262 | 2022-10-04 21:02 | 15.7 | 23.7 | 0
1263 | 2022-10-04 21:03 | 15.6 | 23.5 | 0
1264 | 2022-10-04 21:04 | 15.6 | 23.5 | 0
1265 | 2022-10-04 21:05 | 15.5 | 23.5 | 0
1266 | 2022-10-04 21:06 | 15.7 | 23.5 | 0
1267 | 2022-10-04 21:07 | 15.8 | 23.4 | 0
1268 | 2022-10-04 21:08 | 15.7 | 23.7 | 0
1269 | 2022-10-04 21:09 | 15.6 | 23.1 | 0
1270 | 2022-10-04 21:10 | 15.7 | 22.9 | 0
1271 | 2022-10-04 21:11 | 15.9 | 23.6 | 0
1272 | 2022-10-04 21:12 | 15.5 | 23.5 | 0
1273 | 2022-10-04 21:13 | 15.8 | 23.5 | 0
1274 | 2022-10-04 21:14 | 15.8 | 24.4 | 0
1275 | 2022-10-04 21:15 | 15.9 | 24.5 | 0
1276 | 2022-10-04 21:16 | 15.8 | 23.5 | 0
1277 | 2022-10-04 21:17 | 15.6 | 23.6 | 0
1278 | 2022-10-04 21:18 | 15.5 | 23.1 | 0
1279 | 2022-10-04 21:19 | 15.7 | 23.8 | 0
1280 | 2022-10-04 21:20 | 15.7 | 23.8 | 0
1281 | 2022-10-04 21:21 | 15.4 | 23.1 | 0
1282 | 2022-10-04 21:22 | 15.5 | 22.8 | 0
1283 | 2022-10-04 21:23 | 15.5 | 23.7 | 0
1284 | 2022-10-04 21:24 | 15.4 | 23.9 | 0
1285 | 2022-10-04 21:25 | 15.5 | 23.7 | 0
1286 | 2022-10-04 21:26 | 15.7 | 23.6 | 0
1287 | 2022-10-04 21:27 | 15.4 | 23.3 | 0
1288 | 2022-10-04 21:28 | 15.2 | 23.4 | 0
1289 | 2022-10-04 21:29 | 15.1 | 22.8 | 0
1290 | 2022-10-04 21:30 | 15.3 | 23.3 | 0
1291 | 2022-10-04 21:31 | 15.2 | 23.4 | 0
1292 | 2022-10-04 21:32 | 15.3 | 23.6 | 0
1293 | 2022-10-04 21:33 | 15.3 | 23.4 | 0
1294 | 2022-10-04 21:34 | 15.2 | 23.5 | 0
1295 | 2022-10-04 21:35 | 15.4 | 23.5 | 0
1296 | 2022-10-04 21:36 | 15.6 | 23.2 | 0
1297 | 2022-10-04 21:37 | 15.3 | 24.2 | 0
1298 | 2022-10-04 21:38 | 15.4 | 23.6 | 0
1299 | 2022-10-04 21:39 | 15.2 | 23.5 | 0
1300 | 2022-10-04 21:40 | 14.9 | 23.7 | 0
1301 | 2022-10-04 21:41 | 15.1 | 23.4 | 0
1302 | 2022-10-04 21:42 | 15.2 | 23.5 | 0
1303 | 2022-10-04 21:43 | 15.2 | 23.4 | 0
1304 | 2022-10-04 21:44 | 15.3 | 23.5 | 0
1305 | 2022-10-04 21:45 | 15.5 | 23.7 | 0
1306 | 2022-10-04 21:46 | 15.6 | 23.9 | 0
1307 | 2022-10-04 21:47 | 15.4 | 23.4 | 0
1308 | 2022-10-04 21:48 | 15.5 | 23.6 | 0
1309 | 2022-10-04 21:49 | 15.4 | 24 | 0
1310 | 2022-10-04 21:50 | 15.5 | 24 | 0
1311 | 2022-10-04 21:51 | 15.9 | 23.5 | 0
1312 | 2022-10-04 21:52 | 16.3 | 24.1 | 0
1313 | 2022-10-04 21:53 | 16.1 | 23.6 | 0
1314 | 2022-10-04 21:54 | 15.7 | 23.4 | 0
1315 | 2022-10-04 21:55 | 15.8 | 23.7 | 0
1316 | 2022-10-04 21:56 | 16 | 23.4 | 0
1317 | 2022-10-04 21:57 | 16 | 23.4 | 0
1318 | 2022-10-04 21:58 | 16.1 | 23.5 | 0
1319 | 2022-10-04 21:59 | 15.8 | 24.4 | 0
1320 | 2022-10-04 22:00 | 15.6 | 24.2 | 0
1321 | 2022-10-04 22:01 | 15.3 | 23.5 | 0
1322 | 2022-10-04 22:02 | 15.3 | 23.5 | 0
1323 | 2022-10-04 22:03 | 15.5 | 23.5 | 0
1324 | 2022-10-04 22:04 | 15.7 | 23.4 | 0
1325 | 2022-10-04 22:05 | 15.6 | 23.6 | 0
1326 | 2022-10-04 22:06 | 15.5 | 23.3 | 0
1327 | 2022-10-04 22:07 | 15.9 | 23.2 | 0
1328 | 2022-10-04 22:08 | 15.7 | 22.8 | 0
1329 | 2022-10-04 22:09 | 15.4 | 24 | 0
1330 | 2022-10-04 22:10 | 15.4 | 23.4 | 0
1331 | 2022-10-04 22:11 | 15.2 | 22.8 | 0
1332 | 2022-10-04 22:12 | 15.1 | 22.9 | 0
1333 | 2022-10-04 22:13 | 14.9 | 23.7 | 0
1334 | 2022-10-04 22:14 | 14.8 | 22.9 | 0
1335 | 2022-10-04 22:15 | 14.9 | 23.6 | 0
1336 | 2022-10-04 22:16 | 14.9 | 23.1 | 0
1337 | 2022-10-04 22:17 | 15 | 23.3 | 0
1338 | 2022-10-04 22:18 | 14.9 | 23.9 | 0
1339 | 2022-10-04 22:19 | 14.8 | 23.3 | 0
1340 | 2022-10-04 22:20 | 14.6 | 23.4 | 0
1341 | 2022-10-04 22:21 | 14.3 | 23 | 0
1342 | 2022-10-04 22:22 | 14.3 | 24.3 | 0
1343 | 2022-10-04 22:23 | 14.2 | 23.7 | 0
1344 | 2022-10-04 22:24 | 14.3 | 24 | 0
1345 | 2022-10-04 22:25 | 14.5 | 23.3 | 0
1346 | 2022-10-04 22:26 | 14.8 | 23.6 | 0
1347 | 2022-10-04 22:27 | 15.2 | 23.6 | 0
1348 | 2022-10-04 22:28 | 14.8 | 23.4 | 0
1349 | 2022-10-04 22:29 | 14.6 | 23.1 | 0
1350 | 2022-10-04 22:30 | 14.3 | 23.2 | 0
1351 | 2022-10-04 22:31 | 14.2 | 23.3 | 0
1352 | 2022-10-04 22:32 | 14.2 | 23.6 | 0
1353 | 2022-10-04 22:33 | 14.2 | 23.3 | 0
1354 | 2022-10-04 22:34 | 14.1 | 23.5 | 0
1355 | 2022-10-04 22:35 | 14.2 | 24 | 0
1356 | 2022-10-04 22:36 | 14.2 | 23.3 | 0
1357 | 2022-10-04 22:37 | 14.1 | 23.6 | 0
1358 | 2022-10-04 22:38 | 14 | 23.8 | 0
1359 | 2022-10-04 22:39 | 14.1 | 23.9 | 0
1360 | 2022-10-04 22:40 | 14 | 23.5 | 0
1361 | 2022-10-04 22:41 | 14 | 23.5 | 0
1362 | 2022-10-04 22:42 | 14 | 23.4 | 0
1363 | 2022-10-04 22:43 | 14 | 23.5 | 0
1364 | 2022-10-04 22:44 | 14.3 | 23.7 | 0
1365 | 2022-10-04 22:45 | 14.6 | 23.5 | 0
1366 | 2022-10-04 22:46 | 14.6 | 24.1 | 0
1367 | 2022-10-04 22:47 | 14.8 | 23.4 | 0
1368 | 2022-10-04 22:48 | 15 | 24.2 | 0
1369 | 2022-10-04 22:49 | 14.6 | 23.7 | 0
1370 | 2022-10-04 22:50 | 14.5 | 23.7 | 0
1371 | 2022-10-04 22:51 | 14.4 | 23.5 | 0
1372 | 2022-10-04 22:52 | 14.3 | 23.4 | 0
1373 | 2022-10-04 22:53 | 14.6 | 23.9 | 0
1374 | 2022-10-04 22:54 | 14.8 | 23.4 | 0
1375 | 2022-10-04 22:55 | 14.9 | 23.4 | 0
1376 | 2022-10-04 22:56 | 14.6 | 23.2 | 0
1377 | 2022-10-04 22:57 | 14.7 | 23.8 | 0
1378 | 2022-10-04 22:58 | 14.7 | 23.4 | 0
1379 | 2022-10-04 22:59 | 14.8 | 23.5 | 0
1380 | 2022-10-04 23:00 | 14.9 | 23.6 | 0
1381 | 2022-10-04 23:01 | 14.8 | 23.4 | 0
1382 | 2022-10-04 23:02 | 14.8 | 23.5 | 0
1383 | 2022-10-04 23:03 | 15.4 | 23.4 | 0
1384 | 2022-10-04 23:04 | 15.2 | 23.4 | 0
1385 | 2022-10-04 23:05 | 15 | 23.5 | 0
1386 | 2022-10-04 23:06 | 14.9 | 23.5 | 0
1387 | 2022-10-04 23:07 | 15.2 | 23.3 | 0
1388 | 2022-10-04 23:08 | 15.4 | 23.5 | 0
1389 | 2022-10-04 23:09 | 15.4 | 23.2 | 0
1390 | 2022-10-04 23:10 | 15.2 | 23.5 | 0
1391 | 2022-10-04 23:11 | 15 | 23.3 | 0
1392 | 2022-10-04 23:12 | 15 | 23.6 | 0
1393 | 2022-10-04 23:13 | 15.3 | 23.3 | 0
1394 | 2022-10-04 23:14 | 15.3 | 23.8 | 0
1395 | 2022-10-04 23:15 | 15.2 | 22.8 | 0
1396 | 2022-10-04 23:16 | 15.1 | 23.5 | 0
1397 | 2022-10-04 23:17 | 15.3 | 23.6 | 0
1398 | 2022-10-04 23:18 | 15.6 | 23.5 | 0
1399 | 2022-10-04 23:19 | 15.3 | 23.1 | 0
1400 | 2022-10-04 23:20 | 15.7 | 23.6 | 0
1401 | 2022-10-04 23:21 | 15.7 | 24.2 | 0
1402 | 2022-10-04 23:22 | 15.4 | 23.3 | 0
1403 | 2022-10-04 23:23 | 15.5 | 23.1 | 0
1404 | 2022-10-04 23:24 | 15.3 | 23.2 | 0
1405 | 2022-10-04 23:25 | 15.3 | 23.6 | 0
1406 | 2022-10-04 23:26 | 15.8 | 23.8 | 0
1407 | 2022-10-04 23:27 | 15.7 | 23.5 | 0
1408 | 2022-10-04 23:28 | 15.8 | 23.3 | 0
1409 | 2022-10-04 23:29 | 16.1 | 24.2 | 0
1410 | 2022-10-04 23:30 | 16.2 | 23.7 | 0
1411 | 2022-10-04 23:31 | 16 | 23.5 | 0
1412 | 2022-10-04 23:32 | 16 | 23.8 | 0
1413 | 2022-10-04 23:33 | 16 | 23.3 | 0
1414 | 2022-10-04 23:34 | 16.1 | 23 | 0
1415 | 2022-10-04 23:35 | 15.7 | 23.7 | 0
1416 | 2022-10-04 23:36 | 15.7 | 23.3 | 0
1417 | 2022-10-04 23:37 | 15.7 | 22.7 | 0
1418 | 2022-10-04 23:38 | 15.6 | 23.3 | 0
1419 | 2022-10-04 23:39 | 15.5 | 22.8 | 0
1420 | 2022-10-04 23:40 | 15.7 | 24 | 0
1421 | 2022-10-04 23:41 | 15.7 | 23.3 | 0
1422 | 2022-10-04 23:42 | 15.8 | 23.5 | 0
1423 | 2022-10-04 23:43 | 15.7 | 23.5 | 0
1424 | 2022-10-04 23:44 | 15.7 | 23.6 | 0
1425 | 2022-10-04 23:45 | 15.7 | 23.5 | 0
1426 | 2022-10-04 23:46 | 15.4 | 23.6 | 0
1427 | 2022-10-04 23:47 | 15.3 | 23.1 | 0
1428 | 2022-10-04 23:48 | 15 | 24.1 | 0
1429 | 2022-10-04 23:49 | 14.9 | 23.4 | 0
1430 | 2022-10-04 23:50 | 15.2 | 23.6 | 0
1431 | 2022-10-04 23:51 | 15 | 23.1 | 0
1432 | 2022-10-04 23:52 | 14.7 | 23.5 | 0
1433 | 2022-10-04 23:53 | 14.8 | 23.5 | 0
1434 | 2022-10-04 23:54 | 14.7 | 23.6 | 0
1435 | 2022-10-04 23:55 | 14.6 | 23.6 | 0
1436 | 2022-10-04 23:56 | 14.6 | 23.2 | 0
1437 | 2022-10-04 23:57 | 14.8 | 23.3 | 0
1438 | 2022-10-04 23:58 | 14.7 | 23.4 | 0
1439 | 2022-10-04 23:59 | 14.5 | 23.7 | 0

## 05-10-2022_NO HEAT
| Date&time_x | OUTDOOR_TEMP | INDOOR_TEMP | PYRANOMETER
0 | 2022-10-05 | 14.4 | 23.2 | 0
1 | 2022-10-05 00:01 | 14.2 | 23.4 | 0
2 | 2022-10-05 00:02 | 14.2 | 23.6 | 0
3 | 2022-10-05 00:03 | 14.1 | 23.4 | 0
4 | 2022-10-05 00:04 | 14.2 | 23.3 | 0
5 | 2022-10-05 00:05 | 14 | 23.2 | 0
6 | 2022-10-05 00:06 | 13.9 | 23.7 | 0
7 | 2022-10-05 00:07 | 13.8 | 23.6 | 0
8 | 2022-10-05 00:08 | 13.6 | 23.6 | 0
9 | 2022-10-05 00:09 | 13.8 | 23.1 | 0
10 | 2022-10-05 00:10 | 13.7 | 23 | 0
11 | 2022-10-05 00:11 | 13.8 | 23.7 | 0
12 | 2022-10-05 00:12 | 13.6 | 23.5 | 0
13 | 2022-10-05 00:13 | 13.7 | 23.4 | 0
14 | 2022-10-05 00:14 | 13.6 | 23.7 | 0
15 | 2022-10-05 00:15 | 13.8 | 23.4 | 0
16 | 2022-10-05 00:16 | 13.7 | 23.7 | 0
17 | 2022-10-05 00:17 | 13.5 | 23.4 | 0
18 | 2022-10-05 00:18 | 13.5 | 23.3 | 0
19 | 2022-10-05 00:19 | 13.4 | 23.4 | 0
20 | 2022-10-05 00:20 | 13.4 | 23.5 | 0
21 | 2022-10-05 00:21 | 13.3 | 24.1 | 0
22 | 2022-10-05 00:22 | 13.4 | 23.9 | 0
23 | 2022-10-05 00:23 | 13.2 | 23 | 0
24 | 2022-10-05 00:24 | 13.3 | 23.8 | 0
25 | 2022-10-05 00:25 | 13.3 | 23.3 | 0
26 | 2022-10-05 00:26 | 13.3 | 23.3 | 0
27 | 2022-10-05 00:27 | 13.1 | 23.3 | 0
28 | 2022-10-05 00:28 | 13 | 23.3 | 0
29 | 2022-10-05 00:29 | 13.2 | 23.4 | 0
30 | 2022-10-05 00:30 | 13.3 | 23.4 | 0
31 | 2022-10-05 00:31 | 13.2 | 23.1 | 0
32 | 2022-10-05 00:32 | 13.1 | 24 | 0
33 | 2022-10-05 00:33 | 13.2 | 23.6 | 0
34 | 2022-10-05 00:34 | 13.1 | 24.1 | 0
35 | 2022-10-05 00:35 | 13.1 | 22.9 | 0
36 | 2022-10-05 00:36 | 13.1 | 23.4 | 0
37 | 2022-10-05 00:37 | 13.2 | 23.9 | 0
38 | 2022-10-05 00:38 | 13.8 | 23.4 | 0
39 | 2022-10-05 00:39 | 14.4 | 23.6 | 0
40 | 2022-10-05 00:40 | 14.3 | 22.9 | 0
41 | 2022-10-05 00:41 | 14.8 | 23.6 | 0
42 | 2022-10-05 00:42 | 14.2 | 23.1 | 0
43 | 2022-10-05 00:43 | 14 | 23.4 | 0
44 | 2022-10-05 00:44 | 14.6 | 23.8 | 0
45 | 2022-10-05 00:45 | 15.1 | 24.1 | 0
46 | 2022-10-05 00:46 | 15.7 | 23.8 | 0
47 | 2022-10-05 00:47 | 15.8 | 23.5 | 0
48 | 2022-10-05 00:48 | 15.9 | 23.1 | 0
49 | 2022-10-05 00:49 | 15.7 | 24 | 0
50 | 2022-10-05 00:50 | 15.8 | 23.3 | 0
51 | 2022-10-05 00:51 | 15.7 | 23.1 | 0
52 | 2022-10-05 00:52 | 15.9 | 23.3 | 0
53 | 2022-10-05 00:53 | 15.9 | 23.5 | 0
54 | 2022-10-05 00:54 | 15.9 | 23.3 | 0
55 | 2022-10-05 00:55 | 16 | 23.3 | 0
56 | 2022-10-05 00:56 | 16.3 | 23.6 | 0
57 | 2022-10-05 00:57 | 16.3 | 23.4 | 0
58 | 2022-10-05 00:58 | 16.4 | 23.2 | 0
59 | 2022-10-05 00:59 | 16.5 | 23.5 | 0
60 | 2022-10-05 01:00 | 16.3 | 23 | 0
61 | 2022-10-05 01:01 | 16.3 | 22.9 | 0
62 | 2022-10-05 01:02 | 16.3 | 22.7 | 0
63 | 2022-10-05 01:03 | 16.2 | 23.6 | 0
64 | 2022-10-05 01:04 | 16.3 | 23.2 | 0
65 | 2022-10-05 01:05 | 16.2 | 23.2 | 0
66 | 2022-10-05 01:06 | 16.4 | 23.3 | 0
67 | 2022-10-05 01:07 | 16.4 | 23.3 | 0
68 | 2022-10-05 01:08 | 16.6 | 23.4 | 0
69 | 2022-10-05 01:09 | 16.2 | 23.4 | 0
70 | 2022-10-05 01:10 | 16.1 | 23.5 | 0
71 | 2022-10-05 01:11 | 16.1 | 23.5 | 0
72 | 2022-10-05 01:12 | 16.3 | 23.3 | 0
73 | 2022-10-05 01:13 | 16.4 | 23.5 | 0
74 | 2022-10-05 01:14 | 16.4 | 23.3 | 0
75 | 2022-10-05 01:15 | 16.5 | 23.7 | 0
76 | 2022-10-05 01:16 | 16.3 | 23.3 | 0
77 | 2022-10-05 01:17 | 16.3 | 23.4 | 0
78 | 2022-10-05 01:18 | 16.4 | 23.7 | 0
79 | 2022-10-05 01:19 | 16.4 | 23.7 | 0
80 | 2022-10-05 01:20 | 16.3 | 23.4 | 0
81 | 2022-10-05 01:21 | 16.4 | 23.1 | 0
82 | 2022-10-05 01:22 | 16.3 | 23.6 | 0
83 | 2022-10-05 01:23 | 16.2 | 23.5 | 0
84 | 2022-10-05 01:24 | 16.3 | 23.6 | 0
85 | 2022-10-05 01:25 | 16.4 | 23.2 | 0
86 | 2022-10-05 01:26 | 16.5 | 22.8 | 0
87 | 2022-10-05 01:27 | 16.2 | 23.8 | 0
88 | 2022-10-05 01:28 | 16.2 | 23.8 | 0
89 | 2022-10-05 01:29 | 16.1 | 23.5 | 0
90 | 2022-10-05 01:30 | 15.9 | 23.4 | 0
91 | 2022-10-05 01:31 | 16 | 23.7 | 0
92 | 2022-10-05 01:32 | 16.3 | 24.3 | 0
93 | 2022-10-05 01:33 | 16.3 | 23.1 | 0
94 | 2022-10-05 01:34 | 16.4 | 23.1 | 0
95 | 2022-10-05 01:35 | 16.4 | 23.2 | 0
96 | 2022-10-05 01:36 | 16.2 | 23.8 | 0
97 | 2022-10-05 01:37 | 16.3 | 23.5 | 0
98 | 2022-10-05 01:38 | 16.3 | 23.3 | 0
99 | 2022-10-05 01:39 | 16.4 | 23.2 | 0
100 | 2022-10-05 01:40 | 16.5 | 23.8 | 0
101 | 2022-10-05 01:41 | 16.4 | 23.1 | 0
102 | 2022-10-05 01:42 | 16.3 | 23.6 | 0
103 | 2022-10-05 01:43 | 16 | 23.5 | 0
104 | 2022-10-05 01:44 | 16.3 | 22.9 | 0
105 | 2022-10-05 01:45 | 16.3 | 23 | 0
106 | 2022-10-05 01:46 | 16.1 | 23.4 | 0
107 | 2022-10-05 01:47 | 16.3 | 23.4 | 0
108 | 2022-10-05 01:48 | 16.3 | 23.6 | 0
109 | 2022-10-05 01:49 | 16.4 | 23.4 | 0
110 | 2022-10-05 01:50 | 16.4 | 23.2 | 0
111 | 2022-10-05 01:51 | 16.3 | 23.7 | 0
112 | 2022-10-05 01:52 | 16.1 | 23.5 | 0
113 | 2022-10-05 01:53 | 16.2 | 23.1 | 0
114 | 2022-10-05 01:54 | 16.2 | 23.4 | 0
115 | 2022-10-05 01:55 | 16.2 | 23.5 | 0
116 | 2022-10-05 01:56 | 16.4 | 23.7 | 0
117 | 2022-10-05 01:57 | 16.3 | 23.3 | 0
118 | 2022-10-05 01:58 | 16.2 | 23.2 | 0
119 | 2022-10-05 01:59 | 16.1 | 23.1 | 0
120 | 2022-10-05 02:00 | 16 | 23.4 | 0
121 | 2022-10-05 02:01 | 16 | 23.3 | 0
122 | 2022-10-05 02:02 | 16.1 | 23.3 | 0
123 | 2022-10-05 02:03 | 16.1 | 22.8 | 0
124 | 2022-10-05 02:04 | 15.8 | 23.2 | 0
125 | 2022-10-05 02:05 | 15.7 | 24.3 | 0
126 | 2022-10-05 02:06 | 15.7 | 23.6 | 0
127 | 2022-10-05 02:07 | 15.8 | 23.8 | 0
128 | 2022-10-05 02:08 | 16 | 23.5 | 0
129 | 2022-10-05 02:09 | 15.8 | 22.9 | 0
130 | 2022-10-05 02:10 | 15.9 | 23.3 | 0
131 | 2022-10-05 02:11 | 16.1 | 23.5 | 0
132 | 2022-10-05 02:12 | 16.4 | 22.5 | 0
133 | 2022-10-05 02:13 | 16.4 | 23.2 | 0
134 | 2022-10-05 02:14 | 16 | 23.4 | 0
135 | 2022-10-05 02:15 | 16.1 | 23.4 | 0
136 | 2022-10-05 02:16 | 16.2 | 23.1 | 0
137 | 2022-10-05 02:17 | 16.5 | 23.1 | 0
138 | 2022-10-05 02:18 | 16.6 | 23.5 | 0
139 | 2022-10-05 02:19 | 16.6 | 23.6 | 0
140 | 2022-10-05 02:20 | 16.6 | 22.7 | 0
141 | 2022-10-05 02:21 | 16.6 | 22.6 | 0
142 | 2022-10-05 02:22 | 16.6 | 23.2 | 0
143 | 2022-10-05 02:23 | 16.5 | 23.1 | 0
144 | 2022-10-05 02:24 | 16.5 | 23.4 | 0
145 | 2022-10-05 02:25 | 16.5 | 23.4 | 0
146 | 2022-10-05 02:26 | 16.4 | 23.5 | 0
147 | 2022-10-05 02:27 | 16.5 | 24 | 0
148 | 2022-10-05 02:28 | 16.4 | 23.5 | 0
149 | 2022-10-05 02:29 | 16.3 | 23.2 | 0
150 | 2022-10-05 02:30 | 16.2 | 23.1 | 0
151 | 2022-10-05 02:31 | 16 | 23.4 | 0
152 | 2022-10-05 02:32 | 16 | 23.5 | 0
153 | 2022-10-05 02:33 | 16.2 | 23 | 0
154 | 2022-10-05 02:34 | 16.1 | 23.6 | 0
155 | 2022-10-05 02:35 | 16.1 | 23.5 | 0
156 | 2022-10-05 02:36 | 16 | 23.9 | 0
157 | 2022-10-05 02:37 | 16.3 | 24 | 0
158 | 2022-10-05 02:38 | 16.2 | 22.8 | 0
159 | 2022-10-05 02:39 | 16.1 | 22.4 | 0
160 | 2022-10-05 02:40 | 16.4 | 22.4 | 0
161 | 2022-10-05 02:41 | 16.4 | 23.2 | 0
162 | 2022-10-05 02:42 | 16.2 | 23.4 | 0
163 | 2022-10-05 02:43 | 16.3 | 23 | 0
164 | 2022-10-05 02:44 | 16.3 | 23.8 | 0
165 | 2022-10-05 02:45 | 16.1 | 23.4 | 0
166 | 2022-10-05 02:46 | 16 | 23.1 | 0
167 | 2022-10-05 02:47 | 16 | 23.6 | 0
168 | 2022-10-05 02:48 | 16 | 24.3 | 0
169 | 2022-10-05 02:49 | 15.8 | 23.4 | 0
170 | 2022-10-05 02:50 | 15.3 | 23.1 | 0
171 | 2022-10-05 02:51 | 15.2 | 22.6 | 0
172 | 2022-10-05 02:52 | 15.4 | 23.2 | 0
173 | 2022-10-05 02:53 | 15.2 | 23.3 | 0
174 | 2022-10-05 02:54 | 14.9 | 23.3 | 0
175 | 2022-10-05 02:55 | 14.8 | 22.4 | 0
176 | 2022-10-05 02:56 | 14.7 | 22.8 | 0
177 | 2022-10-05 02:57 | 14.8 | 23.1 | 0
178 | 2022-10-05 02:58 | 15 | 23.3 | 0
179 | 2022-10-05 02:59 | 15.3 | 23.1 | 0
180 | 2022-10-05 03:00 | 15.2 | 24 | 0
181 | 2022-10-05 03:01 | 15.4 | 23.4 | 0
182 | 2022-10-05 03:02 | 15.1 | 23.1 | 0
183 | 2022-10-05 03:03 | 15.4 | 23.1 | 0
184 | 2022-10-05 03:04 | 15.1 | 23.4 | 0
185 | 2022-10-05 03:05 | 15.5 | 23 | 0
186 | 2022-10-05 03:06 | 15.4 | 23.4 | 0
187 | 2022-10-05 03:07 | 15.2 | 23.4 | 0
188 | 2022-10-05 03:08 | 15.1 | 23 | 0
189 | 2022-10-05 03:09 | 15.2 | 23.3 | 0
190 | 2022-10-05 03:10 | 15.5 | 23.3 | 0
191 | 2022-10-05 03:11 | 15.5 | 23.4 | 0
192 | 2022-10-05 03:12 | 15.4 | 23.7 | 0
193 | 2022-10-05 03:13 | 15.2 | 23.2 | 0
194 | 2022-10-05 03:14 | 14.9 | 23.6 | 0
195 | 2022-10-05 03:15 | 14.6 | 23.1 | 0
196 | 2022-10-05 03:16 | 14.5 | 23 | 0
197 | 2022-10-05 03:17 | 14.5 | 23.4 | 0
198 | 2022-10-05 03:18 | 14.3 | 23.4 | 0
199 | 2022-10-05 03:19 | 14.1 | 23.1 | 0
200 | 2022-10-05 03:20 | 14 | 23.2 | 0
201 | 2022-10-05 03:21 | 14.1 | 22.9 | 0
202 | 2022-10-05 03:22 | 13.8 | 23.4 | 0
203 | 2022-10-05 03:23 | 13.8 | 23.2 | 0
204 | 2022-10-05 03:24 | 13.7 | 23.5 | 0
205 | 2022-10-05 03:25 | 13.7 | 22.8 | 0
206 | 2022-10-05 03:26 | 13.5 | 23.5 | 0
207 | 2022-10-05 03:27 | 13.4 | 23.2 | 0
208 | 2022-10-05 03:28 | 13.5 | 23.1 | 0
209 | 2022-10-05 03:29 | 13.4 | 23.5 | 0
210 | 2022-10-05 03:30 | 13.3 | 23.4 | 0
211 | 2022-10-05 03:31 | 13.2 | 23 | 0
212 | 2022-10-05 03:32 | 13.2 | 23 | 0
213 | 2022-10-05 03:33 | 13.4 | 23.3 | 0
214 | 2022-10-05 03:34 | 13.2 | 23.2 | 0
215 | 2022-10-05 03:35 | 13.1 | 23.3 | 0
216 | 2022-10-05 03:36 | 13 | 23.4 | 0
217 | 2022-10-05 03:37 | 13 | 23.4 | 0
218 | 2022-10-05 03:38 | 13 | 23.2 | 0
219 | 2022-10-05 03:39 | 12.8 | 23.2 | 0
220 | 2022-10-05 03:40 | 12.7 | 23.3 | 0
221 | 2022-10-05 03:41 | 13 | 22.7 | 0
222 | 2022-10-05 03:42 | 12.7 | 23.3 | 0
223 | 2022-10-05 03:43 | 12.8 | 22.8 | 0
224 | 2022-10-05 03:44 | 12.7 | 23.4 | 0
225 | 2022-10-05 03:45 | 12.7 | 23.4 | 0
226 | 2022-10-05 03:46 | 12.5 | 23.3 | 0
227 | 2022-10-05 03:47 | 12.7 | 23.3 | 0
228 | 2022-10-05 03:48 | 12.6 | 23.2 | 0
229 | 2022-10-05 03:49 | 12.6 | 23.2 | 0
230 | 2022-10-05 03:50 | 12.5 | 23.5 | 0
231 | 2022-10-05 03:51 | 12.6 | 23.3 | 0
232 | 2022-10-05 03:52 | 12.4 | 23.1 | 0
233 | 2022-10-05 03:53 | 12.4 | 23.3 | 0
234 | 2022-10-05 03:54 | 12.3 | 23.2 | 0
235 | 2022-10-05 03:55 | 12.4 | 23.2 | 0
236 | 2022-10-05 03:56 | 12.4 | 23.2 | 0
237 | 2022-10-05 03:57 | 12.3 | 23.1 | 0
238 | 2022-10-05 03:58 | 12.4 | 23.3 | 0
239 | 2022-10-05 03:59 | 12.2 | 23 | 0
240 | 2022-10-05 04:00 | 12.3 | 23.4 | 0
241 | 2022-10-05 04:01 | 12.2 | 23.1 | 0
242 | 2022-10-05 04:02 | 12.3 | 23.5 | 0
243 | 2022-10-05 04:03 | 12.2 | 23.1 | 0
244 | 2022-10-05 04:04 | 12.4 | 23.8 | 0
245 | 2022-10-05 04:05 | 12.4 | 23 | 0
246 | 2022-10-05 04:06 | 12.5 | 23.2 | 0
247 | 2022-10-05 04:07 | 12.5 | 23.3 | 0
248 | 2022-10-05 04:08 | 12.4 | 23.5 | 0
249 | 2022-10-05 04:09 | 12.7 | 23.2 | 0
250 | 2022-10-05 04:10 | 12.9 | 23.5 | 0
251 | 2022-10-05 04:11 | 13.1 | 22.8 | 0
252 | 2022-10-05 04:12 | 13.1 | 23.5 | 0
253 | 2022-10-05 04:13 | 13.1 | 23.2 | 0
254 | 2022-10-05 04:14 | 13.8 | 24.1 | 0
255 | 2022-10-05 04:15 | 13.7 | 23.3 | 0
256 | 2022-10-05 04:16 | 13.2 | 23.1 | 0
257 | 2022-10-05 04:17 | 13.1 | 23 | 0
258 | 2022-10-05 04:18 | 12.9 | 22.9 | 0
259 | 2022-10-05 04:19 | 12.8 | 23.2 | 0
260 | 2022-10-05 04:20 | 12.7 | 23.1 | 0
261 | 2022-10-05 04:21 | 12.8 | 23.4 | 0
262 | 2022-10-05 04:22 | 12.7 | 22.5 | 0
263 | 2022-10-05 04:23 | 12.8 | 23.7 | 0
264 | 2022-10-05 04:24 | 12.6 | 22.8 | 0
265 | 2022-10-05 04:25 | 12.7 | 23.4 | 0
266 | 2022-10-05 04:26 | 12.7 | 22.5 | 0
267 | 2022-10-05 04:27 | 12.5 | 22.6 | 0
268 | 2022-10-05 04:28 | 12.6 | 23.6 | 0
269 | 2022-10-05 04:29 | 12.6 | 22.9 | 0
270 | 2022-10-05 04:30 | 12.8 | 23.8 | 0
271 | 2022-10-05 04:31 | 12.8 | 22.7 | 0
272 | 2022-10-05 04:32 | 12.6 | 23.7 | 0
273 | 2022-10-05 04:33 | 12.5 | 23.8 | 0
274 | 2022-10-05 04:34 | 12.6 | 23 | 0
275 | 2022-10-05 04:35 | 12.6 | 23.7 | 0
276 | 2022-10-05 04:36 | 12.6 | 23 | 0
277 | 2022-10-05 04:37 | 12.3 | 23.7 | 0
278 | 2022-10-05 04:38 | 12.3 | 22.5 | 0
279 | 2022-10-05 04:39 | 12.3 | 22.8 | 0
280 | 2022-10-05 04:40 | 12.3 | 22.8 | 0
281 | 2022-10-05 04:41 | 12.2 | 23.1 | 0
282 | 2022-10-05 04:42 | 12.1 | 23.5 | 0
283 | 2022-10-05 04:43 | 12.3 | 23.3 | 0
284 | 2022-10-05 04:44 | 12.2 | 23.1 | 0
285 | 2022-10-05 04:45 | 12.2 | 23.1 | 0
286 | 2022-10-05 04:46 | 12 | 22.8 | 0
287 | 2022-10-05 04:47 | 12 | 22.9 | 0
288 | 2022-10-05 04:48 | 11.9 | 23.2 | 0
289 | 2022-10-05 04:49 | 12 | 23.1 | 0
290 | 2022-10-05 04:50 | 12 | 23.4 | 0
291 | 2022-10-05 04:51 | 12 | 23.1 | 0
292 | 2022-10-05 04:52 | 12 | 24.2 | 0
293 | 2022-10-05 04:53 | 11.8 | 23.3 | 0
294 | 2022-10-05 04:54 | 11.8 | 22.4 | 0
295 | 2022-10-05 04:55 | 12 | 23.4 | 0
296 | 2022-10-05 04:56 | 12 | 23.3 | 0
297 | 2022-10-05 04:57 | 11.8 | 23 | 0
298 | 2022-10-05 04:58 | 12.2 | 22.5 | 0
299 | 2022-10-05 04:59 | 12 | 23.6 | 0
300 | 2022-10-05 05:00 | 12.1 | 23.1 | 0
301 | 2022-10-05 05:01 | 12 | 24.1 | 0
302 | 2022-10-05 05:02 | 11.9 | 23.4 | 0
303 | 2022-10-05 05:03 | 11.7 | 23 | 0
304 | 2022-10-05 05:04 | 11.8 | 22.9 | 0
305 | 2022-10-05 05:05 | 11.8 | 23.3 | 0
306 | 2022-10-05 05:06 | 11.7 | 22.6 | 0
307 | 2022-10-05 05:07 | 11.9 | 22.4 | 0
308 | 2022-10-05 05:08 | 11.7 | 23.6 | 0
309 | 2022-10-05 05:09 | 11.7 | 22.3 | 0
310 | 2022-10-05 05:10 | 11.9 | 23.5 | 0
311 | 2022-10-05 05:11 | 11.8 | 24 | 0
312 | 2022-10-05 05:12 | 12 | 23.1 | 0
313 | 2022-10-05 05:13 | 11.8 | 23.6 | 0
314 | 2022-10-05 05:14 | 11.7 | 22.5 | 0
315 | 2022-10-05 05:15 | 11.5 | 23.5 | 0
316 | 2022-10-05 05:16 | 11.9 | 22.9 | 0
317 | 2022-10-05 05:17 | 11.7 | 23.4 | 0
318 | 2022-10-05 05:18 | 11.9 | 23.1 | 0
319 | 2022-10-05 05:19 | 12 | 22.8 | 0
320 | 2022-10-05 05:20 | 11.9 | 23 | 0
321 | 2022-10-05 05:21 | 12 | 23 | 0
322 | 2022-10-05 05:22 | 11.9 | 23 | 0
323 | 2022-10-05 05:23 | 12 | 22.9 | 0
324 | 2022-10-05 05:24 | 11.7 | 23.8 | 0
325 | 2022-10-05 05:25 | 11.9 | 22.6 | 0
326 | 2022-10-05 05:26 | 11.7 | 23.4 | 0
327 | 2022-10-05 05:27 | 11.8 | 22.3 | 0
328 | 2022-10-05 05:28 | 11.8 | 23.5 | 0
329 | 2022-10-05 05:29 | 11.8 | 23.8 | 0
330 | 2022-10-05 05:30 | 11.8 | 22.4 | 0
331 | 2022-10-05 05:31 | 11.7 | 23.3 | 0
332 | 2022-10-05 05:32 | 11.7 | 23.3 | 0
333 | 2022-10-05 05:33 | 11.7 | 23.3 | 0
334 | 2022-10-05 05:34 | 11.6 | 22.6 | 0
335 | 2022-10-05 05:35 | 11.7 | 22.7 | 0
336 | 2022-10-05 05:36 | 11.7 | 23 | 0
337 | 2022-10-05 05:37 | 11.6 | 23.6 | 0
338 | 2022-10-05 05:38 | 11.7 | 22.6 | 0
339 | 2022-10-05 05:39 | 11.8 | 23.4 | 0
340 | 2022-10-05 05:40 | 11.8 | 24 | 0
341 | 2022-10-05 05:41 | 11.5 | 23.8 | 0
342 | 2022-10-05 05:42 | 11.7 | 22.7 | 0
343 | 2022-10-05 05:43 | 11.6 | 23.6 | 0
344 | 2022-10-05 05:44 | 11.5 | 22.9 | 0
345 | 2022-10-05 05:45 | 11.4 | 23 | 0
346 | 2022-10-05 05:46 | 11.5 | 22.7 | 0
347 | 2022-10-05 05:47 | 11.4 | 22.8 | 0
348 | 2022-10-05 05:48 | 11.3 | 23 | 0
349 | 2022-10-05 05:49 | 11.5 | 22.5 | 0
350 | 2022-10-05 05:50 | 11.4 | 23.1 | 0
351 | 2022-10-05 05:51 | 11.5 | 22.9 | 0
352 | 2022-10-05 05:52 | 11.5 | 22.8 | 0
353 | 2022-10-05 05:53 | 11.4 | 22.9 | 0
354 | 2022-10-05 05:54 | 11.3 | 23.2 | 0
355 | 2022-10-05 05:55 | 11.4 | 23.1 | 0
356 | 2022-10-05 05:56 | 11.3 | 22.9 | 0
357 | 2022-10-05 05:57 | 11.4 | 23 | 0
358 | 2022-10-05 05:58 | 11.5 | 23 | 0
359 | 2022-10-05 05:59 | 11.5 | 22.7 | 0
360 | 2022-10-05 06:00 | 11.4 | 22.9 | 0
361 | 2022-10-05 06:01 | 11.4 | 22.9 | 0
362 | 2022-10-05 06:02 | 11.5 | 23 | 0
363 | 2022-10-05 06:03 | 11.3 | 22.7 | 0
364 | 2022-10-05 06:04 | 11.2 | 23 | 0
365 | 2022-10-05 06:05 | 11.2 | 22.8 | 0
366 | 2022-10-05 06:06 | 11.4 | 23.4 | 0
367 | 2022-10-05 06:07 | 11.2 | 22.9 | 0
368 | 2022-10-05 06:08 | 11.3 | 23.3 | 0
369 | 2022-10-05 06:09 | 11.3 | 23.1 | 0
370 | 2022-10-05 06:10 | 11.4 | 22.9 | 0
371 | 2022-10-05 06:11 | 11.4 | 23 | 0
372 | 2022-10-05 06:12 | 11.1 | 22.7 | 0
373 | 2022-10-05 06:13 | 11.1 | 23.1 | 0
374 | 2022-10-05 06:14 | 11.3 | 22.9 | 0
375 | 2022-10-05 06:15 | 11.3 | 22.8 | 0
376 | 2022-10-05 06:16 | 11.3 | 23.2 | 0
377 | 2022-10-05 06:17 | 11.2 | 23 | 0
378 | 2022-10-05 06:18 | 11.2 | 23.2 | 0
379 | 2022-10-05 06:19 | 11.3 | 22.9 | 0
380 | 2022-10-05 06:20 | 11.2 | 23 | 0
381 | 2022-10-05 06:21 | 11.5 | 23.2 | 0
382 | 2022-10-05 06:22 | 11.4 | 23.3 | 0
383 | 2022-10-05 06:23 | 11.3 | 22.4 | 0
384 | 2022-10-05 06:24 | 11.2 | 22.6 | 0
385 | 2022-10-05 06:25 | 11.2 | 23 | 0
386 | 2022-10-05 06:26 | 11.3 | 23 | 0
387 | 2022-10-05 06:27 | 11.2 | 23 | 0
388 | 2022-10-05 06:28 | 11.1 | 23.2 | 0
389 | 2022-10-05 06:29 | 11.3 | 23 | 0
390 | 2022-10-05 06:30 | 11.2 | 23.2 | 0
391 | 2022-10-05 06:31 | 11.3 | 23.4 | 0
392 | 2022-10-05 06:32 | 11.3 | 23.3 | 0
393 | 2022-10-05 06:33 | 11.2 | 23 | 0
394 | 2022-10-05 06:34 | 11.1 | 22.8 | 0
395 | 2022-10-05 06:35 | 11.3 | 22.7 | 0
396 | 2022-10-05 06:36 | 11.1 | 23.3 | 0
397 | 2022-10-05 06:37 | 11.2 | 22.8 | 0
398 | 2022-10-05 06:38 | 11.2 | 23.1 | 0
399 | 2022-10-05 06:39 | 11.2 | 22.7 | 0
400 | 2022-10-05 06:40 | 11 | 23.3 | 0
401 | 2022-10-05 06:41 | 11 | 23 | 0
402 | 2022-10-05 06:42 | 11.3 | 23.2 | 0
403 | 2022-10-05 06:43 | 11.1 | 23.6 | 0
404 | 2022-10-05 06:44 | 11.3 | 22.2 | 0
405 | 2022-10-05 06:45 | 11.3 | 23.6 | 0
406 | 2022-10-05 06:46 | 11.2 | 23.3 | 0
407 | 2022-10-05 06:47 | 11.2 | 23 | 0
408 | 2022-10-05 06:48 | 11.1 | 22.8 | 0
409 | 2022-10-05 06:49 | 11.3 | 23.8 | 0
410 | 2022-10-05 06:50 | 11.3 | 23.5 | 0
411 | 2022-10-05 06:51 | 11.3 | 23 | 0
412 | 2022-10-05 06:52 | 11.1 | 23.5 | 0
413 | 2022-10-05 06:53 | 11.1 | 23.1 | 0
414 | 2022-10-05 06:54 | 11.1 | 23.1 | 0
415 | 2022-10-05 06:55 | 11.3 | 22.7 | 0
416 | 2022-10-05 06:56 | 11.4 | 22.7 | 0
417 | 2022-10-05 06:57 | 11.1 | 22.8 | 0
418 | 2022-10-05 06:58 | 11.2 | 22.6 | 0
419 | 2022-10-05 06:59 | 11.3 | 22.9 | 0
420 | 2022-10-05 07:00 | 11 | 23 | 0
421 | 2022-10-05 07:01 | 11.2 | 23 | 0
422 | 2022-10-05 07:02 | 11.1 | 23 | 0
423 | 2022-10-05 07:03 | 11.1 | 22.9 | 0
424 | 2022-10-05 07:04 | 11.1 | 23.3 | 0
425 | 2022-10-05 07:05 | 11.1 | 22.1 | 0
426 | 2022-10-05 07:06 | 11.3 | 22.6 | 0
427 | 2022-10-05 07:07 | 11.1 | 23.3 | 0
428 | 2022-10-05 07:08 | 11.2 | 22.4 | 0
429 | 2022-10-05 07:09 | 11.1 | 23.1 | 0
430 | 2022-10-05 07:10 | 11.1 | 23.1 | 0
431 | 2022-10-05 07:11 | 11.2 | 22.8 | 0
432 | 2022-10-05 07:12 | 11.2 | 23 | 0
433 | 2022-10-05 07:13 | 11 | 23.1 | 0
434 | 2022-10-05 07:14 | 11.2 | 22.9 | 0
435 | 2022-10-05 07:15 | 11.2 | 22.8 | 0
436 | 2022-10-05 07:16 | 11 | 23.1 | 0
437 | 2022-10-05 07:17 | 11 | 22.7 | 0
438 | 2022-10-05 07:18 | 11.3 | 22.2 | 0
439 | 2022-10-05 07:19 | 11.2 | 23.2 | 0
440 | 2022-10-05 07:20 | 11 | 22.3 | 1
441 | 2022-10-05 07:21 | 11.2 | 22.9 | 2
442 | 2022-10-05 07:22 | 11 | 22.9 | 2
443 | 2022-10-05 07:23 | 11.2 | 22.9 | 2
444 | 2022-10-05 07:24 | 11 | 22.8 | 3
445 | 2022-10-05 07:25 | 11 | 22.8 | 3
446 | 2022-10-05 07:26 | 11 | 22.8 | 4
447 | 2022-10-05 07:27 | 11.2 | 23.1 | 4
448 | 2022-10-05 07:28 | 11 | 22.8 | 5
449 | 2022-10-05 07:29 | 11.1 | 22.8 | 5
450 | 2022-10-05 07:30 | 11.2 | 23.1 | 6
451 | 2022-10-05 07:31 | 11 | 22.4 | 6
452 | 2022-10-05 07:32 | 11.1 | 23.1 | 7
453 | 2022-10-05 07:33 | 11.3 | 23.1 | 7
454 | 2022-10-05 07:34 | 11.2 | 22.9 | 8
455 | 2022-10-05 07:35 | 11.3 | 22.7 | 9
456 | 2022-10-05 07:36 | 11.4 | 23 | 10
457 | 2022-10-05 07:37 | 11.4 | 22.8 | 11
458 | 2022-10-05 07:38 | 11.3 | 22.9 | 12
459 | 2022-10-05 07:39 | 11.4 | 22.8 | 13
460 | 2022-10-05 07:40 | 11.4 | 22.6 | 13
461 | 2022-10-05 07:41 | 11.4 | 22.9 | 13
462 | 2022-10-05 07:42 | 11.4 | 22.8 | 14
463 | 2022-10-05 07:43 | 11.6 | 23.3 | 15
464 | 2022-10-05 07:44 | 12.2 | 22.9 | 16
465 | 2022-10-05 07:45 | 12.1 | 22.9 | 17
466 | 2022-10-05 07:46 | 11.9 | 22.7 | 19
467 | 2022-10-05 07:47 | 11.9 | 22.8 | 20
468 | 2022-10-05 07:48 | 11.8 | 22.9 | 21
469 | 2022-10-05 07:49 | 11.7 | 22.8 | 22
470 | 2022-10-05 07:50 | 11.6 | 22.8 | 23
471 | 2022-10-05 07:51 | 12.1 | 23 | 24
472 | 2022-10-05 07:52 | 11.9 | 22.6 | 25
473 | 2022-10-05 07:53 | 12.2 | 23.1 | 26
474 | 2022-10-05 07:54 | 12 | 22.8 | 27
475 | 2022-10-05 07:55 | 11.9 | 22.8 | 27
476 | 2022-10-05 07:56 | 12 | 22.9 | 27
477 | 2022-10-05 07:57 | 12 | 23 | 27
478 | 2022-10-05 07:58 | 11.9 | 23 | 27
479 | 2022-10-05 07:59 | 12 | 23.3 | 28
480 | 2022-10-05 08:00 | 12.2 | 23 | 29
481 | 2022-10-05 08:01 | 12.1 | 22.6 | 30
482 | 2022-10-05 08:02 | 11.9 | 22.9 | 30
483 | 2022-10-05 08:03 | 12.1 | 22.8 | 30
484 | 2022-10-05 08:04 | 12.3 | 22.8 | 30
485 | 2022-10-05 08:05 | 12.5 | 22.8 | 31
486 | 2022-10-05 08:06 | 12.3 | 22.8 | 33
487 | 2022-10-05 08:07 | 12.4 | 22.7 | 34
488 | 2022-10-05 08:08 | 12.6 | 22.6 | 35
489 | 2022-10-05 08:09 | 12.9 | 23.2 | 35
490 | 2022-10-05 08:10 | 12.6 | 22.6 | 35
491 | 2022-10-05 08:11 | 12.5 | 22.7 | 34
492 | 2022-10-05 08:12 | 12.6 | 23 | 33
493 | 2022-10-05 08:13 | 12.4 | 22.6 | 32
494 | 2022-10-05 08:14 | 12.7 | 23.7 | 32
495 | 2022-10-05 08:15 | 12.6 | 23.7 | 32
496 | 2022-10-05 08:16 | 12.5 | 22.7 | 33
497 | 2022-10-05 08:17 | 12.4 | 23.3 | 33
498 | 2022-10-05 08:18 | 12.6 | 23.4 | 33
499 | 2022-10-05 08:19 | 12.3 | 22.2 | 34
500 | 2022-10-05 08:20 | 12.5 | 23.3 | 34
501 | 2022-10-05 08:21 | 12.9 | 22.1 | 35
502 | 2022-10-05 08:22 | 12.7 | 23.3 | 35
503 | 2022-10-05 08:23 | 12.6 | 22.5 | 36
504 | 2022-10-05 08:24 | 12.6 | 22.4 | 36
505 | 2022-10-05 08:25 | 12.8 | 22.5 | 36
506 | 2022-10-05 08:26 | 12.6 | 22.8 | 36
507 | 2022-10-05 08:27 | 12.5 | 22.7 | 36
508 | 2022-10-05 08:28 | 12.5 | 22.8 | 37
509 | 2022-10-05 08:29 | 12.5 | 23 | 37
510 | 2022-10-05 08:30 | 12.5 | 22.9 | 38
511 | 2022-10-05 08:31 | 12.8 | 22.9 | 39
512 | 2022-10-05 08:32 | 12.9 | 23 | 39
513 | 2022-10-05 08:33 | 12.9 | 23.6 | 42
514 | 2022-10-05 08:34 | 12.8 | 23.7 | 44
515 | 2022-10-05 08:35 | 12.8 | 23.1 | 43
516 | 2022-10-05 08:36 | 13.1 | 22.6 | 57
517 | 2022-10-05 08:37 | 13.1 | 22.7 | 98
518 | 2022-10-05 08:38 | 13.2 | 22 | 114
519 | 2022-10-05 08:39 | 13.4 | 22.7 | 94
520 | 2022-10-05 08:40 | 13.3 | 22.8 | 65
521 | 2022-10-05 08:41 | 14 | 22.4 | 82
522 | 2022-10-05 08:42 | 14.2 | 23.4 | 121
523 | 2022-10-05 08:43 | 14.2 | 23.5 | 194
524 | 2022-10-05 08:44 | 14.1 | 22.6 | 268
525 | 2022-10-05 08:45 | 14.5 | 22.9 | 274
526 | 2022-10-05 08:46 | 14.3 | 22.5 | 277
527 | 2022-10-05 08:47 | 15.2 | 23 | 283
528 | 2022-10-05 08:48 | 15.2 | 22.8 | 289
529 | 2022-10-05 08:49 | 15.6 | 22.9 | 294
530 | 2022-10-05 08:50 | 15.7 | 22.6 | 298
531 | 2022-10-05 08:51 | 15.9 | 22.4 | 303
532 | 2022-10-05 08:52 | 15.8 | 22.9 | 309
533 | 2022-10-05 08:53 | 16 | 22.8 | 315
534 | 2022-10-05 08:54 | 15.6 | 22.6 | 319
535 | 2022-10-05 08:55 | 15.7 | 22.7 | 322
536 | 2022-10-05 08:56 | 16.3 | 22.6 | 324
537 | 2022-10-05 08:57 | 16.5 | 22.7 | 328
538 | 2022-10-05 08:58 | 16.4 | 23 | 333
539 | 2022-10-05 08:59 | 16.5 | 22.5 | 337
540 | 2022-10-05 09:00 | 16.9 | 23.2 | 345
541 | 2022-10-05 09:01 | 17 | 22.2 | 349
542 | 2022-10-05 09:02 | 17.1 | 22.4 | 351
543 | 2022-10-05 09:03 | 17 | 22.9 | 354
544 | 2022-10-05 09:04 | 17.2 | 22.6 | 358
545 | 2022-10-05 09:05 | 17.2 | 22.6 | 362
546 | 2022-10-05 09:06 | 17.4 | 22.2 | 366
547 | 2022-10-05 09:07 | 17.5 | 22.6 | 370
548 | 2022-10-05 09:08 | 17.4 | 22.6 | 375
549 | 2022-10-05 09:09 | 17.4 | 22.5 | 379
550 | 2022-10-05 09:10 | 17.5 | 22.7 | 384
551 | 2022-10-05 09:11 | 17.5 | 22.4 | 390
552 | 2022-10-05 09:12 | 17.7 | 22.5 | 397
553 | 2022-10-05 09:13 | 17.7 | 22.8 | 398
554 | 2022-10-05 09:14 | 17.9 | 22.6 | 402
555 | 2022-10-05 09:15 | 17.6 | 23 | 406
556 | 2022-10-05 09:16 | 17.8 | 23 | 410
557 | 2022-10-05 09:17 | 17.7 | 23.5 | 414
558 | 2022-10-05 09:18 | 17.9 | 22.2 | 418
559 | 2022-10-05 09:19 | 17.8 | 22.8 | 420
560 | 2022-10-05 09:20 | 18 | 22.8 | 428
561 | 2022-10-05 09:21 | 18 | 22.9 | 432
562 | 2022-10-05 09:22 | 18.1 | 23 | 436
563 | 2022-10-05 09:23 | 18 | 23.1 | 439
564 | 2022-10-05 09:24 | 18.2 | 23.1 | 441
565 | 2022-10-05 09:25 | 18.5 | 22.4 | 449
566 | 2022-10-05 09:26 | 18.4 | 23.4 | 452
567 | 2022-10-05 09:27 | 18.9 | 22.3 | 456
568 | 2022-10-05 09:28 | 19.1 | 22.6 | 457
569 | 2022-10-05 09:29 | 18.7 | 22.7 | 460
570 | 2022-10-05 09:30 | 18.7 | 22.8 | 465
571 | 2022-10-05 09:31 | 19.1 | 23.1 | 470
572 | 2022-10-05 09:32 | 19.1 | 22.6 | 473
573 | 2022-10-05 09:33 | 19.2 | 22.8 | 478
574 | 2022-10-05 09:34 | 19.3 | 22.7 | 483
575 | 2022-10-05 09:35 | 18.8 | 22.1 | 485
576 | 2022-10-05 09:36 | 18.9 | 22.9 | 490
577 | 2022-10-05 09:37 | 18.8 | 22.7 | 499
578 | 2022-10-05 09:38 | 18.9 | 22.6 | 500
579 | 2022-10-05 09:39 | 19 | 23.1 | 503
580 | 2022-10-05 09:40 | 19.2 | 22.7 | 510
581 | 2022-10-05 09:41 | 19.6 | 22.9 | 514
582 | 2022-10-05 09:42 | 20 | 23.1 | 519
583 | 2022-10-05 09:43 | 20.2 | 22.9 | 523
584 | 2022-10-05 09:44 | 20.2 | 23 | 524
585 | 2022-10-05 09:45 | 20.2 | 22.8 | 532
586 | 2022-10-05 09:46 | 20.2 | 22.8 | 536
587 | 2022-10-05 09:47 | 19.9 | 23.2 | 538
588 | 2022-10-05 09:48 | 19.8 | 23.1 | 549
589 | 2022-10-05 09:49 | 19.9 | 23.7 | 552
590 | 2022-10-05 09:50 | 19.8 | 23.7 | 555
591 | 2022-10-05 09:51 | 19.6 | 22.6 | 556
592 | 2022-10-05 09:52 | 19.9 | 23.4 | 560
593 | 2022-10-05 09:53 | 19.7 | 22.5 | 567
594 | 2022-10-05 09:54 | 20 | 23.5 | 570
595 | 2022-10-05 09:56 | 20.1 | 23.2 | 576
596 | 2022-10-05 09:56 | 20.2 | 23.2 | 580
597 | 2022-10-05 09:57 | 20.3 | 23.8 | 581
598 | 2022-10-05 09:58 | 19.9 | 22.2 | 587
599 | 2022-10-05 09:59 | 20.2 | 22.4 | 593
600 | 2022-10-05 10:00 | 20.2 | 23.2 | 596
601 | 2022-10-05 10:01 | 20.3 | 23.1 | 606
602 | 2022-10-05 10:03 | 20.5 | 23 | 613
603 | 2022-10-05 10:04 | 20.1 | 23.1 | 620
604 | 2022-10-05 10:04 | 19.9 | 23.1 | 632
605 | 2022-10-05 10:05 | 20 | 23.1 | 650
606 | 2022-10-05 10:06 | 20.5 | 23.1 | 661
607 | 2022-10-05 10:08 | 20.4 | 23 | 668
608 | 2022-10-05 10:08 | 20.4 | 22.9 | 671
609 | 2022-10-05 10:10 | 20.5 | 23.1 | 676
610 | 2022-10-05 10:10 | 20.7 | 23.4 | 652
611 | 2022-10-05 10:12 | 20.8 | 23.3 | 252
612 | 2022-10-05 10:12 | 20.5 | 23.4 | 229
613 | 2022-10-05 10:14 | 21.1 | 24 | 707
614 | 2022-10-05 10:14 | 21.4 | 23 | 695
615 | 2022-10-05 10:16 | 20.6 | 22.3 | 727
616 | 2022-10-05 10:16 | 20.5 | 21.7 | 742
617 | 2022-10-05 10:18 | 20.7 | 21.9 | 741
618 | 2022-10-05 10:19 | 20.4 | 21.2 | 733
619 | 2022-10-05 10:20 | 20.4 | 21.2 | 724
620 | 2022-10-05 10:20 | 20.8 | 22.1 | 727
621 | 2022-10-05 10:21 | 20.7 | 23.2 | 155
622 | 2022-10-05 10:22 | 20.5 | 22.9 | 176
623 | 2022-10-05 10:24 | 20.3 | 21.6 | 778
624 | 2022-10-05 10:24 | 20.4 | 21.5 | 792
625 | 2022-10-05 10:25 | 21 | 22 | 447
626 | 2022-10-05 10:26 | 20.9 | 21.9 | 177
627 | 2022-10-05 10:28 | 20.4 | 21.3 | 600
628 | 2022-10-05 10:28 | 20.4 | 21.5 | 798
629 | 2022-10-05 10:30 | 20.4 | 21.3 | 142
630 | 2022-10-05 10:30 | 20.1 | 21.5 | 226
631 | 2022-10-05 10:32 | 20.4 | 22.1 | 100
632 | 2022-10-05 10:32 | 19.9 | 21.7 | 100
633 | 2022-10-05 10:34 | 19.7 | 22.6 | 102
634 | 2022-10-05 10:35 | 19.7 | 22.4 | 89
635 | 2022-10-05 10:36 | 19.5 | 21.4 | 95
636 | 2022-10-05 10:36 | 19.1 | 21.2 | 113
637 | 2022-10-05 10:38 | 19.3 | 21 | 123
638 | 2022-10-05 10:39 | 19.1 | 21.6 | 129
639 | 2022-10-05 10:40 | 18.9 | 21.9 | 137
640 | 2022-10-05 10:40 | 18.8 | 21.3 | 157
641 | 2022-10-05 10:41 | 19 | 22.2 | 123
642 | 2022-10-05 10:42 | 18.8 | 21.6 | 115
643 | 2022-10-05 10:44 | 18.7 | 21.6 | 129
644 | 2022-10-05 10:44 | 18.8 | 21.5 | 123
645 | 2022-10-05 10:46 | 18.8 | 21.3 | 133
646 | 2022-10-05 10:46 | 18.9 | 22.1 | 833
647 | 2022-10-05 10:48 | 19.1 | 21.4 | 789
648 | 2022-10-05 10:48 | 19.6 | 21.9 | 796
649 | 2022-10-05 10:50 | 19.7 | 21.3 | 460
650 | 2022-10-05 10:50 | 20 | 21 | 630
651 | 2022-10-05 10:52 | 20.4 | 22.2 | 843
652 | 2022-10-05 10:52 | 20.7 | 22.2 | 212
653 | 2022-10-05 10:54 | 20.8 | 22.3 | 694
654 | 2022-10-05 10:55 | 20.6 | 21.6 | 908
655 | 2022-10-05 10:56 | 20.5 | 21.6 | 513
656 | 2022-10-05 10:56 | 20.4 | 21.8 | 670
657 | 2022-10-05 10:57 | 20.4 | 21.5 | 947
658 | 2022-10-05 10:59 | 20.4 | 21.5 | 203
659 | 2022-10-05 11:00 | 20.6 | 20.8 | 227
660 | 2022-10-05 11:01 | 20.4 | 21.3 | 868
661 | 2022-10-05 11:02 | 20.5 | 21.2 | 541
662 | 2022-10-05 11:03 | 20.4 | 21.4 | 918
663 | 2022-10-05 11:04 | 21 | 21.3 | 913
664 | 2022-10-05 11:04 | 21.1 | 21.6 | 708
665 | 2022-10-05 11:06 | 21.1 | 21.7 | 935
666 | 2022-10-05 11:06 | 21.7 | 21.7 | 921
667 | 2022-10-05 11:07 | 22.1 | 21.9 | 224
668 | 2022-10-05 11:08 | 22 | 21.8 | 260
669 | 2022-10-05 11:10 | 21.4 | 21.6 | 1023
670 | 2022-10-05 11:10 | 21 | 21.4 | 978
671 | 2022-10-05 11:11 | 21 | 21.1 | 1070
672 | 2022-10-05 11:12 | 21.5 | 22 | 1083
673 | 2022-10-05 11:13 | 21.4 | 21.4 | 1087
674 | 2022-10-05 11:14 | 22.1 | 21 | 329
675 | 2022-10-05 11:16 | 21.9 | 21.7 | 348
676 | 2022-10-05 11:17 | 22 | 21.7 | 306
677 | 2022-10-05 11:18 | 21.7 | 21.5 | 310
678 | 2022-10-05 11:19 | 21.3 | 22.6 | 336
679 | 2022-10-05 11:20 | 21.1 | 21.4 | 312
680 | 2022-10-05 11:20 | 20.8 | 21.4 | 227
681 | 2022-10-05 11:22 | 20.6 | 21.2 | 197
682 | 2022-10-05 11:23 | 20.7 | 21.6 | 178
683 | 2022-10-05 11:24 | 20.3 | 21.2 | 173
684 | 2022-10-05 11:24 | 20.2 | 21.4 | 184
685 | 2022-10-05 11:26 | 20.3 | 21.3 | 209
686 | 2022-10-05 11:26 | 20 | 21.1 | 195
687 | 2022-10-05 11:27 | 19.9 | 21.2 | 179
688 | 2022-10-05 11:28 | 19.9 | 21 | 164
689 | 2022-10-05 11:29 | 19.8 | 20.7 | 150
690 | 2022-10-05 11:30 | 19.6 | 21 | 140
691 | 2022-10-05 11:31 | 19.6 | 21.2 | 137
692 | 2022-10-05 11:33 | 19.4 | 22.1 | 134
693 | 2022-10-05 11:34 | 19.4 | 21.7 | 133
694 | 2022-10-05 11:34 | 19.6 | 22.3 | 134
695 | 2022-10-05 11:35 | 19.3 | 21.6 | 138
696 | 2022-10-05 11:36 | 19.1 | 21.3 | 149
697 | 2022-10-05 11:38 | 19.2 | 22.3 | 161
698 | 2022-10-05 11:38 | 19.2 | 22.2 | 170
699 | 2022-10-05 11:40 | 19.1 | 21.7 | 171
700 | 2022-10-05 11:40 | 19 | 21.4 | 166
701 | 2022-10-05 11:42 | 19.1 | 21.3 | 161
702 | 2022-10-05 11:42 | 19.1 | 21.1 | 164
703 | 2022-10-05 11:44 | 19 | 21.1 | 182
704 | 2022-10-05 11:44 | 19.1 | 21.3 | 209
705 | 2022-10-05 11:46 | 19.2 | 21.5 | 245
706 | 2022-10-05 11:46 | 19.3 | 21 | 296
707 | 2022-10-05 11:48 | 19.4 | 21.3 | 721
708 | 2022-10-05 11:49 | 19.8 | 21.2 | 576
709 | 2022-10-05 11:50 | 20 | 20.8 | 290
710 | 2022-10-05 11:50 | 19.9 | 20.8 | 235
711 | 2022-10-05 11:51 | 19.7 | 20.9 | 197
712 | 2022-10-05 11:52 | 19.7 | 21.3 | 162
713 | 2022-10-05 11:54 | 19.7 | 21.3 | 143
714 | 2022-10-05 11:54 | 19.8 | 21.6 | 135
715 | 2022-10-05 11:55 | 19.7 | 21.5 | 138
716 | 2022-10-05 11:56 | 19.6 | 20.7 | 153
717 | 2022-10-05 11:58 | 19.2 | 20.6 | 177
718 | 2022-10-05 11:58 | 19.3 | 21.4 | 213
719 | 2022-10-05 12:00 | 19.5 | 20.9 | 253
720 | 2022-10-05 12:00 | 19.3 | 21.7 | 289
721 | 2022-10-05 12:02 | 19.3 | 21.6 | 332
722 | 2022-10-05 12:02 | 19.4 | 21.4 | 1152
723 | 2022-10-05 12:04 | 19.7 | 22 | 437
724 | 2022-10-05 12:05 | 20 | 22.1 | 338
725 | 2022-10-05 12:06 | 19.9 | 20.8 | 263
726 | 2022-10-05 12:06 | 19.8 | 21.5 | 224
727 | 2022-10-05 12:08 | 19.7 | 21.2 | 200
728 | 2022-10-05 12:09 | 19.6 | 21.7 | 169
729 | 2022-10-05 12:10 | 19.8 | 21.6 | 154
730 | 2022-10-05 12:10 | 19.9 | 21.5 | 147
731 | 2022-10-05 12:11 | 19.8 | 21.4 | 145
732 | 2022-10-05 12:12 | 19.7 | 21.3 | 155
733 | 2022-10-05 12:14 | 19.4 | 20.6 | 169
734 | 2022-10-05 12:14 | 19.4 | 21.4 | 172
735 | 2022-10-05 12:16 | 19.2 | 20.7 | 166
736 | 2022-10-05 12:16 | 19.3 | 21.5 | 161
737 | 2022-10-05 12:18 | 19.3 | 21.5 | 162
738 | 2022-10-05 12:18 | 19.4 | 21.4 | 173
739 | 2022-10-05 12:20 | 19.4 | 21.1 | 190
740 | 2022-10-05 12:20 | 19.4 | 21.2 | 208
741 | 2022-10-05 12:22 | 19.1 | 21.3 | 232
742 | 2022-10-05 12:22 | 19.2 | 20.8 | 254
743 | 2022-10-05 12:24 | 19.4 | 20.6 | 271
744 | 2022-10-05 12:25 | 19.4 | 20.8 | 282
745 | 2022-10-05 12:26 | 19.2 | 21 | 286
746 | 2022-10-05 12:26 | 19.4 | 21.1 | 290
747 | 2022-10-05 12:27 | 19.4 | 21.1 | 296
748 | 2022-10-05 12:29 | 19.4 | 21.3 | 300
749 | 2022-10-05 12:30 | 19.4 | 20.9 | 326
750 | 2022-10-05 12:31 | 19.4 | 21.1 | 374
751 | 2022-10-05 12:32 | 19.5 | 21.2 | 403
752 | 2022-10-05 12:33 | 19.9 | 21.3 | 467
753 | 2022-10-05 12:34 | 20 | 21.2 | 656
754 | 2022-10-05 12:34 | 20.3 | 21.6 | 611
755 | 2022-10-05 12:36 | 20.5 | 21.2 | 411
756 | 2022-10-05 12:36 | 20.7 | 21.6 | 462
757 | 2022-10-05 12:37 | 20.7 | 21.8 | 1263
758 | 2022-10-05 12:38 | 21.3 | 21.3 | 611
759 | 2022-10-05 12:40 | 20.8 | 21.7 | 1210
760 | 2022-10-05 12:40 | 21.3 | 21.1 | 1248
761 | 2022-10-05 12:41 | 21.1 | 21.6 | 331
762 | 2022-10-05 12:42 | 20.4 | 21.3 | 357
763 | 2022-10-05 12:43 | 20.5 | 21.2 | 347
764 | 2022-10-05 12:44 | 20.4 | 21.4 | 557
765 | 2022-10-05 12:46 | 20.7 | 20.9 | 357
766 | 2022-10-05 12:47 | 20.6 | 21.4 | 1171
767 | 2022-10-05 12:48 | 20.7 | 21.4 | 1100
768 | 2022-10-05 12:49 | 21.4 | 21 | 717
769 | 2022-10-05 12:50 | 21.6 | 22.3 | 535
770 | 2022-10-05 12:51 | 21.7 | 22.6 | 398
771 | 2022-10-05 12:52 | 21.7 | 22.5 | 470
772 | 2022-10-05 12:53 | 21.5 | 21.7 | 347
773 | 2022-10-05 12:54 | 21.2 | 21.2 | 349
774 | 2022-10-05 12:55 | 21.3 | 21.4 | 333
775 | 2022-10-05 12:56 | 21.2 | 21.2 | 336
776 | 2022-10-05 12:57 | 20.9 | 21.9 | 322
777 | 2022-10-05 12:58 | 20.7 | 21.8 | 291
778 | 2022-10-05 12:59 | 20.4 | 21.1 | 278
779 | 2022-10-05 13:00 | 20 | 21.2 | 278
780 | 2022-10-05 13:01 | 20.4 | 21.3 | 276
781 | 2022-10-05 13:02 | 20.7 | 21.3 | 674
782 | 2022-10-05 13:03 | 20.9 | 21 | 250
783 | 2022-10-05 13:04 | 20.9 | 20.9 | 218
784 | 2022-10-05 13:05 | 20.8 | 21.6 | 203
785 | 2022-10-05 13:06 | 20.9 | 21.9 | 200
786 | 2022-10-05 13:07 | 20.4 | 21.4 | 202
787 | 2022-10-05 13:08 | 20.6 | 21.2 | 201
788 | 2022-10-05 13:09 | 20.5 | 21.4 | 199
789 | 2022-10-05 13:10 | 20.2 | 20.3 | 199
790 | 2022-10-05 13:11 | 20.2 | 20.2 | 208
791 | 2022-10-05 13:12 | 20.2 | 20.7 | 227
792 | 2022-10-05 13:13 | 20.1 | 21.8 | 255
793 | 2022-10-05 13:14 | 20.1 | 20.8 | 291
794 | 2022-10-05 13:15 | 20.1 | 21.7 | 1270
795 | 2022-10-05 13:16 | 20.5 | 20.7 | 1250
796 | 2022-10-05 13:17 | 20.9 | 21.4 | 342
797 | 2022-10-05 13:18 | 21.2 | 21.5 | 456
798 | 2022-10-05 13:19 | 21 | 21.4 | 835
799 | 2022-10-05 13:20 | 21 | 21.6 | 1251
800 | 2022-10-05 13:21 | 21.7 | 21.6 | 1121
801 | 2022-10-05 13:22 | 21.9 | 21.6 | 1191
802 | 2022-10-05 13:23 | 21.6 | 21.8 | 1188
803 | 2022-10-05 13:24 | 21.8 | 21.7 | 813
804 | 2022-10-05 13:25 | 22.4 | 21.8 | 1170
805 | 2022-10-05 13:26 | 22.2 | 21.6 | 957
806 | 2022-10-05 13:27 | 22.5 | 21.7 | 1170
807 | 2022-10-05 13:28 | 22.3 | 22.3 | 1202
808 | 2022-10-05 13:29 | 22.2 | 21.7 | 1245
809 | 2022-10-05 13:30 | 22.6 | 22.5 | 679
810 | 2022-10-05 13:31 | 23 | 22.3 | 746
811 | 2022-10-05 13:32 | 23 | 22.2 | 974
812 | 2022-10-05 13:33 | 22.8 | 22.6 | 767
813 | 2022-10-05 13:34 | 22.4 | 22.2 | 1232
814 | 2022-10-05 13:35 | 22 | 22.1 | 795
815 | 2022-10-05 13:36 | 22.4 | 22 | 1135
816 | 2022-10-05 13:37 | 22 | 22.1 | 1181
817 | 2022-10-05 13:38 | 22.2 | 22.1 | 798
818 | 2022-10-05 13:39 | 22.6 | 22 | 1085
819 | 2022-10-05 13:40 | 21.9 | 22.4 | 1186
820 | 2022-10-05 13:41 | 21.8 | 22.7 | 1158
821 | 2022-10-05 13:42 | 21.8 | 21.7 | 1146
822 | 2022-10-05 13:43 | 22.3 | 22.7 | 1159
823 | 2022-10-05 13:44 | 22.8 | 22.1 | 1151
824 | 2022-10-05 13:45 | 22.4 | 22.4 | 1151
825 | 2022-10-05 13:46 | 22.9 | 22.7 | 1148
826 | 2022-10-05 13:47 | 22.6 | 22.3 | 1146
827 | 2022-10-05 13:48 | 22.4 | 22.4 | 1142
828 | 2022-10-05 13:49 | 22.9 | 22.6 | 1147
829 | 2022-10-05 13:50 | 22.8 | 22.1 | 1168
830 | 2022-10-05 13:51 | 22.8 | 22.5 | 1188
831 | 2022-10-05 13:52 | 22.4 | 22.4 | 1205
832 | 2022-10-05 13:53 | 23 | 22.5 | 335
833 | 2022-10-05 13:54 | 22.9 | 22.6 | 341
834 | 2022-10-05 13:55 | 21.6 | 22.6 | 333
835 | 2022-10-05 13:56 | 21.4 | 22.3 | 319
836 | 2022-10-05 13:57 | 21.3 | 22.4 | 716
837 | 2022-10-05 13:58 | 21.2 | 22.3 | 1191
838 | 2022-10-05 13:59 | 21.3 | 22.3 | 469
839 | 2022-10-05 14:00 | 21.2 | 22.4 | 1165
840 | 2022-10-05 14:01 | 21.9 | 22.2 | 816
841 | 2022-10-05 14:02 | 21.9 | 22.7 | 432
842 | 2022-10-05 14:03 | 22 | 23.1 | 1252
843 | 2022-10-05 14:04 | 22.3 | 22.3 | 1284
844 | 2022-10-05 14:05 | 23.1 | 22.1 | 410
845 | 2022-10-05 14:06 | 23.1 | 22.4 | 345
846 | 2022-10-05 14:07 | 22.2 | 23.1 | 309
847 | 2022-10-05 14:08 | 21.3 | 21.9 | 323
848 | 2022-10-05 14:09 | 21.4 | 22 | 366
849 | 2022-10-05 14:10 | 21.5 | 23.5 | 366
850 | 2022-10-05 14:11 | 21.3 | 23.2 | 377
851 | 2022-10-05 14:12 | 21.5 | 22.7 | 334
852 | 2022-10-05 14:13 | 21.4 | 22.3 | 337
853 | 2022-10-05 14:14 | 21.5 | 21.8 | 335
854 | 2022-10-05 14:15 | 21.1 | 22.8 | 321
855 | 2022-10-05 14:16 | 20.9 | 22 | 305
856 | 2022-10-05 14:17 | 21.1 | 22.1 | 304
857 | 2022-10-05 14:18 | 21.1 | 22.1 | 319
858 | 2022-10-05 14:19 | 21 | 21.9 | 346
859 | 2022-10-05 14:20 | 21.3 | 22.1 | 368
860 | 2022-10-05 14:21 | 20.8 | 22.3 | 370
861 | 2022-10-05 14:22 | 20.9 | 22.3 | 407
862 | 2022-10-05 14:23 | 21.2 | 22.6 | 444
863 | 2022-10-05 14:24 | 21.5 | 22.5 | 1049
864 | 2022-10-05 14:25 | 21.4 | 22.6 | 603
865 | 2022-10-05 14:26 | 21.5 | 22.6 | 471
866 | 2022-10-05 14:27 | 21.6 | 23 | 410
867 | 2022-10-05 14:28 | 21.5 | 22.9 | 386
868 | 2022-10-05 14:29 | 21.3 | 23.1 | 400
869 | 2022-10-05 14:30 | 21.2 | 23 | 406
870 | 2022-10-05 14:31 | 21.1 | 23.1 | 426
871 | 2022-10-05 14:32 | 21.3 | 23.5 | 433
872 | 2022-10-05 14:33 | 21.4 | 22.9 | 477
873 | 2022-10-05 14:34 | 21.4 | 23.5 | 533
874 | 2022-10-05 14:35 | 21.4 | 23.1 | 443
875 | 2022-10-05 14:36 | 21.1 | 23 | 463
876 | 2022-10-05 14:37 | 20.9 | 22.9 | 457
877 | 2022-10-05 14:38 | 21 | 22.7 | 468
878 | 2022-10-05 14:39 | 21.5 | 23 | 1141
879 | 2022-10-05 14:40 | 21.9 | 23.8 | 341
880 | 2022-10-05 14:41 | 21.4 | 23.8 | 570
881 | 2022-10-05 14:42 | 21 | 23.7 | 397
882 | 2022-10-05 14:43 | 21.1 | 22.5 | 444
883 | 2022-10-05 14:44 | 21.3 | 22.6 | 1023
884 | 2022-10-05 14:45 | 21.1 | 24 | 630
885 | 2022-10-05 14:46 | 21.2 | 23.6 | 572
886 | 2022-10-05 14:47 | 21.5 | 23.4 | 762
887 | 2022-10-05 14:48 | 21.5 | 24.1 | 435
888 | 2022-10-05 14:49 | 21.4 | 22.8 | 1100
889 | 2022-10-05 14:50 | 21.6 | 23.1 | 346
890 | 2022-10-05 14:51 | 21.6 | 23.9 | 341
891 | 2022-10-05 14:52 | 21.3 | 22.6 | 275
892 | 2022-10-05 14:53 | 21.2 | 23.2 | 228
893 | 2022-10-05 14:54 | 20.8 | 23.1 | 213
894 | 2022-10-05 14:55 | 20.6 | 23.3 | 186
895 | 2022-10-05 14:56 | 20.4 | 23.3 | 178
896 | 2022-10-05 14:57 | 20.3 | 22.7 | 158
897 | 2022-10-05 14:58 | 20.2 | 23.4 | 154
898 | 2022-10-05 14:59 | 20.2 | 22.5 | 163
899 | 2022-10-05 15:00 | 20.4 | 22.9 | 173
900 | 2022-10-05 15:01 | 19.9 | 22.7 | 929
901 | 2022-10-05 15:02 | 20.6 | 22.9 | 698
902 | 2022-10-05 15:03 | 20.8 | 23.2 | 954
903 | 2022-10-05 15:04 | 20.9 | 23.2 | 1007
904 | 2022-10-05 15:05 | 21.5 | 23.3 | 1010
905 | 2022-10-05 15:06 | 22 | 23.2 | 988
906 | 2022-10-05 15:07 | 22.4 | 23.4 | 966
907 | 2022-10-05 15:08 | 22 | 23.4 | 962
908 | 2022-10-05 15:09 | 22.1 | 23.2 | 143
909 | 2022-10-05 15:10 | 21.7 | 23.6 | 133
910 | 2022-10-05 15:11 | 21.3 | 23.3 | 136
911 | 2022-10-05 15:12 | 21 | 23 | 167
912 | 2022-10-05 15:13 | 20.9 | 23.2 | 939
913 | 2022-10-05 15:14 | 20.9 | 23.5 | 183
914 | 2022-10-05 15:15 | 21.1 | 23.4 | 916
915 | 2022-10-05 15:16 | 21.2 | 23.5 | 910
916 | 2022-10-05 15:17 | 21.3 | 23 | 891
917 | 2022-10-05 15:18 | 21.8 | 23.3 | 918
918 | 2022-10-05 15:19 | 22.1 | 22.8 | 929
919 | 2022-10-05 15:20 | 22.2 | 23.1 | 143
920 | 2022-10-05 15:21 | 21.8 | 23 | 133
921 | 2022-10-05 15:22 | 21.3 | 23.7 | 131
922 | 2022-10-05 15:23 | 20.6 | 23.6 | 895
923 | 2022-10-05 15:24 | 20.9 | 24.3 | 298
924 | 2022-10-05 15:25 | 21.1 | 24.3 | 123
925 | 2022-10-05 15:26 | 21 | 24.3 | 879
926 | 2022-10-05 15:27 | 21.2 | 24.2 | 871
927 | 2022-10-05 15:28 | 21.3 | 23.8 | 864
928 | 2022-10-05 15:29 | 21.7 | 23.2 | 862
929 | 2022-10-05 15:30 | 21.8 | 23.2 | 871
930 | 2022-10-05 15:31 | 21.9 | 23.5 | 463
931 | 2022-10-05 15:32 | 21.9 | 23.1 | 186
932 | 2022-10-05 15:33 | 21.3 | 23.3 | 859
933 | 2022-10-05 15:34 | 21.3 | 23.3 | 911
934 | 2022-10-05 15:35 | 21.3 | 23.4 | 835
935 | 2022-10-05 15:36 | 21.3 | 23 | 931
936 | 2022-10-05 15:37 | 22 | 23.6 | 906
937 | 2022-10-05 15:38 | 22.1 | 22.8 | 910
938 | 2022-10-05 15:39 | 21.6 | 23.4 | 259
939 | 2022-10-05 15:40 | 21.7 | 22.8 | 923
940 | 2022-10-05 15:41 | 22.3 | 23.6 | 236
941 | 2022-10-05 15:42 | 21.9 | 22.9 | 702
942 | 2022-10-05 15:43 | 21.7 | 23.8 | 204
943 | 2022-10-05 15:44 | 21.2 | 23.4 | 184
944 | 2022-10-05 15:45 | 21.2 | 23.5 | 195
945 | 2022-10-05 15:46 | 20.8 | 23 | 794
946 | 2022-10-05 15:47 | 21.2 | 24.2 | 796
947 | 2022-10-05 15:48 | 21.4 | 23.2 | 220
948 | 2022-10-05 15:49 | 21.3 | 23.4 | 218
949 | 2022-10-05 15:50 | 21 | 23.8 | 279
950 | 2022-10-05 15:51 | 20.9 | 24.3 | 741
951 | 2022-10-05 15:52 | 21.4 | 23.3 | 909
952 | 2022-10-05 15:53 | 22 | 23.5 | 894
953 | 2022-10-05 15:54 | 21.6 | 23.4 | 867
954 | 2022-10-05 15:55 | 22 | 23.4 | 785
955 | 2022-10-05 15:56 | 22.2 | 24.3 | 844
956 | 2022-10-05 15:57 | 22 | 23.4 | 814
957 | 2022-10-05 15:58 | 21.4 | 23.4 | 789
958 | 2022-10-05 15:59 | 21.6 | 23.4 | 782
959 | 2022-10-05 16:00 | 21.9 | 23.6 | 778
960 | 2022-10-05 16:01 | 21.6 | 23.4 | 777
961 | 2022-10-05 16:02 | 21.6 | 23.3 | 778
962 | 2022-10-05 16:03 | 21.6 | 23.4 | 784
963 | 2022-10-05 16:04 | 21.5 | 23.5 | 765
964 | 2022-10-05 16:05 | 21.6 | 23.4 | 755
965 | 2022-10-05 16:06 | 21.6 | 23.7 | 754
966 | 2022-10-05 16:07 | 21.8 | 23.1 | 760
967 | 2022-10-05 16:08 | 22 | 23.7 | 768
968 | 2022-10-05 16:09 | 22.2 | 23.8 | 768
969 | 2022-10-05 16:10 | 22.1 | 23.5 | 784
970 | 2022-10-05 16:11 | 22.1 | 22.7 | 292
971 | 2022-10-05 16:12 | 22.6 | 23.8 | 796
972 | 2022-10-05 16:13 | 22.5 | 23.3 | 801
973 | 2022-10-05 16:14 | 22.5 | 22.9 | 797
974 | 2022-10-05 16:15 | 23 | 24.2 | 777
975 | 2022-10-05 16:16 | 22.2 | 23.7 | 783
976 | 2022-10-05 16:17 | 22.6 | 23.6 | 436
977 | 2022-10-05 16:18 | 22.4 | 24.3 | 798
978 | 2022-10-05 16:19 | 22.5 | 23.4 | 746
979 | 2022-10-05 16:20 | 22.4 | 23.4 | 231
980 | 2022-10-05 16:21 | 22 | 23.6 | 232
981 | 2022-10-05 16:22 | 21.8 | 23.7 | 231
982 | 2022-10-05 16:23 | 21.5 | 23.5 | 790
983 | 2022-10-05 16:24 | 21.4 | 24.2 | 768
984 | 2022-10-05 16:25 | 21.8 | 23.5 | 657
985 | 2022-10-05 16:26 | 22.1 | 23.6 | 199
986 | 2022-10-05 16:27 | 21.5 | 23.6 | 211
987 | 2022-10-05 16:28 | 21.3 | 23.5 | 175
988 | 2022-10-05 16:29 | 21.3 | 23.6 | 166
989 | 2022-10-05 16:30 | 21.2 | 23.4 | 168
990 | 2022-10-05 16:31 | 20.8 | 23.9 | 162
991 | 2022-10-05 16:32 | 20.9 | 23.5 | 173
992 | 2022-10-05 16:33 | 20.5 | 23.8 | 177
993 | 2022-10-05 16:34 | 20.4 | 23.6 | 648
994 | 2022-10-05 16:35 | 20.7 | 23.6 | 621
995 | 2022-10-05 16:36 | 20.9 | 23.5 | 609
996 | 2022-10-05 16:37 | 21 | 23.7 | 596
997 | 2022-10-05 16:38 | 21.3 | 23.7 | 591
998 | 2022-10-05 16:39 | 21.3 | 23.9 | 586
999 | 2022-10-05 16:40 | 21.5 | 23.6 | 576
1000 | 2022-10-05 16:41 | 21.5 | 23.7 | 570
1001 | 2022-10-05 16:42 | 21.8 | 23.6 | 566
1002 | 2022-10-05 16:43 | 21.9 | 23.9 | 563
1003 | 2022-10-05 16:44 | 22.1 | 23.5 | 558
1004 | 2022-10-05 16:45 | 22.1 | 23.7 | 557
1005 | 2022-10-05 16:46 | 22.1 | 23.5 | 551
1006 | 2022-10-05 16:47 | 22.2 | 23.8 | 549
1007 | 2022-10-05 16:48 | 22 | 22.9 | 540
1008 | 2022-10-05 16:49 | 22.2 | 23.9 | 535
1009 | 2022-10-05 16:50 | 22.3 | 23.5 | 534
1010 | 2022-10-05 16:51 | 21.6 | 23.8 | 527
1011 | 2022-10-05 16:52 | 21.4 | 22.6 | 524
1012 | 2022-10-05 16:53 | 21.1 | 23.1 | 520
1013 | 2022-10-05 16:54 | 21.3 | 22.7 | 515
1014 | 2022-10-05 16:55 | 21.5 | 22.9 | 512
1015 | 2022-10-05 16:56 | 21 | 22.9 | 509
1016 | 2022-10-05 16:57 | 21.1 | 23 | 505
1017 | 2022-10-05 16:58 | 21.2 | 23.1 | 502
1018 | 2022-10-05 16:59 | 21.4 | 23.1 | 499
1019 | 2022-10-05 17:00 | 21.6 | 23 | 496
1020 | 2022-10-05 17:01 | 21.4 | 23.2 | 492
1021 | 2022-10-05 17:02 | 21.3 | 22.9 | 487
1022 | 2022-10-05 17:03 | 21.2 | 22.9 | 481
1023 | 2022-10-05 17:04 | 21.3 | 22.8 | 475
1024 | 2022-10-05 17:05 | 21.3 | 22.9 | 473
1025 | 2022-10-05 17:06 | 21.4 | 22.9 | 472
1026 | 2022-10-05 17:07 | 21.4 | 22.9 | 477
1027 | 2022-10-05 17:08 | 21.4 | 22.9 | 444
1028 | 2022-10-05 17:09 | 21.2 | 23.1 | 469
1029 | 2022-10-05 17:10 | 20.9 | 22.7 | 464
1030 | 2022-10-05 17:11 | 20.9 | 22.6 | 459
1031 | 2022-10-05 17:12 | 20.9 | 22.4 | 457
1032 | 2022-10-05 17:13 | 20.9 | 22.6 | 453
1033 | 2022-10-05 17:14 | 20.7 | 22.6 | 450
1034 | 2022-10-05 17:15 | 20.9 | 22.8 | 440
1035 | 2022-10-05 17:16 | 20.7 | 21.9 | 431
1036 | 2022-10-05 17:17 | 20.5 | 22.5 | 425
1037 | 2022-10-05 17:18 | 20.5 | 22.8 | 419
1038 | 2022-10-05 17:19 | 20.8 | 22.7 | 414
1039 | 2022-10-05 17:20 | 21 | 23.4 | 406
1040 | 2022-10-05 17:21 | 21 | 23.1 | 399
1041 | 2022-10-05 17:22 | 20.7 | 23.6 | 395
1042 | 2022-10-05 17:23 | 20.6 | 23.2 | 389
1043 | 2022-10-05 17:24 | 20.6 | 23.4 | 384
1044 | 2022-10-05 17:25 | 20.8 | 22.9 | 381
1045 | 2022-10-05 17:26 | 20.4 | 22.7 | 374
1046 | 2022-10-05 17:27 | 20.7 | 22.7 | 368
1047 | 2022-10-05 17:28 | 20.9 | 23.3 | 363
1048 | 2022-10-05 17:29 | 20.7 | 22.5 | 361
1049 | 2022-10-05 17:30 | 20.5 | 22.5 | 357
1050 | 2022-10-05 17:31 | 20.7 | 22.6 | 353
1051 | 2022-10-05 17:32 | 20.5 | 23.6 | 348
1052 | 2022-10-05 17:33 | 20.3 | 22.8 | 343
1053 | 2022-10-05 17:34 | 20.3 | 23 | 337
1054 | 2022-10-05 17:35 | 20.4 | 23.2 | 333
1055 | 2022-10-05 17:36 | 20.5 | 22.8 | 328
1056 | 2022-10-05 17:37 | 20.5 | 23 | 325
1057 | 2022-10-05 17:38 | 20.6 | 22.8 | 321
1058 | 2022-10-05 17:39 | 20.7 | 23.3 | 319
1059 | 2022-10-05 17:40 | 20.6 | 23.2 | 313
1060 | 2022-10-05 17:41 | 20.6 | 22.9 | 308
1061 | 2022-10-05 17:42 | 20.8 | 23.2 | 305
1062 | 2022-10-05 17:43 | 20.8 | 23.2 | 302
1063 | 2022-10-05 17:44 | 20.9 | 23.4 | 299
1064 | 2022-10-05 17:45 | 20.7 | 23.4 | 296
1065 | 2022-10-05 17:46 | 20.4 | 23.8 | 293
1066 | 2022-10-05 17:47 | 20.2 | 23.7 | 288
1067 | 2022-10-05 17:48 | 20.2 | 23.4 | 280
1068 | 2022-10-05 17:49 | 20.5 | 23 | 272
1069 | 2022-10-05 17:50 | 20.2 | 23.2 | 264
1070 | 2022-10-05 17:51 | 20.2 | 23.3 | 258
1071 | 2022-10-05 17:52 | 20.2 | 23.2 | 253
1072 | 2022-10-05 17:53 | 20.2 | 23.2 | 249
1073 | 2022-10-05 17:54 | 20.2 | 23.7 | 245
1074 | 2022-10-05 17:55 | 20.2 | 23.3 | 236
1075 | 2022-10-05 17:56 | 20 | 23.2 | 235
1076 | 2022-10-05 17:57 | 20.1 | 23.3 | 233
1077 | 2022-10-05 17:58 | 19.9 | 23 | 228
1078 | 2022-10-05 17:59 | 20 | 22.8 | 224
1079 | 2022-10-05 18:00 | 20.2 | 23.3 | 221
1080 | 2022-10-05 18:01 | 19.9 | 23.1 | 216
1081 | 2022-10-05 18:02 | 19.9 | 23.4 | 212
1082 | 2022-10-05 18:03 | 19.7 | 23.1 | 207
1083 | 2022-10-05 18:04 | 19.7 | 23.3 | 202
1084 | 2022-10-05 18:05 | 19.8 | 23.2 | 198
1085 | 2022-10-05 18:06 | 19.8 | 23.3 | 194
1086 | 2022-10-05 18:07 | 19.7 | 23.1 | 189
1087 | 2022-10-05 18:08 | 19.9 | 23.1 | 184
1088 | 2022-10-05 18:09 | 19.7 | 23.4 | 181
1089 | 2022-10-05 18:10 | 19.8 | 22.3 | 176
1090 | 2022-10-05 18:11 | 19.7 | 22.9 | 172
1091 | 2022-10-05 18:12 | 19.7 | 22.8 | 169
1092 | 2022-10-05 18:13 | 19.6 | 23.5 | 162
1093 | 2022-10-05 18:14 | 19.7 | 23.4 | 159
1094 | 2022-10-05 18:15 | 19.7 | 23.1 | 154
1095 | 2022-10-05 18:16 | 19.7 | 23.7 | 150
1096 | 2022-10-05 18:17 | 19.5 | 22.9 | 144
1097 | 2022-10-05 18:18 | 19.2 | 23.5 | 141
1098 | 2022-10-05 18:19 | 19.4 | 22.7 | 135
1099 | 2022-10-05 18:20 | 19.2 | 22.8 | 131
1100 | 2022-10-05 18:21 | 19.3 | 23.1 | 127
1101 | 2022-10-05 18:22 | 19.3 | 23.2 | 123
1102 | 2022-10-05 18:23 | 19.1 | 23.3 | 118
1103 | 2022-10-05 18:24 | 19 | 23.2 | 114
1104 | 2022-10-05 18:25 | 19.2 | 23 | 111
1105 | 2022-10-05 18:26 | 18.9 | 23.4 | 106
1106 | 2022-10-05 18:27 | 18.9 | 23.3 | 102
1107 | 2022-10-05 18:28 | 18.9 | 23.3 | 97
1108 | 2022-10-05 18:29 | 18.9 | 23.2 | 94
1109 | 2022-10-05 18:30 | 18.8 | 23.2 | 90
1110 | 2022-10-05 18:31 | 18.9 | 23.3 | 85
1111 | 2022-10-05 18:32 | 18.6 | 22.7 | 82
1112 | 2022-10-05 18:33 | 18.5 | 23.3 | 78
1113 | 2022-10-05 18:34 | 18.6 | 23.1 | 60
1114 | 2022-10-05 18:35 | 18.4 | 23 | 34
1115 | 2022-10-05 18:36 | 18.5 | 23 | 19
1116 | 2022-10-05 18:37 | 18.7 | 22.9 | 18
1117 | 2022-10-05 18:38 | 18.6 | 23.3 | 17
1118 | 2022-10-05 18:39 | 18.4 | 23.3 | 16
1119 | 2022-10-05 18:40 | 18.4 | 23.4 | 16
1120 | 2022-10-05 18:41 | 18.3 | 23.3 | 15
1121 | 2022-10-05 18:42 | 18.3 | 23.2 | 14
1122 | 2022-10-05 18:43 | 18.2 | 23 | 13
1123 | 2022-10-05 18:44 | 18 | 23.2 | 13
1124 | 2022-10-05 18:45 | 18 | 23.1 | 12
1125 | 2022-10-05 18:46 | 18 | 23.2 | 11
1126 | 2022-10-05 18:47 | 18.1 | 23.2 | 10
1127 | 2022-10-05 18:48 | 18 | 22.9 | 9
1128 | 2022-10-05 18:49 | 17.9 | 23 | 9
1129 | 2022-10-05 18:50 | 17.8 | 23.1 | 8
1130 | 2022-10-05 18:51 | 17.7 | 23 | 7
1131 | 2022-10-05 18:52 | 17.7 | 23 | 7
1132 | 2022-10-05 18:53 | 17.8 | 23.1 | 6
1133 | 2022-10-05 18:54 | 17.7 | 23.1 | 5
1134 | 2022-10-05 18:55 | 17.7 | 23.1 | 5
1135 | 2022-10-05 18:56 | 17.6 | 23.1 | 4
1136 | 2022-10-05 18:57 | 17.6 | 23 | 3
1137 | 2022-10-05 18:58 | 17.6 | 23 | 3
1138 | 2022-10-05 18:59 | 17.5 | 22.9 | 2
1139 | 2022-10-05 19:00 | 17.7 | 23.4 | 2
1140 | 2022-10-05 19:01 | 17.5 | 23.1 | 1
1141 | 2022-10-05 19:02 | 17.5 | 23.1 | 1
1142 | 2022-10-05 19:03 | 17.5 | 23 | 0
1143 | 2022-10-05 19:04 | 17.5 | 23 | 0
1144 | 2022-10-05 19:05 | 17.4 | 23 | 0
1145 | 2022-10-05 19:06 | 17.4 | 23 | 0
1146 | 2022-10-05 19:07 | 17.5 | 22.9 | 0
1147 | 2022-10-05 19:08 | 17.4 | 22.9 | 0
1148 | 2022-10-05 19:09 | 17.4 | 23 | 0
1149 | 2022-10-05 19:10 | 17.5 | 22.9 | 0
1150 | 2022-10-05 19:11 | 17.6 | 22.8 | 0
1151 | 2022-10-05 19:12 | 17.4 | 22.4 | 0
1152 | 2022-10-05 19:13 | 17.5 | 23.2 | 0
1153 | 2022-10-05 19:14 | 17.3 | 22.6 | 0
1154 | 2022-10-05 19:15 | 17.3 | 22.9 | 0
1155 | 2022-10-05 19:16 | 17.3 | 23.1 | 0
1156 | 2022-10-05 19:17 | 17.4 | 22.8 | 0
1157 | 2022-10-05 19:18 | 17.3 | 22.8 | 0
1158 | 2022-10-05 19:19 | 17.3 | 23.2 | 0
1159 | 2022-10-05 19:20 | 17.4 | 22.5 | 0
1160 | 2022-10-05 19:21 | 17.3 | 22.9 | 0
1161 | 2022-10-05 19:22 | 17.2 | 23.1 | 0
1162 | 2022-10-05 19:23 | 17.2 | 23.2 | 0
1163 | 2022-10-05 19:24 | 17.2 | 22.6 | 0
1164 | 2022-10-05 19:25 | 17.3 | 22.8 | 0
1165 | 2022-10-05 19:26 | 17.3 | 22.1 | 0
1166 | 2022-10-05 19:27 | 17.3 | 22.7 | 0
1167 | 2022-10-05 19:28 | 17.3 | 23.1 | 0
1168 | 2022-10-05 19:29 | 17.1 | 22.8 | 0
1169 | 2022-10-05 19:30 | 17.2 | 23 | 0
1170 | 2022-10-05 19:31 | 17.1 | 23.7 | 0
1171 | 2022-10-05 19:32 | 17 | 22.8 | 0
1172 | 2022-10-05 19:33 | 17.1 | 23.2 | 0
1173 | 2022-10-05 19:34 | 17.1 | 23.4 | 0
1174 | 2022-10-05 19:35 | 17.1 | 22.5 | 0
1175 | 2022-10-05 19:36 | 17 | 23 | 0
1176 | 2022-10-05 19:37 | 17.1 | 22.8 | 0
1177 | 2022-10-05 19:38 | 17 | 22.6 | 0
1178 | 2022-10-05 19:39 | 17 | 23.2 | 0
1179 | 2022-10-05 19:40 | 17 | 22.9 | 0
1180 | 2022-10-05 19:41 | 16.9 | 22.6 | 0
1181 | 2022-10-05 19:42 | 16.9 | 23.1 | 0
1182 | 2022-10-05 19:43 | 16.8 | 22.7 | 0
1183 | 2022-10-05 19:44 | 16.9 | 22.9 | 0
1184 | 2022-10-05 19:45 | 16.8 | 22.9 | 0
1185 | 2022-10-05 19:46 | 17 | 22.7 | 0
1186 | 2022-10-05 19:47 | 17 | 22.6 | 0
1187 | 2022-10-05 19:48 | 17.1 | 23.1 | 0
1188 | 2022-10-05 19:49 | 16.9 | 22.9 | 0
1189 | 2022-10-05 19:50 | 16.8 | 23.2 | 0
1190 | 2022-10-05 19:51 | 16.8 | 22.7 | 0
1191 | 2022-10-05 19:52 | 17 | 22.8 | 0
1192 | 2022-10-05 19:53 | 16.8 | 22.9 | 0
1193 | 2022-10-05 19:54 | 16.9 | 22.7 | 0
1194 | 2022-10-05 19:55 | 16.8 | 23 | 0
1195 | 2022-10-05 19:56 | 16.9 | 22.5 | 0
1196 | 2022-10-05 19:57 | 16.8 | 23.1 | 0
1197 | 2022-10-05 19:58 | 16.9 | 23.2 | 0
1198 | 2022-10-05 19:59 | 16.7 | 22.4 | 0
1199 | 2022-10-05 20:00 | 16.8 | 22.7 | 0
1200 | 2022-10-05 20:01 | 16.7 | 23 | 0
1201 | 2022-10-05 20:02 | 16.7 | 22.9 | 0
1202 | 2022-10-05 20:03 | 16.8 | 23 | 0
1203 | 2022-10-05 20:04 | 16.8 | 22.9 | 0
1204 | 2022-10-05 20:05 | 16.8 | 23 | 0
1205 | 2022-10-05 20:06 | 16.7 | 23 | 0
1206 | 2022-10-05 20:07 | 16.8 | 22.8 | 0
1207 | 2022-10-05 20:08 | 16.8 | 22.9 | 0
1208 | 2022-10-05 20:09 | 16.7 | 22.9 | 0
1209 | 2022-10-05 20:10 | 16.8 | 22.9 | 0
1210 | 2022-10-05 20:11 | 16.7 | 22.8 | 0
1211 | 2022-10-05 20:12 | 16.7 | 22.7 | 0
1212 | 2022-10-05 20:13 | 16.7 | 23.1 | 0
1213 | 2022-10-05 20:14 | 16.7 | 22.5 | 0
1214 | 2022-10-05 20:15 | 16.7 | 23 | 0
1215 | 2022-10-05 20:16 | 16.6 | 22.9 | 0
1216 | 2022-10-05 20:17 | 16.7 | 22.8 | 0
1217 | 2022-10-05 20:18 | 16.8 | 23.4 | 0
1218 | 2022-10-05 20:19 | 16.9 | 23.3 | 0
1219 | 2022-10-05 20:20 | 16.8 | 22.7 | 0
1220 | 2022-10-05 20:21 | 16.6 | 22.4 | 0
1221 | 2022-10-05 20:22 | 16.6 | 22.8 | 0
1222 | 2022-10-05 20:23 | 16.6 | 22.7 | 0
1223 | 2022-10-05 20:24 | 16.7 | 23.4 | 0
1224 | 2022-10-05 20:25 | 16.5 | 23.1 | 0
1225 | 2022-10-05 20:26 | 16.5 | 23.1 | 0
1226 | 2022-10-05 20:27 | 16.7 | 22.1 | 0
1227 | 2022-10-05 20:28 | 16.7 | 22.3 | 0
1228 | 2022-10-05 20:29 | 16.7 | 22.2 | 0
1229 | 2022-10-05 20:30 | 16.6 | 23.3 | 0
1230 | 2022-10-05 20:31 | 16.7 | 22.6 | 0
1231 | 2022-10-05 20:32 | 16.8 | 22.1 | 0
1232 | 2022-10-05 20:33 | 16.8 | 22.9 | 0
1233 | 2022-10-05 20:34 | 16.7 | 22.9 | 0
1234 | 2022-10-05 20:35 | 16.7 | 22.6 | 0
1235 | 2022-10-05 20:36 | 16.6 | 22.9 | 0
1236 | 2022-10-05 20:37 | 16.7 | 23.2 | 0
1237 | 2022-10-05 20:38 | 16.6 | 23.3 | 0
1238 | 2022-10-05 20:39 | 16.6 | 22.8 | 0
1239 | 2022-10-05 20:40 | 16.5 | 22.1 | 0
1240 | 2022-10-05 20:41 | 16.6 | 22 | 0
1241 | 2022-10-05 20:42 | 16.3 | 23.6 | 0
1242 | 2022-10-05 20:43 | 16.5 | 22.4 | 0
1243 | 2022-10-05 20:44 | 16.3 | 23.4 | 0
1244 | 2022-10-05 20:45 | 16.4 | 23.7 | 0
1245 | 2022-10-05 20:46 | 16.5 | 22.8 | 0
1246 | 2022-10-05 20:47 | 16.5 | 22.8 | 0
1247 | 2022-10-05 20:48 | 16.4 | 22.6 | 0
1248 | 2022-10-05 20:49 | 16.5 | 22.4 | 0
1249 | 2022-10-05 20:50 | 16.4 | 22.8 | 0
1250 | 2022-10-05 20:51 | 16.4 | 22.7 | 0
1251 | 2022-10-05 20:52 | 16.6 | 22.8 | 0
1252 | 2022-10-05 20:53 | 16.4 | 23 | 0
1253 | 2022-10-05 20:54 | 16.5 | 22.5 | 0
1254 | 2022-10-05 20:55 | 16.3 | 22.8 | 0
1255 | 2022-10-05 20:56 | 16.4 | 23.1 | 0
1256 | 2022-10-05 20:57 | 16.5 | 22.9 | 0
1257 | 2022-10-05 20:58 | 16.4 | 23.1 | 0
1258 | 2022-10-05 20:59 | 16.4 | 22.5 | 0
1259 | 2022-10-05 21:00 | 16.5 | 22.5 | 0
1260 | 2022-10-05 21:01 | 16.4 | 22.6 | 0
1261 | 2022-10-05 21:02 | 16.3 | 22.8 | 0
1262 | 2022-10-05 21:03 | 16.2 | 22.7 | 0
1263 | 2022-10-05 21:04 | 16.3 | 22.8 | 0
1264 | 2022-10-05 21:05 | 16.3 | 22.8 | 0
1265 | 2022-10-05 21:06 | 16.3 | 22.7 | 0
1266 | 2022-10-05 21:07 | 16.5 | 22.4 | 0
1267 | 2022-10-05 21:08 | 16.4 | 22.6 | 0
1268 | 2022-10-05 21:09 | 16.4 | 23.1 | 0
1269 | 2022-10-05 21:10 | 16.3 | 22.7 | 0
1270 | 2022-10-05 21:11 | 16.4 | 22.9 | 0
1271 | 2022-10-05 21:12 | 16.7 | 22.9 | 0
1272 | 2022-10-05 21:13 | 16.7 | 23.1 | 0
1273 | 2022-10-05 21:14 | 16.6 | 22.6 | 0
1274 | 2022-10-05 21:15 | 16.6 | 22.9 | 0
1275 | 2022-10-05 21:16 | 16.5 | 23.2 | 0
1276 | 2022-10-05 21:17 | 16.6 | 22.9 | 0
1277 | 2022-10-05 21:18 | 16.6 | 22.9 | 0
1278 | 2022-10-05 21:19 | 16.4 | 22.9 | 0
1279 | 2022-10-05 21:20 | 16.3 | 22.5 | 0
1280 | 2022-10-05 21:21 | 16.5 | 23 | 0
1281 | 2022-10-05 21:22 | 16.5 | 22.8 | 0
1282 | 2022-10-05 21:23 | 16.3 | 22.5 | 0
1283 | 2022-10-05 21:24 | 16.3 | 22.8 | 0
1284 | 2022-10-05 21:25 | 16.5 | 22.9 | 0
1285 | 2022-10-05 21:26 | 16.5 | 22.9 | 0
1286 | 2022-10-05 21:27 | 16.6 | 23 | 0
1287 | 2022-10-05 21:28 | 16.6 | 22.7 | 0
1288 | 2022-10-05 21:29 | 16.4 | 22.5 | 0
1289 | 2022-10-05 21:30 | 16.4 | 22.5 | 0
1290 | 2022-10-05 21:31 | 16.4 | 22.8 | 0
1291 | 2022-10-05 21:32 | 16.6 | 23.1 | 0
1292 | 2022-10-05 21:33 | 16.6 | 23.3 | 0
1293 | 2022-10-05 21:34 | 16.6 | 22.6 | 0
1294 | 2022-10-05 21:35 | 16.6 | 22.7 | 0
1295 | 2022-10-05 21:36 | 16.6 | 22.6 | 0
1296 | 2022-10-05 21:37 | 16.6 | 22.7 | 0
1297 | 2022-10-05 21:38 | 16.6 | 22.8 | 0
1298 | 2022-10-05 21:39 | 16.4 | 22.7 | 0
1299 | 2022-10-05 21:40 | 16.4 | 22.7 | 0
1300 | 2022-10-05 21:41 | 16.5 | 22.9 | 0
1301 | 2022-10-05 21:42 | 16.6 | 23 | 0
1302 | 2022-10-05 21:43 | 16.6 | 22.9 | 0
1303 | 2022-10-05 21:44 | 16.4 | 22.6 | 0
1304 | 2022-10-05 21:45 | 16.4 | 23 | 0
1305 | 2022-10-05 21:46 | 16.2 | 22.5 | 0
1306 | 2022-10-05 21:47 | 16.4 | 22.6 | 0
1307 | 2022-10-05 21:48 | 16.4 | 23.6 | 0
1308 | 2022-10-05 21:49 | 16.2 | 22.9 | 0
1309 | 2022-10-05 21:50 | 16.2 | 22.9 | 0
1310 | 2022-10-05 21:51 | 16.3 | 22.6 | 0
1311 | 2022-10-05 21:52 | 16.4 | 22.7 | 0
1312 | 2022-10-05 21:53 | 16.4 | 22.8 | 0
1313 | 2022-10-05 21:54 | 16.3 | 22.8 | 0
1314 | 2022-10-05 21:55 | 16.3 | 22.9 | 0
1315 | 2022-10-05 21:56 | 16.1 | 23 | 0
1316 | 2022-10-05 21:57 | 16.2 | 22.8 | 0
1317 | 2022-10-05 21:58 | 16 | 22.7 | 0
1318 | 2022-10-05 21:59 | 16.1 | 22.7 | 0
1319 | 2022-10-05 22:00 | 16.2 | 22.8 | 0
1320 | 2022-10-05 22:01 | 16.1 | 22.5 | 0
1321 | 2022-10-05 22:02 | 16.2 | 22.7 | 0
1322 | 2022-10-05 22:03 | 16.3 | 22.8 | 0
1323 | 2022-10-05 22:04 | 16.2 | 22.8 | 0
1324 | 2022-10-05 22:05 | 16.2 | 22.8 | 0
1325 | 2022-10-05 22:06 | 16.2 | 22.7 | 0
1326 | 2022-10-05 22:07 | 16.2 | 22.6 | 0
1327 | 2022-10-05 22:08 | 16.3 | 22.9 | 0
1328 | 2022-10-05 22:09 | 16.4 | 23 | 0
1329 | 2022-10-05 22:10 | 16.3 | 22.5 | 0
1330 | 2022-10-05 22:11 | 16.5 | 23 | 0
1331 | 2022-10-05 22:12 | 16.3 | 22.3 | 0
1332 | 2022-10-05 22:13 | 16.4 | 22.6 | 0
1333 | 2022-10-05 22:14 | 16.3 | 22.7 | 0
1334 | 2022-10-05 22:15 | 16.1 | 22.8 | 0
1335 | 2022-10-05 22:16 | 16.1 | 22.9 | 0
1336 | 2022-10-05 22:17 | 16.1 | 22.6 | 0
1337 | 2022-10-05 22:18 | 16.2 | 22.7 | 0
1338 | 2022-10-05 22:19 | 16.4 | 23.5 | 0
1339 | 2022-10-05 22:20 | 16.2 | 23.3 | 0
1340 | 2022-10-05 22:21 | 16.2 | 22.6 | 0
1341 | 2022-10-05 22:22 | 16.2 | 22.8 | 0
1342 | 2022-10-05 22:23 | 16.4 | 22.6 | 0
1343 | 2022-10-05 22:24 | 16.2 | 22.8 | 0
1344 | 2022-10-05 22:25 | 16.4 | 22.4 | 0
1345 | 2022-10-05 22:26 | 16.4 | 22.8 | 0
1346 | 2022-10-05 22:27 | 16.3 | 23 | 0
1347 | 2022-10-05 22:28 | 16.3 | 22.7 | 0
1348 | 2022-10-05 22:29 | 16.2 | 23 | 0
1349 | 2022-10-05 22:30 | 16.3 | 22.6 | 0
1350 | 2022-10-05 22:31 | 16.1 | 22.9 | 0
1351 | 2022-10-05 22:32 | 16.1 | 23.6 | 0
1352 | 2022-10-05 22:33 | 16.1 | 23.4 | 0
1353 | 2022-10-05 22:34 | 16.3 | 21.9 | 0
1354 | 2022-10-05 22:35 | 16.2 | 22.3 | 0
1355 | 2022-10-05 22:36 | 16.2 | 22.7 | 0
1356 | 2022-10-05 22:37 | 16 | 22.7 | 0
1357 | 2022-10-05 22:38 | 16 | 22.4 | 0
1358 | 2022-10-05 22:39 | 15.9 | 22.9 | 0
1359 | 2022-10-05 22:40 | 15.9 | 22.9 | 0
1360 | 2022-10-05 22:41 | 15.8 | 22.6 | 0
1361 | 2022-10-05 22:42 | 15.7 | 22.6 | 0
1362 | 2022-10-05 22:43 | 16 | 22.9 | 0
1363 | 2022-10-05 22:44 | 16.1 | 22.6 | 0
1364 | 2022-10-05 22:45 | 16.1 | 22.6 | 0
1365 | 2022-10-05 22:46 | 16.1 | 22.5 | 0
1366 | 2022-10-05 22:47 | 16.1 | 22.7 | 0
1367 | 2022-10-05 22:48 | 15.9 | 22.8 | 0
1368 | 2022-10-05 22:49 | 16.1 | 23 | 0
1369 | 2022-10-05 22:50 | 16 | 22.7 | 0
1370 | 2022-10-05 22:51 | 15.9 | 22.8 | 0
1371 | 2022-10-05 22:52 | 16.1 | 22.9 | 0
1372 | 2022-10-05 22:53 | 15.9 | 22.8 | 0
1373 | 2022-10-05 22:54 | 16 | 22.8 | 0
1374 | 2022-10-05 22:55 | 16.2 | 22.7 | 0
1375 | 2022-10-05 22:56 | 16 | 22.4 | 0
1376 | 2022-10-05 22:57 | 16 | 22.6 | 0
1377 | 2022-10-05 22:58 | 16 | 22.6 | 0
1378 | 2022-10-05 22:59 | 15.9 | 23.4 | 0
1379 | 2022-10-05 23:00 | 15.9 | 23 | 0
1380 | 2022-10-05 23:01 | 15.7 | 22.9 | 0
1381 | 2022-10-05 23:02 | 15.4 | 22.7 | 0
1382 | 2022-10-05 23:03 | 15.4 | 22.7 | 0
1383 | 2022-10-05 23:04 | 15.4 | 22.7 | 0
1384 | 2022-10-05 23:05 | 15.1 | 22.8 | 0
1385 | 2022-10-05 23:06 | 15.2 | 22.7 | 0
1386 | 2022-10-05 23:07 | 15.4 | 22.6 | 0
1387 | 2022-10-05 23:08 | 15.4 | 22.7 | 0
1388 | 2022-10-05 23:09 | 15.3 | 22.8 | 0
1389 | 2022-10-05 23:10 | 15.4 | 22.6 | 0
1390 | 2022-10-05 23:11 | 15.1 | 22.8 | 0
1391 | 2022-10-05 23:12 | 15.1 | 22.6 | 0
1392 | 2022-10-05 23:13 | 14.8 | 22.8 | 0
1393 | 2022-10-05 23:14 | 14.7 | 22.7 | 0
1394 | 2022-10-05 23:15 | 14.6 | 22.7 | 0
1395 | 2022-10-05 23:16 | 14.6 | 22.3 | 0
1396 | 2022-10-05 23:17 | 14.5 | 22.8 | 0
1397 | 2022-10-05 23:18 | 14.4 | 23 | 0
1398 | 2022-10-05 23:19 | 14.3 | 22.7 | 0
1399 | 2022-10-05 23:20 | 14.3 | 22.9 | 0
1400 | 2022-10-05 23:21 | 14.3 | 22.4 | 0
1401 | 2022-10-05 23:22 | 14.4 | 22.5 | 0
1402 | 2022-10-05 23:23 | 14.5 | 22.7 | 0
1403 | 2022-10-05 23:24 | 14.7 | 23.3 | 0
1404 | 2022-10-05 23:25 | 14.8 | 22.2 | 0
1405 | 2022-10-05 23:26 | 14.7 | 22.7 | 0
1406 | 2022-10-05 23:27 | 15 | 22.9 | 0
1407 | 2022-10-05 23:28 | 15 | 23.5 | 0
1408 | 2022-10-05 23:29 | 14.7 | 22.3 | 0
1409 | 2022-10-05 23:30 | 14.4 | 22.2 | 0
1410 | 2022-10-05 23:31 | 14.4 | 22.9 | 0
1411 | 2022-10-05 23:32 | 14.2 | 22.7 | 0
1412 | 2022-10-05 23:33 | 14.3 | 22.7 | 0
1413 | 2022-10-05 23:34 | 14.8 | 22.8 | 0
1414 | 2022-10-05 23:35 | 14.9 | 22.7 | 0
1415 | 2022-10-05 23:36 | 14.5 | 22.7 | 0
1416 | 2022-10-05 23:37 | 14.5 | 22 | 0
1417 | 2022-10-05 23:38 | 14.2 | 23 | 0
1418 | 2022-10-05 23:39 | 14.6 | 23.1 | 0
1419 | 2022-10-05 23:40 | 14.9 | 23.4 | 0
1420 | 2022-10-05 23:41 | 14.8 | 22.5 | 0
1421 | 2022-10-05 23:42 | 14.7 | 22.6 | 0
1422 | 2022-10-05 23:43 | 14.6 | 23.3 | 0
1423 | 2022-10-05 23:44 | 14.4 | 22.7 | 0
1424 | 2022-10-05 23:45 | 14.8 | 22.4 | 0
1425 | 2022-10-05 23:46 | 15.1 | 22.1 | 0
1426 | 2022-10-05 23:47 | 15 | 22.8 | 0
1427 | 2022-10-05 23:48 | 14.5 | 22.4 | 0
1428 | 2022-10-05 23:49 | 14.7 | 22.9 | 0
1429 | 2022-10-05 23:50 | 14.3 | 23 | 0
1430 | 2022-10-05 23:51 | 14.8 | 22.4 | 0
1431 | 2022-10-05 23:52 | 14.4 | 22.9 | 0
1432 | 2022-10-05 23:53 | 14.4 | 22.6 | 0
1433 | 2022-10-05 23:54 | 14.1 | 22.5 | 0
1434 | 2022-10-05 23:55 | 14 | 22.7 | 0
1435 | 2022-10-05 23:56 | 14.2 | 22.3 | 0
1436 | 2022-10-05 23:57 | 14 | 22.8 | 0
1437 | 2022-10-05 23:58 | 14 | 22.5 | 0
1438 | 2022-10-05 23:59 | 14.3 | 22.7 | 0
1439 | 2022-10-06 | 14.4 | 22.6 | 0

## 06-10-2022_NO HEAT
| Date&time_x | OUTDOOR_TEMP | INDOOR_TEMP | PYRANOMETER
0 | 2022-10-06 00:01 | 14.8 | 22.8 | 0
1 | 2022-10-06 00:02 | 14.7 | 22.8 | 0
2 | 2022-10-06 00:03 | 14.5 | 22.7 | 0
3 | 2022-10-06 00:04 | 14.6 | 22.6 | 0
4 | 2022-10-06 00:05 | 14.3 | 22.5 | 0
5 | 2022-10-06 00:06 | 14.4 | 22.8 | 0
6 | 2022-10-06 00:07 | 14.2 | 22.8 | 0
7 | 2022-10-06 00:08 | 14.3 | 22.7 | 0
8 | 2022-10-06 00:09 | 14.5 | 22.6 | 0
9 | 2022-10-06 00:10 | 15 | 23.1 | 0
10 | 2022-10-06 00:11 | 15.1 | 22.4 | 0
11 | 2022-10-06 00:12 | 15.1 | 22.9 | 0
12 | 2022-10-06 00:13 | 15.3 | 23 | 0
13 | 2022-10-06 00:14 | 15.2 | 22.9 | 0
14 | 2022-10-06 00:15 | 14.9 | 22.6 | 0
15 | 2022-10-06 00:16 | 14.7 | 22.6 | 0
16 | 2022-10-06 00:17 | 14.8 | 23.1 | 0
17 | 2022-10-06 00:18 | 14.8 | 23.4 | 0
18 | 2022-10-06 00:19 | 15.2 | 22.3 | 0
19 | 2022-10-06 00:20 | 14.8 | 22.9 | 0
20 | 2022-10-06 00:21 | 14.7 | 21.8 | 0
21 | 2022-10-06 00:22 | 14.4 | 23.1 | 0
22 | 2022-10-06 00:23 | 14.6 | 22.4 | 0
23 | 2022-10-06 00:24 | 14.4 | 22.6 | 0
24 | 2022-10-06 00:25 | 14.4 | 22.7 | 0
25 | 2022-10-06 00:26 | 14.2 | 22.7 | 0
26 | 2022-10-06 00:27 | 14.1 | 22.3 | 0
27 | 2022-10-06 00:28 | 13.9 | 23.6 | 0
28 | 2022-10-06 00:29 | 13.9 | 23 | 0
29 | 2022-10-06 00:30 | 13.8 | 22.9 | 0
30 | 2022-10-06 00:31 | 13.7 | 23 | 0
31 | 2022-10-06 00:32 | 13.6 | 23.5 | 0
32 | 2022-10-06 00:33 | 13.8 | 22.5 | 0
33 | 2022-10-06 00:34 | 13.4 | 23 | 0
34 | 2022-10-06 00:35 | 13.4 | 22.3 | 0
35 | 2022-10-06 00:36 | 13.3 | 23 | 0
36 | 2022-10-06 00:37 | 13.3 | 21.9 | 0
37 | 2022-10-06 00:38 | 13.5 | 22.7 | 0
38 | 2022-10-06 00:39 | 13.3 | 22.8 | 0
39 | 2022-10-06 00:40 | 13.3 | 22.8 | 0
40 | 2022-10-06 00:41 | 13.4 | 23.2 | 0
41 | 2022-10-06 00:42 | 13.3 | 22.9 | 0
42 | 2022-10-06 00:43 | 13.3 | 22.6 | 0
43 | 2022-10-06 00:44 | 13.2 | 22.6 | 0
44 | 2022-10-06 00:45 | 13.2 | 22.7 | 0
45 | 2022-10-06 00:46 | 13.1 | 22.8 | 0
46 | 2022-10-06 00:47 | 13.2 | 22.6 | 0
47 | 2022-10-06 00:48 | 13 | 22.9 | 0
48 | 2022-10-06 00:49 | 13.2 | 23.1 | 0
49 | 2022-10-06 00:50 | 13.5 | 22.6 | 0
50 | 2022-10-06 00:51 | 13.6 | 22.1 | 0
51 | 2022-10-06 00:52 | 13.4 | 22.6 | 0
52 | 2022-10-06 00:53 | 13.9 | 22.6 | 0
53 | 2022-10-06 00:54 | 13.8 | 22.8 | 0
54 | 2022-10-06 00:55 | 14.4 | 22.8 | 0
55 | 2022-10-06 00:56 | 14.8 | 22.6 | 0
56 | 2022-10-06 00:57 | 14.4 | 22.8 | 0
57 | 2022-10-06 00:58 | 14.3 | 22.8 | 0
58 | 2022-10-06 00:59 | 14 | 22.6 | 0
59 | 2022-10-06 01:00 | 14.2 | 23 | 0
60 | 2022-10-06 01:01 | 14.1 | 22.8 | 0
61 | 2022-10-06 01:02 | 14 | 22.6 | 0
62 | 2022-10-06 01:03 | 14.1 | 22.5 | 0
63 | 2022-10-06 01:04 | 13.8 | 22.5 | 0
64 | 2022-10-06 01:05 | 13.7 | 22.7 | 0
65 | 2022-10-06 01:06 | 13.5 | 22.6 | 0
66 | 2022-10-06 01:07 | 13.3 | 22.7 | 0
67 | 2022-10-06 01:08 | 13.3 | 22.6 | 0
68 | 2022-10-06 01:09 | 13.4 | 22.6 | 0
69 | 2022-10-06 01:10 | 13.3 | 22.6 | 0
70 | 2022-10-06 01:11 | 13.2 | 22.7 | 0
71 | 2022-10-06 01:12 | 13.1 | 22.6 | 0
72 | 2022-10-06 01:13 | 13.1 | 22.5 | 0
73 | 2022-10-06 01:14 | 13 | 22.6 | 0
74 | 2022-10-06 01:15 | 13.1 | 22.6 | 0
75 | 2022-10-06 01:16 | 13.1 | 22.7 | 0
76 | 2022-10-06 01:17 | 13 | 22.6 | 0
77 | 2022-10-06 01:18 | 12.9 | 22.6 | 0
78 | 2022-10-06 01:19 | 13 | 22.6 | 0
79 | 2022-10-06 01:20 | 12.8 | 22.6 | 0
80 | 2022-10-06 01:21 | 12.9 | 22.6 | 0
81 | 2022-10-06 01:22 | 13 | 22.6 | 0
82 | 2022-10-06 01:23 | 14.2 | 23 | 0
83 | 2022-10-06 01:24 | 14.7 | 23.1 | 0
84 | 2022-10-06 01:25 | 15 | 22.5 | 0
85 | 2022-10-06 01:26 | 14.6 | 23 | 0
86 | 2022-10-06 01:27 | 14.2 | 23 | 0
87 | 2022-10-06 01:28 | 13.7 | 22.9 | 0
88 | 2022-10-06 01:29 | 13.4 | 22.5 | 0
89 | 2022-10-06 01:30 | 13.2 | 22.4 | 0
90 | 2022-10-06 01:31 | 13.1 | 22.8 | 0
91 | 2022-10-06 01:32 | 12.9 | 23 | 0
92 | 2022-10-06 01:33 | 12.8 | 22.6 | 0
93 | 2022-10-06 01:34 | 13 | 22.8 | 0
94 | 2022-10-06 01:35 | 12.9 | 22.4 | 0
95 | 2022-10-06 01:36 | 12.9 | 22.4 | 0
96 | 2022-10-06 01:37 | 12.8 | 22.5 | 0
97 | 2022-10-06 01:38 | 12.7 | 22.6 | 0
98 | 2022-10-06 01:39 | 12.6 | 22.4 | 0
99 | 2022-10-06 01:40 | 12.5 | 22.7 | 0
100 | 2022-10-06 01:41 | 12.4 | 22.6 | 0
101 | 2022-10-06 01:42 | 12.6 | 22.5 | 0
102 | 2022-10-06 01:43 | 12.6 | 22.5 | 0
103 | 2022-10-06 01:44 | 12.5 | 22.7 | 0
104 | 2022-10-06 01:45 | 12.5 | 22.5 | 0
105 | 2022-10-06 01:46 | 12.4 | 22.5 | 0
106 | 2022-10-06 01:47 | 12.5 | 22.8 | 0
107 | 2022-10-06 01:48 | 12.3 | 22.9 | 0
108 | 2022-10-06 01:49 | 12.4 | 22.5 | 0
109 | 2022-10-06 01:50 | 12.4 | 22.7 | 0
110 | 2022-10-06 01:51 | 12.3 | 22.6 | 0
111 | 2022-10-06 01:52 | 12.3 | 22.5 | 0
112 | 2022-10-06 01:53 | 12.3 | 22.7 | 0
113 | 2022-10-06 01:54 | 12.2 | 22.6 | 0
114 | 2022-10-06 01:55 | 12.3 | 22.5 | 0
115 | 2022-10-06 01:56 | 12.4 | 22.5 | 0
116 | 2022-10-06 01:57 | 12.4 | 23.1 | 0
117 | 2022-10-06 01:58 | 12.4 | 22.4 | 0
118 | 2022-10-06 01:59 | 12.5 | 22.6 | 0
119 | 2022-10-06 02:00 | 12.2 | 22.6 | 0
120 | 2022-10-06 02:01 | 12.2 | 22.1 | 0
121 | 2022-10-06 02:02 | 12.1 | 22.4 | 0
122 | 2022-10-06 02:03 | 12.1 | 22.4 | 0
123 | 2022-10-06 02:04 | 12.1 | 22.6 | 0
124 | 2022-10-06 02:05 | 12.2 | 22.5 | 0
125 | 2022-10-06 02:06 | 12.1 | 22.5 | 0
126 | 2022-10-06 02:07 | 12 | 22.5 | 0
127 | 2022-10-06 02:08 | 12 | 22.6 | 0
128 | 2022-10-06 02:09 | 11.9 | 22.9 | 0
129 | 2022-10-06 02:10 | 12.1 | 22.8 | 0
130 | 2022-10-06 02:11 | 12 | 22.6 | 0
131 | 2022-10-06 02:12 | 12.2 | 22.7 | 0
132 | 2022-10-06 02:13 | 12.3 | 22.7 | 0
133 | 2022-10-06 02:14 | 12.1 | 22.3 | 0
134 | 2022-10-06 02:15 | 12 | 22.3 | 0
135 | 2022-10-06 02:16 | 12.1 | 23.1 | 0
136 | 2022-10-06 02:17 | 12.1 | 22.6 | 0
137 | 2022-10-06 02:18 | 11.9 | 22.1 | 0
138 | 2022-10-06 02:19 | 12.1 | 23.1 | 0
139 | 2022-10-06 02:20 | 12.1 | 23 | 0
140 | 2022-10-06 02:21 | 12.2 | 22.2 | 0
141 | 2022-10-06 02:22 | 12.1 | 21.9 | 0
142 | 2022-10-06 02:23 | 12.1 | 21.6 | 0
143 | 2022-10-06 02:24 | 12.2 | 22.4 | 0
144 | 2022-10-06 02:25 | 12 | 22 | 0
145 | 2022-10-06 02:26 | 12.1 | 23 | 0
146 | 2022-10-06 02:27 | 12.1 | 22.3 | 0
147 | 2022-10-06 02:28 | 12.2 | 21.8 | 0
148 | 2022-10-06 02:29 | 12 | 22.6 | 0
149 | 2022-10-06 02:30 | 12 | 22.5 | 0
150 | 2022-10-06 02:31 | 12.1 | 23.1 | 0
151 | 2022-10-06 02:32 | 12 | 23.1 | 0
152 | 2022-10-06 02:33 | 12 | 23.3 | 0
153 | 2022-10-06 02:34 | 12 | 22.8 | 0
154 | 2022-10-06 02:35 | 12 | 22.3 | 0
155 | 2022-10-06 02:36 | 12.2 | 22.7 | 0
156 | 2022-10-06 02:37 | 12.1 | 22.5 | 0
157 | 2022-10-06 02:38 | 12.3 | 22.8 | 0
158 | 2022-10-06 02:39 | 12.2 | 22.6 | 0
159 | 2022-10-06 02:40 | 12.8 | 23.3 | 0
160 | 2022-10-06 02:41 | 12.8 | 23.2 | 0
161 | 2022-10-06 02:42 | 13 | 22.5 | 0
162 | 2022-10-06 02:43 | 13.2 | 22.9 | 0
163 | 2022-10-06 02:44 | 13.1 | 22.2 | 0
164 | 2022-10-06 02:45 | 12.6 | 22.5 | 0
165 | 2022-10-06 02:46 | 12.6 | 22.3 | 0
166 | 2022-10-06 02:47 | 12.5 | 23 | 0
167 | 2022-10-06 02:48 | 12.4 | 22.2 | 0
168 | 2022-10-06 02:49 | 12.3 | 22.8 | 0
169 | 2022-10-06 02:50 | 12.2 | 22.6 | 0
170 | 2022-10-06 02:51 | 12.4 | 22.7 | 0
171 | 2022-10-06 02:52 | 12.4 | 22.4 | 0
172 | 2022-10-06 02:53 | 12.3 | 22.4 | 0
173 | 2022-10-06 02:54 | 12.3 | 22.3 | 0
174 | 2022-10-06 02:55 | 12.5 | 22.3 | 0
175 | 2022-10-06 02:56 | 12.5 | 22.7 | 0
176 | 2022-10-06 02:57 | 13 | 22.6 | 0
177 | 2022-10-06 02:58 | 13.1 | 22.5 | 0
178 | 2022-10-06 02:59 | 13.2 | 22.7 | 0
179 | 2022-10-06 03:00 | 13.2 | 23.1 | 0
180 | 2022-10-06 03:01 | 13.4 | 23.3 | 0
181 | 2022-10-06 03:02 | 13.6 | 23 | 0
182 | 2022-10-06 03:03 | 13.6 | 22.9 | 0
183 | 2022-10-06 03:04 | 13.5 | 22.1 | 0
184 | 2022-10-06 03:05 | 13.4 | 22.5 | 0
185 | 2022-10-06 03:06 | 13.2 | 21.7 | 0
186 | 2022-10-06 03:07 | 13.1 | 23 | 0
187 | 2022-10-06 03:08 | 13.2 | 22.4 | 0
188 | 2022-10-06 03:09 | 13.2 | 22.6 | 0
189 | 2022-10-06 03:10 | 13.2 | 22.4 | 0
190 | 2022-10-06 03:11 | 13.2 | 22.3 | 0
191 | 2022-10-06 03:12 | 13.2 | 22.5 | 0
192 | 2022-10-06 03:13 | 13.1 | 22.4 | 0
193 | 2022-10-06 03:14 | 13.1 | 22.5 | 0
194 | 2022-10-06 03:15 | 13.1 | 22 | 0
195 | 2022-10-06 03:16 | 13 | 22.6 | 0
196 | 2022-10-06 03:17 | 13.1 | 22.3 | 0
197 | 2022-10-06 03:18 | 13.1 | 22.3 | 0
198 | 2022-10-06 03:19 | 13 | 23.1 | 0
199 | 2022-10-06 03:20 | 12.9 | 22.5 | 0
200 | 2022-10-06 03:21 | 13.2 | 22.6 | 0
201 | 2022-10-06 03:22 | 13.3 | 22.7 | 0
202 | 2022-10-06 03:23 | 13.2 | 22.4 | 0
203 | 2022-10-06 03:24 | 13.2 | 22.8 | 0
204 | 2022-10-06 03:25 | 13.1 | 22.5 | 0
205 | 2022-10-06 03:26 | 13 | 22.4 | 0
206 | 2022-10-06 03:27 | 13.2 | 21.9 | 0
207 | 2022-10-06 03:28 | 13.1 | 22.2 | 0
208 | 2022-10-06 03:29 | 13.2 | 22.1 | 0
209 | 2022-10-06 03:30 | 13.1 | 22.4 | 0
210 | 2022-10-06 03:31 | 13.5 | 22.2 | 0
211 | 2022-10-06 03:32 | 13.9 | 22.5 | 0
212 | 2022-10-06 03:33 | 14.1 | 22.7 | 0
213 | 2022-10-06 03:34 | 14.3 | 22.3 | 0
214 | 2022-10-06 03:35 | 14.5 | 22.6 | 0
215 | 2022-10-06 03:36 | 14.2 | 22.1 | 0
216 | 2022-10-06 03:37 | 14.6 | 22.6 | 0
217 | 2022-10-06 03:38 | 14.5 | 22.6 | 0
218 | 2022-10-06 03:39 | 14.2 | 21.9 | 0
219 | 2022-10-06 03:40 | 14.1 | 22.7 | 0
220 | 2022-10-06 03:41 | 14 | 22.4 | 0
221 | 2022-10-06 03:42 | 14.1 | 22.2 | 0
222 | 2022-10-06 03:43 | 14 | 22.4 | 0
223 | 2022-10-06 03:44 | 14.1 | 22 | 0
224 | 2022-10-06 03:45 | 14.2 | 22.8 | 0
225 | 2022-10-06 03:46 | 14.5 | 23.2 | 0
226 | 2022-10-06 03:47 | 14.4 | 22.3 | 0
227 | 2022-10-06 03:48 | 14.3 | 22.9 | 0
228 | 2022-10-06 03:49 | 14.4 | 22.1 | 0
229 | 2022-10-06 03:50 | 14.3 | 22.1 | 0
230 | 2022-10-06 03:51 | 14.5 | 22.2 | 0
231 | 2022-10-06 03:52 | 14.3 | 23.1 | 0
232 | 2022-10-06 03:53 | 14.4 | 22.1 | 0
233 | 2022-10-06 03:54 | 14.4 | 21.7 | 0
234 | 2022-10-06 03:55 | 14.7 | 22.3 | 0
235 | 2022-10-06 03:56 | 14.6 | 23.2 | 0
236 | 2022-10-06 03:57 | 14.8 | 23 | 0
237 | 2022-10-06 03:58 | 15.1 | 22.3 | 0
238 | 2022-10-06 03:59 | 15.3 | 22.5 | 0
239 | 2022-10-06 04:00 | 15.3 | 21.9 | 0
240 | 2022-10-06 04:01 | 15.3 | 21.9 | 0
241 | 2022-10-06 04:02 | 15.3 | 22.8 | 0
242 | 2022-10-06 04:03 | 15.3 | 22.5 | 0
243 | 2022-10-06 04:04 | 15.1 | 22.6 | 0
244 | 2022-10-06 04:05 | 15 | 22.3 | 0
245 | 2022-10-06 04:06 | 14.7 | 22.5 | 0
246 | 2022-10-06 04:07 | 14.7 | 23.2 | 0
247 | 2022-10-06 04:08 | 14.7 | 23.3 | 0
248 | 2022-10-06 04:09 | 14.7 | 22.4 | 0
249 | 2022-10-06 04:10 | 14.3 | 21.8 | 0
250 | 2022-10-06 04:11 | 14.3 | 22.7 | 0
251 | 2022-10-06 04:12 | 14.3 | 21.6 | 0
252 | 2022-10-06 04:13 | 14.4 | 22.1 | 0
253 | 2022-10-06 04:14 | 14.7 | 22.8 | 0
254 | 2022-10-06 04:15 | 14.6 | 22 | 0
255 | 2022-10-06 04:16 | 14.5 | 22.3 | 0
256 | 2022-10-06 04:17 | 14.5 | 21.8 | 0
257 | 2022-10-06 04:18 | 14.5 | 22.7 | 0
258 | 2022-10-06 04:19 | 14.2 | 21.9 | 0
259 | 2022-10-06 04:20 | 14.3 | 23.1 | 0
260 | 2022-10-06 04:21 | 14.1 | 23.2 | 0
261 | 2022-10-06 04:22 | 14 | 22.4 | 0
262 | 2022-10-06 04:23 | 14 | 22.5 | 0
263 | 2022-10-06 04:24 | 14.4 | 22.8 | 0
264 | 2022-10-06 04:25 | 14.1 | 22 | 0
265 | 2022-10-06 04:26 | 14 | 23 | 0
266 | 2022-10-06 04:27 | 13.8 | 23.2 | 0
267 | 2022-10-06 04:28 | 13.8 | 22.8 | 0
268 | 2022-10-06 04:29 | 13.7 | 22.2 | 0
269 | 2022-10-06 04:30 | 13.6 | 22.6 | 0
270 | 2022-10-06 04:31 | 13.8 | 22.3 | 0
271 | 2022-10-06 04:32 | 13.7 | 22.9 | 0
272 | 2022-10-06 04:33 | 13.7 | 22.2 | 0
273 | 2022-10-06 04:34 | 13.8 | 22.4 | 0
274 | 2022-10-06 04:35 | 13.7 | 22 | 0
275 | 2022-10-06 04:36 | 13.4 | 22.9 | 0
276 | 2022-10-06 04:37 | 13.5 | 23.1 | 0
277 | 2022-10-06 04:38 | 13.8 | 23.1 | 0
278 | 2022-10-06 04:39 | 14.1 | 21.9 | 0
279 | 2022-10-06 04:40 | 14.2 | 21.7 | 0
280 | 2022-10-06 04:41 | 14.2 | 22.3 | 0
281 | 2022-10-06 04:42 | 14.6 | 22 | 0
282 | 2022-10-06 04:43 | 14.6 | 22.9 | 0
283 | 2022-10-06 04:44 | 14.6 | 23.3 | 0
284 | 2022-10-06 04:45 | 14.7 | 23.1 | 0
285 | 2022-10-06 04:46 | 14.8 | 23.2 | 0
286 | 2022-10-06 04:47 | 14.7 | 22.1 | 0
287 | 2022-10-06 04:48 | 14.8 | 22.5 | 0
288 | 2022-10-06 04:49 | 14.7 | 21.8 | 0
289 | 2022-10-06 04:50 | 14.5 | 22.7 | 0
290 | 2022-10-06 04:51 | 14.7 | 23.1 | 0
291 | 2022-10-06 04:52 | 14.8 | 21.6 | 0
292 | 2022-10-06 04:53 | 14.5 | 21.7 | 0
293 | 2022-10-06 04:54 | 14.7 | 22.9 | 0
294 | 2022-10-06 04:55 | 14.3 | 22.4 | 0
295 | 2022-10-06 04:56 | 14.2 | 22.8 | 0
296 | 2022-10-06 04:57 | 14 | 22.1 | 0
297 | 2022-10-06 04:58 | 14.3 | 23.2 | 0
298 | 2022-10-06 04:59 | 14.4 | 22.5 | 0
299 | 2022-10-06 05:00 | 14.4 | 22.4 | 0
300 | 2022-10-06 05:01 | 14.5 | 22.3 | 0
301 | 2022-10-06 05:02 | 14.7 | 22.3 | 0
302 | 2022-10-06 05:03 | 14.5 | 22.4 | 0
303 | 2022-10-06 05:04 | 14.8 | 22.3 | 0
304 | 2022-10-06 05:05 | 14.7 | 22.5 | 0
305 | 2022-10-06 05:06 | 14.6 | 22.7 | 0
306 | 2022-10-06 05:07 | 14.6 | 22 | 0
307 | 2022-10-06 05:08 | 14.4 | 22.3 | 0
308 | 2022-10-06 05:09 | 14.4 | 22.6 | 0
309 | 2022-10-06 05:10 | 14.7 | 22.4 | 0
310 | 2022-10-06 05:11 | 14.9 | 22.3 | 0
311 | 2022-10-06 05:12 | 15 | 22.7 | 0
312 | 2022-10-06 05:13 | 14.8 | 22.1 | 0
313 | 2022-10-06 05:14 | 14.9 | 22.5 | 0
314 | 2022-10-06 05:15 | 15 | 22.1 | 0
315 | 2022-10-06 05:16 | 14.8 | 22.3 | 0
316 | 2022-10-06 05:17 | 14.9 | 22.8 | 0
317 | 2022-10-06 05:18 | 14.8 | 22.3 | 0
318 | 2022-10-06 05:19 | 14.9 | 21.8 | 0
319 | 2022-10-06 05:20 | 15 | 21.4 | 0
320 | 2022-10-06 05:21 | 15 | 21.9 | 0
321 | 2022-10-06 05:22 | 15 | 22.2 | 0
322 | 2022-10-06 05:23 | 14.9 | 21.7 | 0
323 | 2022-10-06 05:24 | 14.7 | 21.7 | 0
324 | 2022-10-06 05:25 | 15 | 22.6 | 0
325 | 2022-10-06 05:26 | 14.9 | 22.6 | 0
326 | 2022-10-06 05:27 | 14.9 | 21.9 | 0
327 | 2022-10-06 05:28 | 14.9 | 22.5 | 0
328 | 2022-10-06 05:29 | 14.8 | 21.6 | 0
329 | 2022-10-06 05:30 | 14.5 | 21.5 | 0
330 | 2022-10-06 05:31 | 14.5 | 22 | 0
331 | 2022-10-06 05:32 | 14.7 | 23 | 0
332 | 2022-10-06 05:33 | 14.7 | 21.7 | 0
333 | 2022-10-06 05:34 | 14.8 | 22.1 | 0
334 | 2022-10-06 05:35 | 14.6 | 22.8 | 0
335 | 2022-10-06 05:36 | 15.2 | 23.1 | 0
336 | 2022-10-06 05:37 | 15.4 | 22.9 | 0
337 | 2022-10-06 05:38 | 15.2 | 22.1 | 0
338 | 2022-10-06 05:39 | 15.1 | 22.5 | 0
339 | 2022-10-06 05:40 | 15.1 | 22.4 | 0
340 | 2022-10-06 05:41 | 15.2 | 22.3 | 0
341 | 2022-10-06 05:42 | 15.2 | 22.3 | 0
342 | 2022-10-06 05:43 | 15.2 | 22.1 | 0
343 | 2022-10-06 05:44 | 15.3 | 22.5 | 0
344 | 2022-10-06 05:45 | 15.4 | 22.3 | 0
345 | 2022-10-06 05:46 | 15.2 | 22.2 | 0
346 | 2022-10-06 05:47 | 15.2 | 22.3 | 0
347 | 2022-10-06 05:48 | 15.3 | 22.9 | 0
348 | 2022-10-06 05:49 | 15.3 | 22.1 | 0
349 | 2022-10-06 05:50 | 15.4 | 21.5 | 0
350 | 2022-10-06 05:51 | 15.3 | 21.6 | 0
351 | 2022-10-06 05:52 | 15.4 | 22.6 | 0
352 | 2022-10-06 05:53 | 15.3 | 22.4 | 0
353 | 2022-10-06 05:54 | 15.4 | 22.7 | 0
354 | 2022-10-06 05:55 | 15.5 | 22.4 | 0
355 | 2022-10-06 05:56 | 15.3 | 21.8 | 0
356 | 2022-10-06 05:57 | 15.3 | 21.7 | 0
357 | 2022-10-06 05:58 | 15.4 | 22.3 | 0
358 | 2022-10-06 05:59 | 15.4 | 21.8 | 0
359 | 2022-10-06 06:00 | 15.4 | 21.9 | 0
360 | 2022-10-06 06:01 | 15.5 | 22.7 | 0
361 | 2022-10-06 06:02 | 15.3 | 22.4 | 0
362 | 2022-10-06 06:03 | 15.4 | 22.3 | 0
363 | 2022-10-06 06:04 | 15.3 | 22.3 | 0
364 | 2022-10-06 06:05 | 15.1 | 22.4 | 0
365 | 2022-10-06 06:06 | 15.3 | 21.9 | 0
366 | 2022-10-06 06:07 | 15.4 | 22.3 | 0
367 | 2022-10-06 06:08 | 15.3 | 22.4 | 0
368 | 2022-10-06 06:09 | 15.3 | 22.1 | 0
369 | 2022-10-06 06:10 | 15.3 | 22.9 | 0
370 | 2022-10-06 06:11 | 15.3 | 22.4 | 0
371 | 2022-10-06 06:12 | 15.2 | 22.3 | 0
372 | 2022-10-06 06:13 | 15.2 | 22.4 | 0
373 | 2022-10-06 06:14 | 15.3 | 22 | 0
374 | 2022-10-06 06:15 | 15.4 | 22.1 | 0
375 | 2022-10-06 06:16 | 15.3 | 22 | 0
376 | 2022-10-06 06:17 | 15.1 | 22.5 | 0
377 | 2022-10-06 06:18 | 15.2 | 22 | 0
378 | 2022-10-06 06:19 | 15.1 | 21.7 | 0
379 | 2022-10-06 06:20 | 15.1 | 22 | 0
380 | 2022-10-06 06:21 | 15 | 21.8 | 0
381 | 2022-10-06 06:22 | 15.1 | 22.5 | 0
382 | 2022-10-06 06:23 | 15 | 21.9 | 0
383 | 2022-10-06 06:24 | 14.8 | 22.2 | 0
384 | 2022-10-06 06:25 | 15 | 22.5 | 0
385 | 2022-10-06 06:26 | 14.9 | 22.1 | 0
386 | 2022-10-06 06:27 | 15.1 | 22.2 | 0
387 | 2022-10-06 06:28 | 15 | 22.6 | 0
388 | 2022-10-06 06:29 | 15.3 | 21.7 | 0
389 | 2022-10-06 06:30 | 15.1 | 22.1 | 0
390 | 2022-10-06 06:31 | 15.2 | 21.9 | 0
391 | 2022-10-06 06:32 | 14.9 | 22.2 | 0
392 | 2022-10-06 06:33 | 14.9 | 22.6 | 0
393 | 2022-10-06 06:34 | 15.1 | 22.7 | 0
394 | 2022-10-06 06:35 | 15.1 | 23 | 0
395 | 2022-10-06 06:36 | 15.2 | 22.7 | 0
396 | 2022-10-06 06:37 | 15.1 | 21.6 | 0
397 | 2022-10-06 06:38 | 15 | 21.7 | 0
398 | 2022-10-06 06:39 | 15.1 | 21.8 | 0
399 | 2022-10-06 06:40 | 14.9 | 21.9 | 0
400 | 2022-10-06 06:41 | 15.1 | 21.7 | 0
401 | 2022-10-06 06:42 | 15.1 | 22.4 | 0
402 | 2022-10-06 06:43 | 15.4 | 22.1 | 0
403 | 2022-10-06 06:44 | 15.2 | 22.7 | 0
404 | 2022-10-06 06:45 | 15.2 | 22.4 | 0
405 | 2022-10-06 06:46 | 15.2 | 22 | 0
406 | 2022-10-06 06:47 | 15.1 | 23 | 0
407 | 2022-10-06 06:48 | 15.1 | 22.7 | 0
408 | 2022-10-06 06:49 | 15.2 | 22.1 | 0
409 | 2022-10-06 06:50 | 15.1 | 22.2 | 0
410 | 2022-10-06 06:51 | 15 | 22.1 | 0
411 | 2022-10-06 06:52 | 15.3 | 22 | 0
412 | 2022-10-06 06:53 | 15.3 | 22.5 | 0
413 | 2022-10-06 06:54 | 15.2 | 22.2 | 0
414 | 2022-10-06 06:55 | 15.1 | 22.2 | 0
415 | 2022-10-06 06:56 | 15.1 | 22.1 | 0
416 | 2022-10-06 06:57 | 15 | 22.2 | 0
417 | 2022-10-06 06:58 | 14.9 | 22.1 | 0
418 | 2022-10-06 06:59 | 15 | 21.9 | 0
419 | 2022-10-06 07:00 | 14.8 | 21.6 | 0
420 | 2022-10-06 07:01 | 14.9 | 21.8 | 0
421 | 2022-10-06 07:02 | 15 | 21.5 | 0
422 | 2022-10-06 07:03 | 15 | 20.9 | 0
423 | 2022-10-06 07:04 | 15.1 | 20.8 | 0
424 | 2022-10-06 07:05 | 15.3 | 20.4 | 0
425 | 2022-10-06 07:06 | 15.6 | 20.4 | 0
426 | 2022-10-06 07:07 | 15.3 | 20 | 0
427 | 2022-10-06 07:08 | 15.4 | 19.8 | 0
428 | 2022-10-06 07:09 | 15.4 | 20.1 | 0
429 | 2022-10-06 07:10 | 15.2 | 20 | 0
430 | 2022-10-06 07:11 | 15.2 | 19.6 | 0
431 | 2022-10-06 07:12 | 15.3 | 19.6 | 0
432 | 2022-10-06 07:13 | 15.2 | 19.9 | 0
433 | 2022-10-06 07:14 | 15.4 | 20 | 0
434 | 2022-10-06 07:15 | 15.5 | 19.8 | 0
435 | 2022-10-06 07:16 | 15.4 | 19.6 | 0
436 | 2022-10-06 07:17 | 15.6 | 20 | 0
437 | 2022-10-06 07:18 | 15.4 | 20.1 | 0
438 | 2022-10-06 07:19 | 15.5 | 18.9 | 0
439 | 2022-10-06 07:20 | 15.4 | 19.9 | 0
440 | 2022-10-06 07:21 | 15.2 | 19.7 | 0
441 | 2022-10-06 07:22 | 15.3 | 19.6 | 0
442 | 2022-10-06 07:23 | 15.1 | 19.4 | 1
443 | 2022-10-06 07:24 | 15.4 | 19.6 | 1
444 | 2022-10-06 07:25 | 15.4 | 19.3 | 1
445 | 2022-10-06 07:26 | 15.3 | 19.6 | 2
446 | 2022-10-06 07:27 | 15.4 | 19.5 | 2
447 | 2022-10-06 07:28 | 15.4 | 19.7 | 2
448 | 2022-10-06 07:29 | 15.4 | 19.4 | 3
449 | 2022-10-06 07:30 | 15.4 | 20.2 | 3
450 | 2022-10-06 07:31 | 15.4 | 18.4 | 4
451 | 2022-10-06 07:32 | 15.7 | 19.1 | 5
452 | 2022-10-06 07:33 | 15.7 | 19.5 | 5
453 | 2022-10-06 07:34 | 15.5 | 19.6 | 6
454 | 2022-10-06 07:35 | 15.6 | 19.9 | 6
455 | 2022-10-06 07:36 | 15.4 | 19.2 | 7
456 | 2022-10-06 07:37 | 15.5 | 19.3 | 7
457 | 2022-10-06 07:38 | 15.4 | 18.6 | 8
458 | 2022-10-06 07:39 | 15.5 | 19.1 | 8
459 | 2022-10-06 07:40 | 15.4 | 18.8 | 9
460 | 2022-10-06 07:41 | 15.4 | 19.2 | 9
461 | 2022-10-06 07:42 | 15.5 | 19.1 | 10
462 | 2022-10-06 07:43 | 15.4 | 19.2 | 11
463 | 2022-10-06 07:44 | 15.3 | 19.4 | 11
464 | 2022-10-06 07:45 | 15.2 | 19.4 | 11
465 | 2022-10-06 07:46 | 15.4 | 19.3 | 12
466 | 2022-10-06 07:47 | 15.4 | 18.4 | 13
467 | 2022-10-06 07:48 | 15.4 | 18.7 | 13
468 | 2022-10-06 07:49 | 15.6 | 18.9 | 14
469 | 2022-10-06 07:50 | 15.4 | 19.2 | 14
470 | 2022-10-06 07:51 | 15.4 | 18.8 | 15
471 | 2022-10-06 07:52 | 15.3 | 18.6 | 15
472 | 2022-10-06 07:53 | 15.4 | 19.4 | 16
473 | 2022-10-06 07:54 | 15.5 | 19.5 | 17
474 | 2022-10-06 07:55 | 15.4 | 19.3 | 17
475 | 2022-10-06 07:56 | 15.5 | 19.4 | 18
476 | 2022-10-06 07:57 | 15.4 | 18.9 | 18
477 | 2022-10-06 07:58 | 15.3 | 20 | 18
478 | 2022-10-06 07:59 | 15.3 | 20.3 | 19
479 | 2022-10-06 08:00 | 15.3 | 20.1 | 19
480 | 2022-10-06 08:01 | 15.2 | 19.6 | 20
481 | 2022-10-06 08:02 | 15.2 | 19.1 | 20
482 | 2022-10-06 08:03 | 15.3 | 19.4 | 21
483 | 2022-10-06 08:04 | 15.5 | 19.3 | 21
484 | 2022-10-06 08:05 | 15.4 | 19.5 | 22
485 | 2022-10-06 08:06 | 15.3 | 19.6 | 23
486 | 2022-10-06 08:07 | 15.4 | 18.9 | 22
487 | 2022-10-06 08:08 | 15.4 | 19.6 | 23
488 | 2022-10-06 08:09 | 15.3 | 19.1 | 23
489 | 2022-10-06 08:10 | 15.2 | 19.9 | 23
490 | 2022-10-06 08:11 | 15.3 | 20.2 | 24
491 | 2022-10-06 08:12 | 15.5 | 20 | 24
492 | 2022-10-06 08:13 | 15.4 | 20.6 | 24
493 | 2022-10-06 08:14 | 15.3 | 20.1 | 25
494 | 2022-10-06 08:15 | 15.4 | 20.6 | 26
495 | 2022-10-06 08:16 | 15.3 | 20.7 | 26
496 | 2022-10-06 08:17 | 15.3 | 21 | 27
497 | 2022-10-06 08:18 | 15.2 | 20.7 | 26
498 | 2022-10-06 08:19 | 15.3 | 21.1 | 26
499 | 2022-10-06 08:20 | 15 | 20.6 | 27
500 | 2022-10-06 08:21 | 15.2 | 21.5 | 27
501 | 2022-10-06 08:22 | 15.4 | 21.5 | 28
502 | 2022-10-06 08:23 | 15.5 | 20.3 | 28
503 | 2022-10-06 08:24 | 15.3 | 20.5 | 29
504 | 2022-10-06 08:25 | 15.2 | 21 | 30
505 | 2022-10-06 08:26 | 15.2 | 21.3 | 30
506 | 2022-10-06 08:27 | 15.3 | 20.4 | 31
507 | 2022-10-06 08:28 | 15.2 | 21.1 | 31
508 | 2022-10-06 08:29 | 15.1 | 21.5 | 32
509 | 2022-10-06 08:30 | 15.2 | 21.7 | 33
510 | 2022-10-06 08:31 | 15.6 | 21.5 | 35
511 | 2022-10-06 08:32 | 15.7 | 21.3 | 35
512 | 2022-10-06 08:33 | 15.7 | 21.8 | 34
513 | 2022-10-06 08:34 | 15.9 | 21.9 | 35
514 | 2022-10-06 08:35 | 15.9 | 21.1 | 37
515 | 2022-10-06 08:36 | 16.2 | 21 | 38
516 | 2022-10-06 08:37 | 16.2 | 20.8 | 45
517 | 2022-10-06 08:38 | 16.3 | 21.3 | 65
518 | 2022-10-06 08:39 | 16.2 | 21.1 | 108
519 | 2022-10-06 08:40 | 16.3 | 20.8 | 134
520 | 2022-10-06 08:41 | 16.6 | 21.2 | 190
521 | 2022-10-06 08:42 | 16.6 | 21.1 | 208
522 | 2022-10-06 08:43 | 16.7 | 21.5 | 231
523 | 2022-10-06 08:44 | 16.8 | 20.6 | 240
524 | 2022-10-06 08:45 | 16.8 | 20.3 | 290
525 | 2022-10-06 08:46 | 16.8 | 21.1 | 299
526 | 2022-10-06 08:47 | 16.9 | 20.2 | 300
527 | 2022-10-06 08:48 | 16.8 | 21.4 | 258
528 | 2022-10-06 08:49 | 17 | 20.4 | 314
529 | 2022-10-06 08:50 | 16.8 | 20.7 | 318
530 | 2022-10-06 08:51 | 16.8 | 20.9 | 323
531 | 2022-10-06 08:52 | 16.8 | 21.3 | 326
532 | 2022-10-06 08:53 | 16.8 | 21.8 | 331
533 | 2022-10-06 08:54 | 17 | 21.5 | 338
534 | 2022-10-06 08:55 | 16.9 | 20.7 | 339
535 | 2022-10-06 08:56 | 17 | 21.2 | 343
536 | 2022-10-06 08:57 | 17 | 20.7 | 348
537 | 2022-10-06 08:58 | 17.2 | 21.1 | 356
538 | 2022-10-06 08:59 | 17 | 20.8 | 360
539 | 2022-10-06 09:00 | 17.2 | 21.1 | 361
540 | 2022-10-06 09:01 | 17.1 | 20.8 | 366
541 | 2022-10-06 09:02 | 17.2 | 20.9 | 376
542 | 2022-10-06 09:03 | 17.2 | 21.7 | 380
543 | 2022-10-06 09:04 | 17.4 | 21.9 | 379
544 | 2022-10-06 09:05 | 17.2 | 21.5 | 387
545 | 2022-10-06 09:06 | 17.2 | 20.7 | 388
546 | 2022-10-06 09:07 | 17.4 | 21.4 | 391
547 | 2022-10-06 09:08 | 17.3 | 21.6 | 397
548 | 2022-10-06 09:09 | 17.4 | 22 | 401
549 | 2022-10-06 09:10 | 17.3 | 21.1 | 412
550 | 2022-10-06 09:11 | 17.4 | 20.8 | 409
551 | 2022-10-06 09:12 | 17.4 | 21.1 | 419
552 | 2022-10-06 09:13 | 17.3 | 21 | 421
553 | 2022-10-06 09:14 | 17.4 | 21.5 | 427
554 | 2022-10-06 09:15 | 17.5 | 21 | 435
555 | 2022-10-06 09:16 | 17.4 | 21.4 | 428
556 | 2022-10-06 09:17 | 17.5 | 20.3 | 441
557 | 2022-10-06 09:18 | 17.7 | 20.7 | 446
558 | 2022-10-06 09:19 | 17.7 | 21.5 | 454
559 | 2022-10-06 09:20 | 17.9 | 21.7 | 457
560 | 2022-10-06 09:21 | 17.7 | 20.9 | 461
561 | 2022-10-06 09:22 | 17.6 | 20.4 | 463
562 | 2022-10-06 09:23 | 17.6 | 21.2 | 469
563 | 2022-10-06 09:24 | 17.7 | 21.3 | 473
564 | 2022-10-06 09:25 | 17.8 | 21.3 | 478
565 | 2022-10-06 09:26 | 17.9 | 21 | 482
566 | 2022-10-06 09:27 | 18 | 21 | 484
567 | 2022-10-06 09:28 | 18.2 | 21.2 | 95
568 | 2022-10-06 09:29 | 18.1 | 21.4 | 487
569 | 2022-10-06 09:30 | 17.9 | 21.2 | 499
570 | 2022-10-06 09:31 | 18.2 | 21.1 | 503
571 | 2022-10-06 09:32 | 18.4 | 21 | 505
572 | 2022-10-06 09:33 | 18.4 | 21.3 | 513
573 | 2022-10-06 09:34 | 18.3 | 20.5 | 44
574 | 2022-10-06 09:35 | 17.9 | 21.3 | 525
575 | 2022-10-06 09:36 | 17.9 | 21.2 | 525
576 | 2022-10-06 09:37 | 18.1 | 21.3 | 529
577 | 2022-10-06 09:38 | 18.3 | 21.5 | 534
578 | 2022-10-06 09:39 | 18.4 | 20.7 | 534
579 | 2022-10-06 09:40 | 18.5 | 21.3 | 543
580 | 2022-10-06 09:41 | 18.5 | 21.8 | 553
581 | 2022-10-06 09:42 | 18.6 | 21.3 | 549
582 | 2022-10-06 09:43 | 18.7 | 21.4 | 552
583 | 2022-10-06 09:44 | 18.8 | 21.1 | 560
584 | 2022-10-06 09:45 | 18.8 | 20.1 | 564
585 | 2022-10-06 09:46 | 18.9 | 20.2 | 565
586 | 2022-10-06 09:47 | 18.9 | 19.4 | 565
587 | 2022-10-06 09:48 | 19.2 | 19.8 | 568
588 | 2022-10-06 09:49 | 19 | 19.8 | 575
589 | 2022-10-06 09:50 | 19.2 | 19.4 | 582
590 | 2022-10-06 09:51 | 19.3 | 19.8 | 586
591 | 2022-10-06 09:52 | 19.3 | 20 | 590
592 | 2022-10-06 09:53 | 19.6 | 19.8 | 592
593 | 2022-10-06 09:54 | 19.8 | 20 | 594
594 | 2022-10-06 09:55 | 19.8 | 20.2 | 600
595 | 2022-10-06 09:56 | 19.5 | 20.5 | 607
596 | 2022-10-06 09:57 | 19.8 | 20.4 | 608
597 | 2022-10-06 09:58 | 19.7 | 20.4 | 612
598 | 2022-10-06 09:59 | 19.2 | 19.9 | 617
599 | 2022-10-06 10:00 | 19 | 20.4 | 625
600 | 2022-10-06 10:01 | 19.3 | 20 | 625
601 | 2022-10-06 10:02 | 19.5 | 20.1 | 637
602 | 2022-10-06 10:03 | 19.9 | 19.9 | 632
603 | 2022-10-06 10:04 | 19.9 | 20 | 639
604 | 2022-10-06 10:05 | 19.7 | 20.2 | 640
605 | 2022-10-06 10:06 | 19.6 | 20 | 642
606 | 2022-10-06 10:07 | 19.3 | 20 | 652
607 | 2022-10-06 10:08 | 19.3 | 19.6 | 649
608 | 2022-10-06 10:09 | 19.4 | 19.9 | 654
609 | 2022-10-06 10:10 | 19.6 | 19.7 | 660
610 | 2022-10-06 10:11 | 19.6 | 18.7 | 664
611 | 2022-10-06 10:12 | 19.9 | 19.4 | 672
612 | 2022-10-06 10:13 | 19.9 | 19.4 | 673
613 | 2022-10-06 10:14 | 19.8 | 19.7 | 676
614 | 2022-10-06 10:15 | 19.4 | 19.9 | 684
615 | 2022-10-06 10:16 | 19.7 | 19.6 | 688
616 | 2022-10-06 10:17 | 19.6 | 20 | 693
617 | 2022-10-06 10:18 | 19.8 | 20 | 695
618 | 2022-10-06 10:19 | 20.1 | 20.1 | 698
619 | 2022-10-06 10:20 | 20.3 | 20 | 701
620 | 2022-10-06 10:21 | 20.3 | 20 | 706
621 | 2022-10-06 10:22 | 20.3 | 19.8 | 712
622 | 2022-10-06 10:23 | 20 | 19.8 | 708
623 | 2022-10-06 10:24 | 19.8 | 20 | 718
624 | 2022-10-06 10:25 | 20 | 19.6 | 723
625 | 2022-10-06 10:26 | 20.1 | 19.7 | 722
626 | 2022-10-06 10:27 | 20.3 | 20 | 727
627 | 2022-10-06 10:28 | 20.1 | 19.9 | 732
628 | 2022-10-06 10:29 | 20.1 | 19.9 | 735
629 | 2022-10-06 10:30 | 20.3 | 19.9 | 741
630 | 2022-10-06 10:31 | 20.2 | 20 | 744
631 | 2022-10-06 10:32 | 20.2 | 19.6 | 750
632 | 2022-10-06 10:33 | 20.4 | 20.1 | 756
633 | 2022-10-06 10:34 | 20.4 | 20.1 | 752
634 | 2022-10-06 10:35 | 20.1 | 19.7 | 757
635 | 2022-10-06 10:36 | 19.7 | 20.1 | 761
636 | 2022-10-06 10:37 | 20 | 20.1 | 767
637 | 2022-10-06 10:38 | 19.8 | 19.9 | 767
638 | 2022-10-06 10:39 | 19.6 | 19.5 | 770
639 | 2022-10-06 10:40 | 20 | 19.7 | 777
640 | 2022-10-06 10:41 | 19.8 | 19.7 | 782
641 | 2022-10-06 10:42 | 20.2 | 19.7 | 781
642 | 2022-10-06 10:43 | 19.9 | 19.7 | 779
643 | 2022-10-06 10:44 | 20 | 19.8 | 786
644 | 2022-10-06 10:45 | 20.2 | 20 | 786
645 | 2022-10-06 10:46 | 20.3 | 19.8 | 786
646 | 2022-10-06 10:47 | 20.3 | 20.1 | 798
647 | 2022-10-06 10:48 | 20.6 | 20.5 | 795
648 | 2022-10-06 10:49 | 20.4 | 19.5 | 796
649 | 2022-10-06 10:50 | 20.1 | 19.4 | 801
650 | 2022-10-06 10:51 | 20.3 | 19.5 | 807
651 | 2022-10-06 10:52 | 20.6 | 20.2 | 810
652 | 2022-10-06 10:53 | 20.3 | 19.7 | 813
653 | 2022-10-06 10:54 | 20.3 | 20.1 | 825
654 | 2022-10-06 10:55 | 19.9 | 19.7 | 826
655 | 2022-10-06 10:56 | 20.3 | 19.8 | 828
656 | 2022-10-06 10:57 | 20.3 | 19.7 | 845
657 | 2022-10-06 10:58 | 20 | 19.8 | 842
658 | 2022-10-06 10:59 | 20.1 | 19.2 | 856
659 | 2022-10-06 11:00 | 20.4 | 20 | 146
660 | 2022-10-06 11:01 | 19.8 | 20.2 | 460
661 | 2022-10-06 11:02 | 19.6 | 19.8 | 880
662 | 2022-10-06 11:03 | 19.6 | 19.7 | 876
663 | 2022-10-06 11:04 | 20.3 | 19.9 | 876
664 | 2022-10-06 11:05 | 20.1 | 19.9 | 863
665 | 2022-10-06 11:06 | 20.1 | 20.2 | 875
666 | 2022-10-06 11:07 | 20.3 | 20.1 | 881
667 | 2022-10-06 11:08 | 20.8 | 20.4 | 646
668 | 2022-10-06 11:09 | 20.9 | 20.5 | 899
669 | 2022-10-06 11:10 | 20.7 | 20.8 | 930
670 | 2022-10-06 11:11 | 20.9 | 21.1 | 929
671 | 2022-10-06 11:12 | 21.4 | 21.6 | 933
672 | 2022-10-06 11:13 | 21.4 | 21.7 | 234
673 | 2022-10-06 11:14 | 20.5 | 21.4 | 963
674 | 2022-10-06 11:15 | 20.2 | 21.2 | 987
675 | 2022-10-06 11:16 | 20.4 | 20.7 | 243
676 | 2022-10-06 11:17 | 20 | 20.9 | 397
677 | 2022-10-06 11:18 | 19.9 | 20.3 | 226
678 | 2022-10-06 11:19 | 20.2 | 21.6 | 1075
679 | 2022-10-06 11:20 | 20.5 | 22.4 | 745
680 | 2022-10-06 11:21 | 20.6 | 22 | 315
681 | 2022-10-06 11:22 | 20.5 | 21.7 | 985
682 | 2022-10-06 11:23 | 20.7 | 21.4 | 951
683 | 2022-10-06 11:24 | 20.8 | 21.6 | 843
684 | 2022-10-06 11:25 | 20.7 | 21.2 | 0
685 | 2022-10-06 11:26 | 20.4 | 21.9 | 271
686 | 2022-10-06 11:27 | 20.8 | 21.4 | 1014
687 | 2022-10-06 11:28 | 20.7 | 21.8 | 410
688 | 2022-10-06 11:29 | 20.4 | 21.6 | 202
689 | 2022-10-06 11:30 | 19.8 | 22 | 169
690 | 2022-10-06 11:31 | 19.6 | 21 | 163
691 | 2022-10-06 11:32 | 19.3 | 21.8 | 165
692 | 2022-10-06 11:33 | 19 | 21.9 | 162
693 | 2022-10-06 11:34 | 19.2 | 21.2 | 1010
694 | 2022-10-06 11:35 | 19.4 | 22.4 | 326
695 | 2022-10-06 11:36 | 19.5 | 21.6 | 174
696 | 2022-10-06 11:37 | 19.5 | 21.4 | 240
697 | 2022-10-06 11:38 | 19.5 | 22.4 | 1034
698 | 2022-10-06 11:39 | 19.9 | 21.8 | 902
699 | 2022-10-06 11:40 | 20 | 22 | 455
700 | 2022-10-06 11:41 | 20.3 | 22 | 980
701 | 2022-10-06 11:42 | 20.7 | 21.3 | 979
702 | 2022-10-06 11:43 | 20.7 | 21.8 | 984
703 | 2022-10-06 11:44 | 21 | 21.8 | 1008
704 | 2022-10-06 11:45 | 21.5 | 21.7 | 1013
705 | 2022-10-06 11:46 | 21.4 | 21.8 | 995
706 | 2022-10-06 11:47 | 21.1 | 21 | 978
707 | 2022-10-06 11:48 | 21.1 | 21.6 | 983
708 | 2022-10-06 11:49 | 21.4 | 21.7 | 992
709 | 2022-10-06 11:50 | 21.7 | 22.2 | 1011
710 | 2022-10-06 11:51 | 21.8 | 22.1 | 1034
711 | 2022-10-06 11:52 | 21.9 | 21.9 | 1041
712 | 2022-10-06 11:53 | 21.6 | 22 | 1024
713 | 2022-10-06 11:54 | 22.5 | 22.2 | 1018
714 | 2022-10-06 11:55 | 21.7 | 21.9 | 1020
715 | 2022-10-06 11:56 | 21.8 | 22 | 1020
716 | 2022-10-06 11:57 | 21.8 | 21.3 | 1031
717 | 2022-10-06 11:58 | 22.5 | 21.4 | 1050
718 | 2022-10-06 11:59 | 22.5 | 21.1 | 1082
719 | 2022-10-06 12:00 | 22.3 | 21.3 | 644
720 | 2022-10-06 12:01 | 22.4 | 22 | 455
721 | 2022-10-06 12:02 | 22.6 | 21.9 | 1065
722 | 2022-10-06 12:03 | 21.9 | 22 | 1037
723 | 2022-10-06 12:04 | 21.8 | 21.8 | 1101
724 | 2022-10-06 12:05 | 21.9 | 21.9 | 1108
725 | 2022-10-06 12:06 | 21.7 | 22.1 | 1121
726 | 2022-10-06 12:07 | 21.7 | 22.2 | 1139
727 | 2022-10-06 12:08 | 21.5 | 22.4 | 1132
728 | 2022-10-06 12:09 | 21.4 | 23 | 1102
729 | 2022-10-06 12:10 | 21.4 | 21.6 | 1059
730 | 2022-10-06 12:11 | 21.9 | 21.9 | 1046
731 | 2022-10-06 12:12 | 22.2 | 21.7 | 1034
732 | 2022-10-06 12:13 | 21.8 | 22.5 | 1037
733 | 2022-10-06 12:14 | 21.9 | 22.2 | 1056
734 | 2022-10-06 12:15 | 22.2 | 22.3 | 1075
735 | 2022-10-06 12:16 | 22.5 | 22.4 | 1098
736 | 2022-10-06 12:17 | 22.7 | 22.2 | 1127
737 | 2022-10-06 12:18 | 22.7 | 22.8 | 1162
738 | 2022-10-06 12:19 | 22.8 | 21.9 | 1183
739 | 2022-10-06 12:20 | 22.7 | 22.1 | 1237
740 | 2022-10-06 12:21 | 22.4 | 22.1 | 299
741 | 2022-10-06 12:22 | 21.7 | 22.1 | 333
742 | 2022-10-06 12:23 | 21.6 | 22 | 323
743 | 2022-10-06 12:24 | 21.9 | 22.1 | 1219
744 | 2022-10-06 12:25 | 21.6 | 22 | 1234
745 | 2022-10-06 12:26 | 22.2 | 21.9 | 1211
746 | 2022-10-06 12:27 | 22.1 | 22 | 313
747 | 2022-10-06 12:28 | 21.9 | 22.1 | 1156
748 | 2022-10-06 12:29 | 21.9 | 22 | 1131
749 | 2022-10-06 12:30 | 21.9 | 22.1 | 1120
750 | 2022-10-06 12:31 | 22.3 | 22.1 | 1115
751 | 2022-10-06 12:32 | 22.8 | 22.6 | 1133
752 | 2022-10-06 12:33 | 22.9 | 22 | 1162
753 | 2022-10-06 12:34 | 22.8 | 22.1 | 1199
754 | 2022-10-06 12:35 | 22.7 | 22.6 | 1182
755 | 2022-10-06 12:36 | 22.7 | 22.1 | 330
756 | 2022-10-06 12:37 | 22.1 | 22.1 | 1197
757 | 2022-10-06 12:38 | 22.1 | 22.1 | 1142
758 | 2022-10-06 12:39 | 22.7 | 22.3 | 1151
759 | 2022-10-06 12:40 | 22.3 | 22.2 | 1152
760 | 2022-10-06 12:41 | 22.3 | 22.2 | 1135
761 | 2022-10-06 12:42 | 21.9 | 22.2 | 1144
762 | 2022-10-06 12:43 | 22.1 | 22 | 1178
763 | 2022-10-06 12:44 | 22.3 | 22.1 | 303
764 | 2022-10-06 12:45 | 22.4 | 22.2 | 1184
765 | 2022-10-06 12:46 | 22.2 | 22.3 | 350
766 | 2022-10-06 12:47 | 22 | 22.9 | 1173
767 | 2022-10-06 12:48 | 21.9 | 21.7 | 408
768 | 2022-10-06 12:49 | 21.6 | 22.5 | 310
769 | 2022-10-06 12:50 | 22.5 | 21.8 | 1148
770 | 2022-10-06 12:51 | 22.5 | 22.2 | 1131
771 | 2022-10-06 12:52 | 22.1 | 22.6 | 1143
772 | 2022-10-06 12:53 | 22.5 | 21.9 | 1150
773 | 2022-10-06 12:54 | 22.1 | 21.8 | 233
774 | 2022-10-06 12:55 | 22 | 22.1 | 272
775 | 2022-10-06 12:56 | 22.2 | 22.1 | 1211
776 | 2022-10-06 12:57 | 22.4 | 23.1 | 272
777 | 2022-10-06 12:58 | 22.3 | 22.5 | 363
778 | 2022-10-06 12:59 | 22.4 | 22.5 | 315
779 | 2022-10-06 13:00 | 22.1 | 22.5 | 292
780 | 2022-10-06 13:01 | 21.9 | 22.2 | 376
781 | 2022-10-06 13:02 | 21.8 | 22.6 | 1231
782 | 2022-10-06 13:03 | 22.4 | 23 | 1194
783 | 2022-10-06 13:04 | 22.5 | 23 | 1171
784 | 2022-10-06 13:05 | 22.9 | 22.3 | 1140
785 | 2022-10-06 13:06 | 22.3 | 23.2 | 997
786 | 2022-10-06 13:07 | 22.3 | 23.2 | 1063
787 | 2022-10-06 13:08 | 22 | 22.8 | 1087
788 | 2022-10-06 13:09 | 22.6 | 22.2 | 1202
789 | 2022-10-06 13:10 | 22.8 | 22.5 | 1206
790 | 2022-10-06 13:11 | 22.9 | 23 | 1196
791 | 2022-10-06 13:12 | 23 | 22.6 | 371
792 | 2022-10-06 13:13 | 22.6 | 22 | 389
793 | 2022-10-06 13:14 | 22.4 | 22.7 | 1292
794 | 2022-10-06 13:15 | 22.3 | 22.6 | 1110
795 | 2022-10-06 13:16 | 22.3 | 22.4 | 301
796 | 2022-10-06 13:17 | 21.5 | 22.5 | 272
797 | 2022-10-06 13:18 | 21.2 | 22.3 | 275
798 | 2022-10-06 13:19 | 21.5 | 22.9 | 869
799 | 2022-10-06 13:20 | 21.9 | 22.5 | 933
800 | 2022-10-06 13:21 | 22.3 | 22.8 | 1064
801 | 2022-10-06 13:22 | 22.4 | 23 | 1136
802 | 2022-10-06 13:23 | 22.5 | 22.5 | 1209
803 | 2022-10-06 13:24 | 21.9 | 23 | 1163
804 | 2022-10-06 13:25 | 22.3 | 23 | 1187
805 | 2022-10-06 13:26 | 23 | 22.2 | 1196
806 | 2022-10-06 13:27 | 22.2 | 22.6 | 1223
807 | 2022-10-06 13:28 | 22.7 | 22.4 | 361
808 | 2022-10-06 13:29 | 22.5 | 22.7 | 334
809 | 2022-10-06 13:30 | 22.1 | 22.6 | 578
810 | 2022-10-06 13:31 | 22.2 | 22.7 | 355
811 | 2022-10-06 13:32 | 22 | 23.2 | 1277
812 | 2022-10-06 13:33 | 22.2 | 21.9 | 464
813 | 2022-10-06 13:34 | 22.3 | 21.7 | 1214
814 | 2022-10-06 13:35 | 22.2 | 22.2 | 1061
815 | 2022-10-06 13:36 | 22.4 | 21.6 | 911
816 | 2022-10-06 13:37 | 22.3 | 21.8 | 790
817 | 2022-10-06 13:38 | 22 | 21.7 | 821
818 | 2022-10-06 13:39 | 21.6 | 22.6 | 871
819 | 2022-10-06 13:40 | 21.8 | 22.2 | 784
820 | 2022-10-06 13:41 | 21.5 | 21.9 | 587
821 | 2022-10-06 13:42 | 21.3 | 22.5 | 271
822 | 2022-10-06 13:43 | 21.4 | 22.4 | 304
823 | 2022-10-06 13:44 | 21.6 | 22.5 | 350
824 | 2022-10-06 13:45 | 22.1 | 22.3 | 1228
825 | 2022-10-06 13:46 | 22.9 | 22 | 1229
826 | 2022-10-06 13:47 | 22.2 | 22.1 | 803
827 | 2022-10-06 13:48 | 21.4 | 23.1 | 473
828 | 2022-10-06 13:49 | 21.8 | 22.4 | 907
829 | 2022-10-06 13:50 | 22 | 22.1 | 800
830 | 2022-10-06 13:51 | 21.8 | 22.4 | 330
831 | 2022-10-06 13:52 | 21.4 | 22.5 | 339
832 | 2022-10-06 13:53 | 21.8 | 22.6 | 780
833 | 2022-10-06 13:54 | 21.9 | 22.8 | 866
834 | 2022-10-06 13:55 | 21.9 | 22.6 | 351
835 | 2022-10-06 13:56 | 22 | 22.4 | 1014
836 | 2022-10-06 13:57 | 22.4 | 22.4 | 1075
837 | 2022-10-06 13:58 | 22.3 | 22.5 | 712
838 | 2022-10-06 13:59 | 22.4 | 22.8 | 1138
839 | 2022-10-06 14:00 | 22.2 | 22.4 | 1070
840 | 2022-10-06 14:01 | 22 | 23.7 | 831
841 | 2022-10-06 14:02 | 22.6 | 22.8 | 1150
842 | 2022-10-06 14:03 | 22.5 | 22.5 | 369
843 | 2022-10-06 14:04 | 21.8 | 22.7 | 377
844 | 2022-10-06 14:05 | 22 | 22.7 | 1111
845 | 2022-10-06 14:06 | 22.4 | 22.5 | 896
846 | 2022-10-06 14:07 | 22.4 | 22.7 | 1199
847 | 2022-10-06 14:08 | 21.9 | 22.1 | 486
848 | 2022-10-06 14:09 | 21.9 | 23.1 | 1120
849 | 2022-10-06 14:10 | 22.1 | 21.9 | 1121
850 | 2022-10-06 14:11 | 21.9 | 22.8 | 1039
851 | 2022-10-06 14:12 | 22.1 | 23.7 | 604
852 | 2022-10-06 14:13 | 22 | 22.4 | 498
853 | 2022-10-06 14:14 | 21.7 | 22.7 | 564
854 | 2022-10-06 14:15 | 21.7 | 22.8 | 592
855 | 2022-10-06 14:16 | 22.2 | 22.3 | 755
856 | 2022-10-06 14:17 | 22.2 | 21.8 | 797
857 | 2022-10-06 14:18 | 21.9 | 22.5 | 830
858 | 2022-10-06 14:19 | 21.6 | 22.8 | 806
859 | 2022-10-06 14:20 | 21.6 | 22.8 | 583
860 | 2022-10-06 14:21 | 22.1 | 22 | 1026
861 | 2022-10-06 14:22 | 22.3 | 22.6 | 1079
862 | 2022-10-06 14:23 | 22.5 | 22.5 | 1083
863 | 2022-10-06 14:24 | 22.6 | 22.7 | 436
864 | 2022-10-06 14:25 | 22 | 22.6 | 1065
865 | 2022-10-06 14:26 | 22.3 | 23 | 860
866 | 2022-10-06 14:27 | 22.1 | 23.6 | 780
867 | 2022-10-06 14:28 | 21.9 | 23.3 | 316
868 | 2022-10-06 14:29 | 21.6 | 23 | 392
869 | 2022-10-06 14:30 | 21.7 | 22.9 | 436
870 | 2022-10-06 14:31 | 22.2 | 23 | 919
871 | 2022-10-06 14:32 | 22.4 | 22.6 | 1116
872 | 2022-10-06 14:33 | 22.1 | 22.7 | 1092
873 | 2022-10-06 14:34 | 22.3 | 23.2 | 1149
874 | 2022-10-06 14:35 | 22.3 | 22.8 | 1156
875 | 2022-10-06 14:36 | 22.7 | 22.8 | 1136
876 | 2022-10-06 14:37 | 22.5 | 22.9 | 1160
877 | 2022-10-06 14:38 | 22.5 | 22.7 | 1176
878 | 2022-10-06 14:39 | 22.3 | 23.4 | 1158
879 | 2022-10-06 14:40 | 22.4 | 22.8 | 1055
880 | 2022-10-06 14:41 | 22.7 | 23.3 | 1011
881 | 2022-10-06 14:42 | 23.3 | 24 | 1087
882 | 2022-10-06 14:43 | 23.7 | 23.1 | 952
883 | 2022-10-06 14:44 | 23.1 | 23.6 | 321
884 | 2022-10-06 14:45 | 22.9 | 23.8 | 1040
885 | 2022-10-06 14:46 | 23 | 23.5 | 509
886 | 2022-10-06 14:47 | 22.4 | 23.6 | 1024
887 | 2022-10-06 14:48 | 22.3 | 23.4 | 546
888 | 2022-10-06 14:49 | 22.4 | 22.8 | 854
889 | 2022-10-06 14:50 | 22.2 | 22.9 | 755
890 | 2022-10-06 14:51 | 22.3 | 23.2 | 1063
891 | 2022-10-06 14:52 | 22.8 | 23.3 | 1115
892 | 2022-10-06 14:53 | 23.1 | 22.9 | 999
893 | 2022-10-06 14:54 | 22.7 | 22.7 | 957
894 | 2022-10-06 14:55 | 22.8 | 22.9 | 968
895 | 2022-10-06 14:56 | 22.8 | 22.9 | 1171
896 | 2022-10-06 14:57 | 22.7 | 23.1 | 990
897 | 2022-10-06 14:58 | 23.2 | 23.1 | 1031
898 | 2022-10-06 14:59 | 23 | 23.2 | 1020
899 | 2022-10-06 15:00 | 23 | 23.1 | 1050
900 | 2022-10-06 15:01 | 23 | 23.3 | 1098
901 | 2022-10-06 15:02 | 22.6 | 23.2 | 616
902 | 2022-10-06 15:03 | 22.8 | 22.1 | 731
903 | 2022-10-06 15:04 | 22.3 | 23.1 | 582
904 | 2022-10-06 15:05 | 22.2 | 22.7 | 750
905 | 2022-10-06 15:06 | 21.9 | 23.4 | 882
906 | 2022-10-06 15:07 | 21.5 | 23.3 | 268
907 | 2022-10-06 15:08 | 21.6 | 22.7 | 730
908 | 2022-10-06 15:09 | 21.3 | 23.6 | 291
909 | 2022-10-06 15:10 | 21.3 | 23.7 | 575
910 | 2022-10-06 15:11 | 21.4 | 23.8 | 668
911 | 2022-10-06 15:12 | 21.5 | 23.7 | 815
912 | 2022-10-06 15:13 | 21.4 | 22.8 | 829
913 | 2022-10-06 15:14 | 21.3 | 22.5 | 210
914 | 2022-10-06 15:15 | 21.2 | 23.1 | 235
915 | 2022-10-06 15:16 | 21.1 | 22.6 | 272
916 | 2022-10-06 15:17 | 21 | 22.9 | 378
917 | 2022-10-06 15:18 | 21.2 | 23.2 | 292
918 | 2022-10-06 15:19 | 21.7 | 22.6 | 780
919 | 2022-10-06 15:20 | 21.5 | 23.7 | 309
920 | 2022-10-06 15:21 | 21.5 | 23.5 | 223
921 | 2022-10-06 15:22 | 21.7 | 24 | 197
922 | 2022-10-06 15:23 | 21.4 | 22.8 | 184
923 | 2022-10-06 15:24 | 21 | 22.9 | 193
924 | 2022-10-06 15:25 | 21.3 | 22.5 | 461
925 | 2022-10-06 15:26 | 21.6 | 23 | 936
926 | 2022-10-06 15:27 | 21.7 | 22.8 | 562
927 | 2022-10-06 15:28 | 21.4 | 23.8 | 277
928 | 2022-10-06 15:29 | 21.3 | 23 | 303
929 | 2022-10-06 15:30 | 20.9 | 23.9 | 254
930 | 2022-10-06 15:31 | 20.9 | 22.9 | 266
931 | 2022-10-06 15:32 | 20.7 | 23.4 | 238
932 | 2022-10-06 15:33 | 20.7 | 23.1 | 218
933 | 2022-10-06 15:34 | 20.4 | 24 | 241
934 | 2022-10-06 15:35 | 20.4 | 23 | 263
935 | 2022-10-06 15:36 | 20.4 | 22.9 | 332
936 | 2022-10-06 15:37 | 20.3 | 23.7 | 253
937 | 2022-10-06 15:38 | 20.5 | 23.4 | 221
938 | 2022-10-06 15:39 | 20.6 | 22.7 | 213
939 | 2022-10-06 15:40 | 20.7 | 23.8 | 206
940 | 2022-10-06 15:41 | 20.8 | 23.9 | 168
941 | 2022-10-06 15:42 | 20.7 | 22.7 | 209
942 | 2022-10-06 15:43 | 20.8 | 23.5 | 201
943 | 2022-10-06 15:44 | 20.6 | 22.7 | 208
944 | 2022-10-06 15:45 | 20.6 | 23.3 | 187
945 | 2022-10-06 15:46 | 20.5 | 22.2 | 189
946 | 2022-10-06 15:47 | 20.5 | 23.3 | 210
947 | 2022-10-06 15:48 | 20.6 | 23.2 | 231
948 | 2022-10-06 15:49 | 20.6 | 22.1 | 208
949 | 2022-10-06 15:50 | 20.3 | 22.1 | 257
950 | 2022-10-06 15:51 | 20.3 | 22.6 | 265
951 | 2022-10-06 15:52 | 20.3 | 23 | 329
952 | 2022-10-06 15:53 | 20.5 | 22.2 | 242
953 | 2022-10-06 15:54 | 20.4 | 22.3 | 194
954 | 2022-10-06 15:55 | 20.3 | 23.1 | 192
955 | 2022-10-06 15:56 | 20.3 | 24 | 161
956 | 2022-10-06 15:57 | 20.2 | 23.2 | 160
957 | 2022-10-06 15:58 | 20.2 | 23.6 | 169
958 | 2022-10-06 15:59 | 20.2 | 23.8 | 184
959 | 2022-10-06 16:00 | 20.2 | 22.8 | 190
960 | 2022-10-06 16:01 | 20.2 | 23.2 | 157
961 | 2022-10-06 16:02 | 20.3 | 23.2 | 144
962 | 2022-10-06 16:03 | 20.3 | 23 | 171
963 | 2022-10-06 16:04 | 20.3 | 23.3 | 274
964 | 2022-10-06 16:05 | 20.4 | 23 | 646
965 | 2022-10-06 16:06 | 20.5 | 22.9 | 187
966 | 2022-10-06 16:07 | 20.5 | 23.3 | 169
967 | 2022-10-06 16:08 | 20.3 | 23.9 | 164
968 | 2022-10-06 16:09 | 20.4 | 24.1 | 342
969 | 2022-10-06 16:10 | 20.5 | 23.8 | 694
970 | 2022-10-06 16:11 | 20.5 | 22.8 | 310
971 | 2022-10-06 16:12 | 20.3 | 22.9 | 184
972 | 2022-10-06 16:13 | 20.3 | 23.6 | 189
973 | 2022-10-06 16:14 | 20.4 | 22.4 | 251
974 | 2022-10-06 16:15 | 20.3 | 22.8 | 496
975 | 2022-10-06 16:16 | 20.4 | 23.6 | 167
976 | 2022-10-06 16:17 | 20.3 | 23.2 | 149
977 | 2022-10-06 16:18 | 20.2 | 23.2 | 139
978 | 2022-10-06 16:19 | 20 | 22.7 | 141
979 | 2022-10-06 16:20 | 19.9 | 23.2 | 270
980 | 2022-10-06 16:21 | 20 | 23.9 | 196
981 | 2022-10-06 16:22 | 20.4 | 23.1 | 311
982 | 2022-10-06 16:23 | 20.5 | 23 | 690
983 | 2022-10-06 16:24 | 20.8 | 22.6 | 692
984 | 2022-10-06 16:25 | 20.9 | 22.5 | 732
985 | 2022-10-06 16:26 | 20.6 | 23.2 | 262
986 | 2022-10-06 16:27 | 21.1 | 23.4 | 763
987 | 2022-10-06 16:28 | 21.1 | 22.8 | 198
988 | 2022-10-06 16:29 | 21 | 23.4 | 207
989 | 2022-10-06 16:30 | 20.8 | 22.8 | 300
990 | 2022-10-06 16:31 | 20.6 | 23.2 | 164
991 | 2022-10-06 16:32 | 20.5 | 23.4 | 328
992 | 2022-10-06 16:33 | 20.3 | 23 | 228
993 | 2022-10-06 16:34 | 20.2 | 23.4 | 132
994 | 2022-10-06 16:35 | 20.3 | 23.3 | 111
995 | 2022-10-06 16:36 | 20.1 | 23.1 | 124
996 | 2022-10-06 16:37 | 20.1 | 22.9 | 155
997 | 2022-10-06 16:38 | 20 | 22.3 | 156
998 | 2022-10-06 16:39 | 20.1 | 22 | 199
999 | 2022-10-06 16:40 | 20.4 | 22.9 | 636
1000 | 2022-10-06 16:41 | 20.5 | 23.7 | 572
1001 | 2022-10-06 16:42 | 20.3 | 24 | 289
1002 | 2022-10-06 16:43 | 20.2 | 22.5 | 223
1003 | 2022-10-06 16:44 | 20.5 | 22.8 | 183
1004 | 2022-10-06 16:45 | 20.7 | 23.4 | 487
1005 | 2022-10-06 16:46 | 20.6 | 22.4 | 596
1006 | 2022-10-06 16:47 | 20.8 | 23.1 | 422
1007 | 2022-10-06 16:48 | 20.8 | 23 | 302
1008 | 2022-10-06 16:49 | 20.4 | 23.1 | 307
1009 | 2022-10-06 16:50 | 20.2 | 23 | 347
1010 | 2022-10-06 16:51 | 20.1 | 22.3 | 380
1011 | 2022-10-06 16:52 | 20.1 | 23.2 | 244
1012 | 2022-10-06 16:53 | 20 | 21.9 | 140
1013 | 2022-10-06 16:54 | 19.9 | 22.8 | 121
1014 | 2022-10-06 16:55 | 19.9 | 22.9 | 120
1015 | 2022-10-06 16:56 | 19.6 | 23 | 216
1016 | 2022-10-06 16:57 | 19.8 | 22.7 | 152
1017 | 2022-10-06 16:58 | 19.8 | 23 | 283
1018 | 2022-10-06 16:59 | 19.8 | 23.2 | 278
1019 | 2022-10-06 17:00 | 19.9 | 22.7 | 176
1020 | 2022-10-06 17:01 | 19.8 | 22.8 | 164
1021 | 2022-10-06 17:02 | 19.7 | 22.8 | 166
1022 | 2022-10-06 17:03 | 19.4 | 22.9 | 220
1023 | 2022-10-06 17:04 | 19.7 | 22.7 | 403
1024 | 2022-10-06 17:05 | 19.9 | 23 | 328
1025 | 2022-10-06 17:06 | 19.7 | 22.9 | 176
1026 | 2022-10-06 17:07 | 19.6 | 22.9 | 154
1027 | 2022-10-06 17:08 | 19.6 | 22.7 | 167
1028 | 2022-10-06 17:09 | 19.6 | 23.3 | 117
1029 | 2022-10-06 17:10 | 19.3 | 23 | 117
1030 | 2022-10-06 17:11 | 19.5 | 22.8 | 157
1031 | 2022-10-06 17:12 | 19.7 | 22.6 | 215
1032 | 2022-10-06 17:13 | 19.5 | 22.8 | 164
1033 | 2022-10-06 17:14 | 19.6 | 22.6 | 114
1034 | 2022-10-06 17:15 | 19.6 | 22.7 | 171
1035 | 2022-10-06 17:16 | 19.4 | 22.3 | 118
1036 | 2022-10-06 17:17 | 19.4 | 22 | 127
1037 | 2022-10-06 17:18 | 19.5 | 21.9 | 294
1038 | 2022-10-06 17:19 | 19.6 | 23.1 | 219
1039 | 2022-10-06 17:20 | 19.6 | 22.3 | 437
1040 | 2022-10-06 17:21 | 19.8 | 22.7 | 256
1041 | 2022-10-06 17:22 | 19.5 | 22.8 | 120
1042 | 2022-10-06 17:23 | 19.5 | 22.7 | 212
1043 | 2022-10-06 17:24 | 19.2 | 22.9 | 97
1044 | 2022-10-06 17:25 | 19.3 | 23.3 | 134
1045 | 2022-10-06 17:26 | 19.4 | 23 | 307
1046 | 2022-10-06 17:27 | 20 | 22.5 | 399
1047 | 2022-10-06 17:28 | 20 | 22.7 | 404
1048 | 2022-10-06 17:29 | 19.9 | 23 | 391
1049 | 2022-10-06 17:30 | 20.2 | 22.1 | 363
1050 | 2022-10-06 17:31 | 20.1 | 22.1 | 208
1051 | 2022-10-06 17:32 | 19.8 | 23.1 | 102
1052 | 2022-10-06 17:33 | 19.7 | 23.4 | 81
1053 | 2022-10-06 17:34 | 19.4 | 23.2 | 79
1054 | 2022-10-06 17:35 | 19.1 | 22.6 | 79
1055 | 2022-10-06 17:36 | 19.2 | 22.8 | 80
1056 | 2022-10-06 17:37 | 19 | 22.4 | 150
1057 | 2022-10-06 17:38 | 19.1 | 22.9 | 159
1058 | 2022-10-06 17:39 | 19 | 22.7 | 237
1059 | 2022-10-06 17:40 | 19.1 | 22.7 | 302
1060 | 2022-10-06 17:41 | 19.2 | 22.6 | 309
1061 | 2022-10-06 17:42 | 19.2 | 22.8 | 157
1062 | 2022-10-06 17:43 | 18.9 | 22.8 | 94
1063 | 2022-10-06 17:44 | 19 | 22.9 | 85
1064 | 2022-10-06 17:45 | 18.9 | 22.5 | 126
1065 | 2022-10-06 17:46 | 18.7 | 23 | 79
1066 | 2022-10-06 17:47 | 18.9 | 22.9 | 118
1067 | 2022-10-06 17:48 | 19.1 | 22.6 | 190
1068 | 2022-10-06 17:49 | 19 | 22.8 | 223
1069 | 2022-10-06 17:50 | 18.9 | 23.1 | 219
1070 | 2022-10-06 17:51 | 19 | 23 | 80
1071 | 2022-10-06 17:52 | 18.8 | 22.8 | 105
1072 | 2022-10-06 17:53 | 18.8 | 23.2 | 66
1073 | 2022-10-06 17:54 | 18.6 | 22.8 | 77
1074 | 2022-10-06 17:55 | 18.5 | 23.4 | 109
1075 | 2022-10-06 17:56 | 18.4 | 23.4 | 74
1076 | 2022-10-06 17:57 | 18.5 | 22.9 | 95
1077 | 2022-10-06 17:58 | 18.5 | 22.9 | 133
1078 | 2022-10-06 17:59 | 18.6 | 23.2 | 134
1079 | 2022-10-06 18:00 | 18.5 | 22.8 | 77
1080 | 2022-10-06 18:01 | 18.5 | 22.8 | 67
1081 | 2022-10-06 18:02 | 18.3 | 22.6 | 59
1082 | 2022-10-06 18:03 | 18.2 | 22.8 | 68
1083 | 2022-10-06 18:04 | 18.2 | 22.7 | 73
1084 | 2022-10-06 18:05 | 18.3 | 22.7 | 69
1085 | 2022-10-06 18:06 | 18.2 | 22.5 | 62
1086 | 2022-10-06 18:07 | 18.1 | 22.5 | 54
1087 | 2022-10-06 18:08 | 18.3 | 23.1 | 57
1088 | 2022-10-06 18:09 | 18.2 | 21.8 | 72
1089 | 2022-10-06 18:10 | 18 | 22.5 | 73
1090 | 2022-10-06 18:11 | 18.2 | 22.7 | 96
1091 | 2022-10-06 18:12 | 18.1 | 22.6 | 93
1092 | 2022-10-06 18:13 | 18.3 | 22.5 | 89
1093 | 2022-10-06 18:14 | 18.2 | 22.4 | 61
1094 | 2022-10-06 18:15 | 18.1 | 23 | 55
1095 | 2022-10-06 18:16 | 18.2 | 22.1 | 51
1096 | 2022-10-06 18:17 | 18 | 22.5 | 59
1097 | 2022-10-06 18:18 | 17.9 | 22.4 | 58
1098 | 2022-10-06 18:19 | 17.9 | 22.8 | 51
1099 | 2022-10-06 18:20 | 17.9 | 22.9 | 44
1100 | 2022-10-06 18:21 | 17.9 | 22.6 | 41
1101 | 2022-10-06 18:22 | 17.8 | 22.5 | 38
1102 | 2022-10-06 18:23 | 17.9 | 22.7 | 37
1103 | 2022-10-06 18:24 | 17.9 | 22.6 | 34
1104 | 2022-10-06 18:25 | 17.8 | 22.5 | 33
1105 | 2022-10-06 18:26 | 17.8 | 22.7 | 31
1106 | 2022-10-06 18:27 | 17.8 | 22.5 | 31
1107 | 2022-10-06 18:28 | 17.8 | 22.6 | 31
1108 | 2022-10-06 18:29 | 17.9 | 22.3 | 30
1109 | 2022-10-06 18:30 | 17.9 | 22.4 | 29
1110 | 2022-10-06 18:31 | 17.6 | 22.1 | 31
1111 | 2022-10-06 18:32 | 17.6 | 22.4 | 33
1112 | 2022-10-06 18:33 | 17.8 | 21.9 | 32
1113 | 2022-10-06 18:34 | 17.6 | 22.6 | 29
1114 | 2022-10-06 18:35 | 17.6 | 22.3 | 25
1115 | 2022-10-06 18:36 | 17.7 | 22.5 | 31
1116 | 2022-10-06 18:37 | 17.6 | 22.5 | 31
1117 | 2022-10-06 18:38 | 17.5 | 22.6 | 22
1118 | 2022-10-06 18:39 | 17.7 | 22.6 | 18
1119 | 2022-10-06 18:40 | 17.5 | 22.7 | 16
1120 | 2022-10-06 18:41 | 17.6 | 22.5 | 15
1121 | 2022-10-06 18:42 | 17.5 | 22.6 | 12
1122 | 2022-10-06 18:43 | 17.5 | 22.5 | 11
1123 | 2022-10-06 18:44 | 17.4 | 22.6 | 11
1124 | 2022-10-06 18:45 | 17.3 | 22.5 | 10
1125 | 2022-10-06 18:46 | 17.4 | 22.6 | 10
1126 | 2022-10-06 18:47 | 17.4 | 22.7 | 10
1127 | 2022-10-06 18:48 | 17.4 | 22.6 | 9
1128 | 2022-10-06 18:49 | 17.4 | 22.6 | 9
1129 | 2022-10-06 18:50 | 17.4 | 22.6 | 9
1130 | 2022-10-06 18:51 | 17.5 | 22.7 | 8
1131 | 2022-10-06 18:52 | 17.4 | 22.7 | 7
1132 | 2022-10-06 18:53 | 17.3 | 22.5 | 5
1133 | 2022-10-06 18:54 | 17.4 | 22.4 | 4
1134 | 2022-10-06 18:55 | 17.4 | 22.7 | 3
1135 | 2022-10-06 18:56 | 17.4 | 22.8 | 3
1136 | 2022-10-06 18:57 | 17.4 | 23 | 2
1137 | 2022-10-06 18:58 | 17.4 | 23.1 | 1
1138 | 2022-10-06 18:59 | 17.3 | 22.4 | 1
1139 | 2022-10-06 19:00 | 17.4 | 22.5 | 0
1140 | 2022-10-06 19:01 | 17.3 | 22.7 | 0
1141 | 2022-10-06 19:02 | 17.2 | 22.6 | 0
1142 | 2022-10-06 19:03 | 17.2 | 22.6 | 0
1143 | 2022-10-06 19:04 | 17.2 | 22.6 | 0
1144 | 2022-10-06 19:05 | 17.1 | 22.5 | 0
1145 | 2022-10-06 19:06 | 17.1 | 22.6 | 0
1146 | 2022-10-06 19:07 | 17.1 | 22.2 | 0
1147 | 2022-10-06 19:08 | 17.1 | 22.6 | 0
1148 | 2022-10-06 19:09 | 17.1 | 22.7 | 0
1149 | 2022-10-06 19:10 | 17 | 22.4 | 0
1150 | 2022-10-06 19:11 | 17.1 | 22.7 | 0
1151 | 2022-10-06 19:12 | 17 | 22.9 | 0
1152 | 2022-10-06 19:13 | 17 | 21.9 | 0
1153 | 2022-10-06 19:14 | 17.1 | 22.7 | 0
1154 | 2022-10-06 19:15 | 17.2 | 22.5 | 0
1155 | 2022-10-06 19:16 | 17.1 | 22.5 | 0
1156 | 2022-10-06 19:17 | 17.2 | 22.1 | 0
1157 | 2022-10-06 19:18 | 17 | 22.6 | 0
1158 | 2022-10-06 19:19 | 17 | 22.6 | 0
1159 | 2022-10-06 19:20 | 16.9 | 22.4 | 0
1160 | 2022-10-06 19:21 | 16.9 | 22.4 | 0
1161 | 2022-10-06 19:22 | 17 | 22.6 | 0
1162 | 2022-10-06 19:23 | 16.8 | 22.6 | 0
1163 | 2022-10-06 19:24 | 16.9 | 22.5 | 0
1164 | 2022-10-06 19:25 | 16.8 | 22.4 | 0
1165 | 2022-10-06 19:26 | 16.9 | 22.5 | 0
1166 | 2022-10-06 19:27 | 17 | 22.7 | 0
1167 | 2022-10-06 19:28 | 16.9 | 22.3 | 0
1168 | 2022-10-06 19:29 | 16.7 | 22.6 | 0
1169 | 2022-10-06 19:30 | 16.8 | 22.4 | 0
1170 | 2022-10-06 19:31 | 16.8 | 22.6 | 0
1171 | 2022-10-06 19:32 | 16.6 | 22.4 | 0
1172 | 2022-10-06 19:33 | 16.5 | 22.5 | 0
1173 | 2022-10-06 19:34 | 16.5 | 22.7 | 0
1174 | 2022-10-06 19:35 | 16.4 | 22.4 | 0
1175 | 2022-10-06 19:36 | 16.4 | 22.4 | 0
1176 | 2022-10-06 19:37 | 16.6 | 22.5 | 0
1177 | 2022-10-06 19:38 | 16.5 | 22.4 | 0
1178 | 2022-10-06 19:39 | 16.6 | 22.4 | 0
1179 | 2022-10-06 19:40 | 16.5 | 22.6 | 0
1180 | 2022-10-06 19:41 | 16.6 | 22.5 | 0
1181 | 2022-10-06 19:42 | 16.8 | 22.6 | 0
1182 | 2022-10-06 19:43 | 16.8 | 22.6 | 0
1183 | 2022-10-06 19:44 | 16.6 | 22.5 | 0
1184 | 2022-10-06 19:45 | 16.7 | 22.6 | 0
1185 | 2022-10-06 19:46 | 16.7 | 22.4 | 0
1186 | 2022-10-06 19:47 | 16.7 | 22.6 | 0
1187 | 2022-10-06 19:48 | 16.6 | 22.6 | 0
1188 | 2022-10-06 19:49 | 16.7 | 22.4 | 0
1189 | 2022-10-06 19:50 | 16.8 | 22.5 | 0
1190 | 2022-10-06 19:51 | 16.7 | 22.6 | 0
1191 | 2022-10-06 19:52 | 16.8 | 22.6 | 0
1192 | 2022-10-06 19:53 | 16.7 | 22.5 | 0
1193 | 2022-10-06 19:54 | 16.7 | 22.5 | 0
1194 | 2022-10-06 19:55 | 16.7 | 22.5 | 0
1195 | 2022-10-06 19:56 | 16.6 | 22.4 | 0
1196 | 2022-10-06 19:57 | 16.5 | 22.5 | 0
1197 | 2022-10-06 19:58 | 16.4 | 22.6 | 0
1198 | 2022-10-06 19:59 | 16.5 | 22.5 | 0
1199 | 2022-10-06 20:00 | 16.6 | 22.5 | 0
1200 | 2022-10-06 20:01 | 16.8 | 22.4 | 0
1201 | 2022-10-06 20:02 | 16.8 | 22.5 | 0
1202 | 2022-10-06 20:03 | 16.6 | 22.6 | 0
1203 | 2022-10-06 20:04 | 16.6 | 22.5 | 0
1204 | 2022-10-06 20:05 | 16.3 | 22.6 | 0
1205 | 2022-10-06 20:06 | 16.5 | 22.5 | 0
1206 | 2022-10-06 20:07 | 16.3 | 22.2 | 0
1207 | 2022-10-06 20:08 | 16.2 | 22.3 | 0
1208 | 2022-10-06 20:09 | 16.1 | 22.4 | 0
1209 | 2022-10-06 20:10 | 15.9 | 22.7 | 0
1210 | 2022-10-06 20:11 | 16 | 22.1 | 0
1211 | 2022-10-06 20:12 | 16 | 22.3 | 0
1212 | 2022-10-06 20:13 | 15.9 | 22.5 | 0
1213 | 2022-10-06 20:14 | 16.2 | 22.4 | 0
1214 | 2022-10-06 20:15 | 16.3 | 22.5 | 0
1215 | 2022-10-06 20:16 | 16.3 | 22 | 0
1216 | 2022-10-06 20:17 | 16.2 | 22.5 | 0
1217 | 2022-10-06 20:18 | 16.2 | 23 | 0
1218 | 2022-10-06 20:19 | 16.4 | 22.5 | 0
1219 | 2022-10-06 20:20 | 16.2 | 22.3 | 0
1220 | 2022-10-06 20:21 | 16.1 | 22.5 | 0
1221 | 2022-10-06 20:22 | 16.4 | 22.3 | 0
1222 | 2022-10-06 20:23 | 16.4 | 22.5 | 0
1223 | 2022-10-06 20:24 | 16.3 | 22.6 | 0
1224 | 2022-10-06 20:25 | 16.2 | 22.4 | 0
1225 | 2022-10-06 20:26 | 16.4 | 22.5 | 0
1226 | 2022-10-06 20:27 | 16.6 | 22.1 | 0
1227 | 2022-10-06 20:28 | 16.4 | 22.4 | 0
1228 | 2022-10-06 20:29 | 16.5 | 22.6 | 0
1229 | 2022-10-06 20:30 | 16.3 | 22.4 | 0
1230 | 2022-10-06 20:31 | 16.5 | 22.4 | 0
1231 | 2022-10-06 20:32 | 16.3 | 23.1 | 0
1232 | 2022-10-06 20:33 | 16.4 | 22.2 | 0
1233 | 2022-10-06 20:34 | 16.3 | 22.6 | 0
1234 | 2022-10-06 20:35 | 16.2 | 21.9 | 0
1235 | 2022-10-06 20:36 | 16.1 | 22.8 | 0
1236 | 2022-10-06 20:37 | 16.3 | 22.6 | 0
1237 | 2022-10-06 20:38 | 16.2 | 22.8 | 0
1238 | 2022-10-06 20:39 | 16 | 22.1 | 0
1239 | 2022-10-06 20:40 | 16.1 | 22.6 | 0
1240 | 2022-10-06 20:41 | 16.2 | 21.8 | 0
1241 | 2022-10-06 20:42 | 16.4 | 22.6 | 0
1242 | 2022-10-06 20:43 | 16.2 | 23.3 | 0
1243 | 2022-10-06 20:44 | 16.2 | 22.4 | 0
1244 | 2022-10-06 20:45 | 16.3 | 22.2 | 0
1245 | 2022-10-06 20:46 | 16.5 | 22.8 | 0
1246 | 2022-10-06 20:47 | 16.5 | 23.2 | 0
1247 | 2022-10-06 20:48 | 16.2 | 22.6 | 0
1248 | 2022-10-06 20:49 | 16.2 | 22.4 | 0
1249 | 2022-10-06 20:50 | 16.3 | 22.1 | 0
1250 | 2022-10-06 20:51 | 16.1 | 22.5 | 0
1251 | 2022-10-06 20:52 | 16.2 | 23 | 0
1252 | 2022-10-06 20:53 | 16.4 | 23.1 | 0
1253 | 2022-10-06 20:54 | 16.2 | 23.1 | 0
1254 | 2022-10-06 20:55 | 16.1 | 22.4 | 0
1255 | 2022-10-06 20:56 | 16 | 22.5 | 0
1256 | 2022-10-06 20:57 | 15.9 | 23.3 | 0
1257 | 2022-10-06 20:58 | 15.8 | 22.8 | 0
1258 | 2022-10-06 20:59 | 15.4 | 22.6 | 0
1259 | 2022-10-06 21:00 | 15.3 | 22.5 | 0
1260 | 2022-10-06 21:01 | 15.2 | 22.3 | 0
1261 | 2022-10-06 21:02 | 15 | 22.5 | 0
1262 | 2022-10-06 21:03 | 15.3 | 22.5 | 0
1263 | 2022-10-06 21:04 | 15.7 | 22.5 | 0
1264 | 2022-10-06 21:05 | 15.7 | 22.4 | 0
1265 | 2022-10-06 21:06 | 15.9 | 22.4 | 0
1266 | 2022-10-06 21:07 | 16 | 22.5 | 0
1267 | 2022-10-06 21:08 | 16 | 22.2 | 0
1268 | 2022-10-06 21:09 | 15.8 | 22.3 | 0
1269 | 2022-10-06 21:10 | 15.7 | 22.1 | 0
1270 | 2022-10-06 21:11 | 16 | 22.6 | 0
1271 | 2022-10-06 21:12 | 15.7 | 21.9 | 0
1272 | 2022-10-06 21:13 | 15.5 | 22.1 | 0
1273 | 2022-10-06 21:14 | 15.6 | 21.8 | 0
1274 | 2022-10-06 21:15 | 16 | 22.5 | 0
1275 | 2022-10-06 21:16 | 16.1 | 22.3 | 0
1276 | 2022-10-06 21:17 | 16.1 | 22.1 | 0
1277 | 2022-10-06 21:18 | 16.2 | 22.5 | 0
1278 | 2022-10-06 21:19 | 16.2 | 22.2 | 0
1279 | 2022-10-06 21:20 | 15.9 | 22.6 | 0
1280 | 2022-10-06 21:21 | 15.6 | 21.9 | 0
1281 | 2022-10-06 21:22 | 15.6 | 22.4 | 0
1282 | 2022-10-06 21:23 | 15.3 | 22.2 | 0
1283 | 2022-10-06 21:24 | 15.3 | 23.1 | 0
1284 | 2022-10-06 21:25 | 15.4 | 23 | 0
1285 | 2022-10-06 21:26 | 15.3 | 22.6 | 0
1286 | 2022-10-06 21:27 | 15.2 | 22.8 | 0
1287 | 2022-10-06 21:28 | 15.2 | 22.2 | 0
1288 | 2022-10-06 21:29 | 15.1 | 22.5 | 0
1289 | 2022-10-06 21:30 | 14.9 | 22.4 | 0
1290 | 2022-10-06 21:31 | 14.8 | 22.2 | 0
1291 | 2022-10-06 21:32 | 14.7 | 22.6 | 0
1292 | 2022-10-06 21:33 | 14.6 | 22.4 | 0
1293 | 2022-10-06 21:34 | 14.6 | 22.7 | 0
1294 | 2022-10-06 21:35 | 14.7 | 22.7 | 0
1295 | 2022-10-06 21:36 | 14.5 | 22.2 | 0
1296 | 2022-10-06 21:37 | 14.5 | 22.9 | 0
1297 | 2022-10-06 21:38 | 14.5 | 22.5 | 0
1298 | 2022-10-06 21:39 | 14.1 | 22.1 | 0
1299 | 2022-10-06 21:40 | 14.1 | 22.8 | 0
1300 | 2022-10-06 21:41 | 14.1 | 22.4 | 0
1301 | 2022-10-06 21:42 | 14.2 | 21.7 | 0
1302 | 2022-10-06 21:43 | 14.8 | 21.5 | 0
1303 | 2022-10-06 21:44 | 14.7 | 21.7 | 0
1304 | 2022-10-06 21:45 | 14.6 | 22.5 | 0
1305 | 2022-10-06 21:46 | 14.5 | 22.2 | 0
1306 | 2022-10-06 21:47 | 14.4 | 21.9 | 0
1307 | 2022-10-06 21:48 | 14.4 | 22.6 | 0
1308 | 2022-10-06 21:49 | 14.2 | 21.7 | 0
1309 | 2022-10-06 21:50 | 14.1 | 22.7 | 0
1310 | 2022-10-06 21:51 | 14.5 | 22.3 | 0
1311 | 2022-10-06 21:52 | 14.8 | 22.3 | 0
1312 | 2022-10-06 21:53 | 15 | 22.6 | 0
1313 | 2022-10-06 21:54 | 15.1 | 22.4 | 0
1314 | 2022-10-06 21:55 | 14.8 | 22.6 | 0
1315 | 2022-10-06 21:56 | 14.9 | 22.5 | 0
1316 | 2022-10-06 21:57 | 14.6 | 21.6 | 0
1317 | 2022-10-06 21:58 | 14.5 | 22.5 | 0
1318 | 2022-10-06 21:59 | 14 | 22.7 | 0
1319 | 2022-10-06 22:00 | 14 | 22.5 | 0
1320 | 2022-10-06 22:01 | 13.9 | 22.5 | 0
1321 | 2022-10-06 22:02 | 14.7 | 22.6 | 0
1322 | 2022-10-06 22:03 | 14.8 | 22.4 | 0
1323 | 2022-10-06 22:04 | 14.3 | 22.4 | 0
1324 | 2022-10-06 22:05 | 14.2 | 22.4 | 0
1325 | 2022-10-06 22:06 | 14.1 | 22.4 | 0
1326 | 2022-10-06 22:07 | 14.1 | 22.4 | 0
1327 | 2022-10-06 22:08 | 14.1 | 22.4 | 0
1328 | 2022-10-06 22:09 | 14 | 22.1 | 0
1329 | 2022-10-06 22:10 | 13.8 | 22.1 | 0
1330 | 2022-10-06 22:11 | 13.8 | 21.7 | 0
1331 | 2022-10-06 22:12 | 13.5 | 22.8 | 0
1332 | 2022-10-06 22:13 | 13.5 | 23 | 0
1333 | 2022-10-06 22:14 | 13.9 | 22.9 | 0
1334 | 2022-10-06 22:15 | 14.3 | 22.4 | 0
1335 | 2022-10-06 22:16 | 14.1 | 22.4 | 0
1336 | 2022-10-06 22:17 | 13.8 | 23.1 | 0
1337 | 2022-10-06 22:18 | 13.7 | 22.6 | 0
1338 | 2022-10-06 22:19 | 13.7 | 22.1 | 0
1339 | 2022-10-06 22:20 | 15.2 | 22.5 | 0
1340 | 2022-10-06 22:21 | 14.9 | 22.4 | 0
1341 | 2022-10-06 22:22 | 14.5 | 22.5 | 0
1342 | 2022-10-06 22:23 | 14.4 | 21.7 | 0
1343 | 2022-10-06 22:24 | 14.2 | 22.3 | 0
1344 | 2022-10-06 22:25 | 14.1 | 22.4 | 0
1345 | 2022-10-06 22:26 | 14.3 | 22.4 | 0
1346 | 2022-10-06 22:27 | 14.3 | 22.7 | 0
1347 | 2022-10-06 22:28 | 14.4 | 22.8 | 0
1348 | 2022-10-06 22:29 | 14.5 | 22.8 | 0
1349 | 2022-10-06 22:30 | 14.4 | 22.2 | 0
1350 | 2022-10-06 22:31 | 14.3 | 22.3 | 0
1351 | 2022-10-06 22:32 | 14.3 | 22.7 | 0
1352 | 2022-10-06 22:33 | 14.3 | 22.6 | 0
1353 | 2022-10-06 22:34 | 14.4 | 22.6 | 0
1354 | 2022-10-06 22:35 | 14.3 | 22.5 | 0
1355 | 2022-10-06 22:36 | 13.9 | 22.6 | 0
1356 | 2022-10-06 22:37 | 14 | 22.5 | 0
1357 | 2022-10-06 22:38 | 13.9 | 22.3 | 0
1358 | 2022-10-06 22:39 | 14.5 | 22.2 | 0
1359 | 2022-10-06 22:40 | 14.4 | 22.3 | 0
1360 | 2022-10-06 22:41 | 14.3 | 22.5 | 0
1361 | 2022-10-06 22:42 | 14.4 | 22.3 | 0
1362 | 2022-10-06 22:43 | 14.5 | 22.5 | 0
1363 | 2022-10-06 22:44 | 14.4 | 22.3 | 0
1364 | 2022-10-06 22:45 | 14.6 | 22.5 | 0
1365 | 2022-10-06 22:46 | 14.6 | 22.4 | 0
1366 | 2022-10-06 22:47 | 14.2 | 23 | 0
1367 | 2022-10-06 22:48 | 13.9 | 22.3 | 0
1368 | 2022-10-06 22:49 | 13.8 | 22.4 | 0
1369 | 2022-10-06 22:50 | 13.4 | 22.3 | 0
1370 | 2022-10-06 22:51 | 13.6 | 22.1 | 0
1371 | 2022-10-06 22:52 | 13.7 | 22.3 | 0
1372 | 2022-10-06 22:53 | 13.6 | 22.5 | 0
1373 | 2022-10-06 22:54 | 13.8 | 22.3 | 0
1374 | 2022-10-06 22:55 | 14.2 | 22.4 | 0
1375 | 2022-10-06 22:56 | 14.5 | 22.3 | 0
1376 | 2022-10-06 22:57 | 14.9 | 22.5 | 0
1377 | 2022-10-06 22:58 | 15.3 | 22.4 | 0
1378 | 2022-10-06 22:59 | 15.8 | 22.2 | 0
1379 | 2022-10-06 23:00 | 15.9 | 22.4 | 0
1380 | 2022-10-06 23:01 | 16.1 | 22.2 | 0
1381 | 2022-10-06 23:02 | 15.9 | 22.6 | 0
1382 | 2022-10-06 23:03 | 15.8 | 22.4 | 0
1383 | 2022-10-06 23:04 | 15.5 | 22.3 | 0
1384 | 2022-10-06 23:05 | 16.3 | 22.2 | 0
1385 | 2022-10-06 23:06 | 16.2 | 22.3 | 0
1386 | 2022-10-06 23:07 | 16 | 22.2 | 0
1387 | 2022-10-06 23:08 | 15.8 | 22.4 | 0
1388 | 2022-10-06 23:09 | 15.6 | 22.3 | 0
1389 | 2022-10-06 23:10 | 15.6 | 21.4 | 0
1390 | 2022-10-06 23:11 | 15.9 | 22.8 | 0
1391 | 2022-10-06 23:12 | 16.1 | 23 | 0
1392 | 2022-10-06 23:13 | 16.1 | 22.7 | 0
1393 | 2022-10-06 23:14 | 15.8 | 22.6 | 0
1394 | 2022-10-06 23:15 | 15.7 | 22.8 | 0
1395 | 2022-10-06 23:16 | 15.3 | 22.5 | 0
1396 | 2022-10-06 23:17 | 15.5 | 22.4 | 0
1397 | 2022-10-06 23:18 | 15.6 | 22.3 | 0
1398 | 2022-10-06 23:19 | 15.7 | 22.5 | 0
1399 | 2022-10-06 23:20 | 15.5 | 22.6 | 0
1400 | 2022-10-06 23:21 | 15.7 | 22.2 | 0
1401 | 2022-10-06 23:22 | 15.3 | 22 | 0
1402 | 2022-10-06 23:23 | 15.5 | 22.6 | 0
1403 | 2022-10-06 23:24 | 15.6 | 22.1 | 0
1404 | 2022-10-06 23:25 | 15.9 | 21.8 | 0
1405 | 2022-10-06 23:26 | 16 | 22.3 | 0
1406 | 2022-10-06 23:27 | 16.1 | 22.3 | 0
1407 | 2022-10-06 23:28 | 16.1 | 22.1 | 0
1408 | 2022-10-06 23:29 | 16.2 | 22.2 | 0
1409 | 2022-10-06 23:30 | 16.2 | 22.3 | 0
1410 | 2022-10-06 23:31 | 16.4 | 22.8 | 0
1411 | 2022-10-06 23:32 | 16.4 | 22.2 | 0
1412 | 2022-10-06 23:33 | 16.3 | 21.4 | 0
1413 | 2022-10-06 23:34 | 16.5 | 21.5 | 0
1414 | 2022-10-06 23:35 | 16.4 | 22 | 0
1415 | 2022-10-06 23:36 | 16.5 | 21.4 | 0
1416 | 2022-10-06 23:37 | 16.3 | 22.7 | 0
1417 | 2022-10-06 23:38 | 16.5 | 22.4 | 0
1418 | 2022-10-06 23:39 | 16.6 | 22.3 | 0
1419 | 2022-10-06 23:40 | 16.6 | 21.5 | 0
1420 | 2022-10-06 23:41 | 16.5 | 21.6 | 0
1421 | 2022-10-06 23:42 | 16.4 | 22.1 | 0
1422 | 2022-10-06 23:43 | 16.4 | 22.4 | 0
1423 | 2022-10-06 23:44 | 16.5 | 22.4 | 0
1424 | 2022-10-06 23:45 | 16.6 | 22.4 | 0
1425 | 2022-10-06 23:46 | 16.4 | 22.3 | 0
1426 | 2022-10-06 23:47 | 16.4 | 22.4 | 0
1427 | 2022-10-06 23:48 | 16.4 | 22.1 | 0
1428 | 2022-10-06 23:49 | 16.5 | 22.7 | 0
1429 | 2022-10-06 23:50 | 16.3 | 21.5 | 0
1430 | 2022-10-06 23:51 | 16.5 | 22.2 | 0
1431 | 2022-10-06 23:52 | 16.4 | 22.3 | 0
1432 | 2022-10-06 23:53 | 16.5 | 22 | 0
1433 | 2022-10-06 23:54 | 16.5 | 22.2 | 0
1434 | 2022-10-06 23:55 | 16.5 | 22.3 | 0
1435 | 2022-10-06 23:56 | 16.6 | 22.5 | 0
1436 | 2022-10-06 23:57 | 16.5 | 22.1 | 0
1437 | 2022-10-06 23:58 | 16.6 | 22.2 | 0
1438 | 2022-10-06 23:59 | 16.5 | 22.4 | 0
1439 | 2022-10-07 | 16.5 | 22.4 | 0

## 07-10-2022_NO HEAT
| Date&time_x | OUTDOOR_TEMP | INDOOR_TEMP | PYRANOMETER
0 | 2022-10-07 00:01 | 16.4 | 22.9 | 0
1 | 2022-10-07 00:02 | 16.5 | 22.4 | 0
2 | 2022-10-07 00:03 | 16.6 | 22.3 | 0
3 | 2022-10-07 00:04 | 16.4 | 22.3 | 0
4 | 2022-10-07 00:05 | 16.4 | 22.2 | 0
5 | 2022-10-07 00:06 | 16.3 | 22.1 | 0
6 | 2022-10-07 00:07 | 16.5 | 22.2 | 0
7 | 2022-10-07 00:08 | 16.4 | 22.3 | 0
8 | 2022-10-07 00:09 | 16.3 | 22.4 | 0
9 | 2022-10-07 00:10 | 16.5 | 22.2 | 0
10 | 2022-10-07 00:11 | 16.5 | 22.6 | 0
11 | 2022-10-07 00:12 | 16.4 | 22.3 | 0
12 | 2022-10-07 00:13 | 16.4 | 22.3 | 0
13 | 2022-10-07 00:14 | 16.5 | 22.1 | 0
14 | 2022-10-07 00:15 | 16.5 | 22 | 0
15 | 2022-10-07 00:16 | 16.4 | 22.1 | 0
16 | 2022-10-07 00:17 | 16.5 | 22.4 | 0
17 | 2022-10-07 00:18 | 16.3 | 22.6 | 0
18 | 2022-10-07 00:19 | 16.3 | 22.3 | 0
19 | 2022-10-07 00:20 | 16.2 | 22.4 | 0
20 | 2022-10-07 00:21 | 16.1 | 22.2 | 0
21 | 2022-10-07 00:22 | 16.1 | 21.6 | 0
22 | 2022-10-07 00:23 | 16.2 | 21.4 | 0
23 | 2022-10-07 00:24 | 16.3 | 22.6 | 0
24 | 2022-10-07 00:25 | 16.3 | 22.1 | 0
25 | 2022-10-07 00:26 | 16.1 | 22.2 | 0
26 | 2022-10-07 00:27 | 16.1 | 22.2 | 0
27 | 2022-10-07 00:28 | 16.2 | 22.6 | 0
28 | 2022-10-07 00:29 | 16.1 | 22.1 | 0
29 | 2022-10-07 00:30 | 16.3 | 22.4 | 0
30 | 2022-10-07 00:31 | 16.2 | 22.6 | 0
31 | 2022-10-07 00:32 | 16.3 | 22.1 | 0
32 | 2022-10-07 00:33 | 16.2 | 22.4 | 0
33 | 2022-10-07 00:34 | 16.2 | 22.1 | 0
34 | 2022-10-07 00:35 | 16.3 | 22.3 | 0
35 | 2022-10-07 00:36 | 16.1 | 21.9 | 0
36 | 2022-10-07 00:37 | 16.3 | 21.7 | 0
37 | 2022-10-07 00:38 | 16.2 | 22.1 | 0
38 | 2022-10-07 00:39 | 16.3 | 22.1 | 0
39 | 2022-10-07 00:40 | 16.2 | 22.5 | 0
40 | 2022-10-07 00:41 | 16.2 | 22.2 | 0
41 | 2022-10-07 00:42 | 16.2 | 22.4 | 0
42 | 2022-10-07 00:43 | 16.1 | 22.2 | 0
43 | 2022-10-07 00:44 | 16.3 | 22.4 | 0
44 | 2022-10-07 00:45 | 16.1 | 22.6 | 0
45 | 2022-10-07 00:46 | 16.2 | 22.7 | 0
46 | 2022-10-07 00:47 | 16.2 | 22.2 | 0
47 | 2022-10-07 00:48 | 16.1 | 22.7 | 0
48 | 2022-10-07 00:49 | 16.2 | 22.1 | 0
49 | 2022-10-07 00:50 | 16 | 22.4 | 0
50 | 2022-10-07 00:51 | 15.9 | 22.1 | 0
51 | 2022-10-07 00:52 | 16.1 | 22.2 | 0
52 | 2022-10-07 00:53 | 16 | 22.2 | 0
53 | 2022-10-07 00:54 | 16.1 | 22.3 | 0
54 | 2022-10-07 00:55 | 16 | 22.2 | 0
55 | 2022-10-07 00:56 | 16 | 22.1 | 0
56 | 2022-10-07 00:57 | 16.2 | 22.3 | 0
57 | 2022-10-07 00:58 | 16.3 | 22.1 | 0
58 | 2022-10-07 00:59 | 16.2 | 22.5 | 0
59 | 2022-10-07 01:00 | 16.6 | 22.3 | 0
60 | 2022-10-07 01:01 | 16.5 | 22.4 | 0
61 | 2022-10-07 01:02 | 16.4 | 22.6 | 0
62 | 2022-10-07 01:03 | 16.5 | 22.1 | 0
63 | 2022-10-07 01:04 | 16.5 | 22.3 | 0
64 | 2022-10-07 01:05 | 16.4 | 22.3 | 0
65 | 2022-10-07 01:06 | 16.4 | 22.2 | 0
66 | 2022-10-07 01:07 | 16.4 | 22.2 | 0
67 | 2022-10-07 01:08 | 16.3 | 22.4 | 0
68 | 2022-10-07 01:09 | 16.1 | 22.4 | 0
69 | 2022-10-07 01:10 | 16.1 | 22.1 | 0
70 | 2022-10-07 01:11 | 16.2 | 22 | 0
71 | 2022-10-07 01:12 | 16.3 | 22 | 0
72 | 2022-10-07 01:13 | 16.4 | 21.7 | 0
73 | 2022-10-07 01:14 | 16.2 | 22.4 | 0
74 | 2022-10-07 01:15 | 16.4 | 22.2 | 0
75 | 2022-10-07 01:16 | 16.4 | 22.9 | 0
76 | 2022-10-07 01:17 | 16.3 | 22.1 | 0
77 | 2022-10-07 01:18 | 16.3 | 22.1 | 0
78 | 2022-10-07 01:19 | 16.2 | 22.4 | 0
79 | 2022-10-07 01:20 | 16.2 | 22.2 | 0
80 | 2022-10-07 01:21 | 16.3 | 22.3 | 0
81 | 2022-10-07 01:22 | 16.2 | 21.8 | 0
82 | 2022-10-07 01:23 | 16.3 | 22.6 | 0
83 | 2022-10-07 01:24 | 16.3 | 22.3 | 0
84 | 2022-10-07 01:25 | 16.2 | 22.2 | 0
85 | 2022-10-07 01:26 | 16.4 | 22.2 | 0
86 | 2022-10-07 01:27 | 16.6 | 22.3 | 0
87 | 2022-10-07 01:28 | 16.3 | 22.3 | 0
88 | 2022-10-07 01:29 | 16.3 | 22.3 | 0
89 | 2022-10-07 01:30 | 16.3 | 22.2 | 0
90 | 2022-10-07 01:31 | 16.5 | 22.2 | 0
91 | 2022-10-07 01:32 | 16.3 | 22.8 | 0
92 | 2022-10-07 01:33 | 16.4 | 23 | 0
93 | 2022-10-07 01:34 | 16.3 | 22.2 | 0
94 | 2022-10-07 01:35 | 16.3 | 22 | 0
95 | 2022-10-07 01:36 | 16 | 22.6 | 0
96 | 2022-10-07 01:37 | 16.1 | 21.7 | 0
97 | 2022-10-07 01:38 | 16.2 | 22.3 | 0
98 | 2022-10-07 01:39 | 16.1 | 22.7 | 0
99 | 2022-10-07 01:40 | 16.3 | 22.1 | 0
100 | 2022-10-07 01:41 | 16 | 22.6 | 0
101 | 2022-10-07 01:42 | 16.2 | 22.1 | 0
102 | 2022-10-07 01:43 | 16 | 22.1 | 0
103 | 2022-10-07 01:44 | 16 | 22.4 | 0
104 | 2022-10-07 01:45 | 16.1 | 22.1 | 0
105 | 2022-10-07 01:46 | 16.1 | 22.1 | 0
106 | 2022-10-07 01:47 | 16 | 22.1 | 0
107 | 2022-10-07 01:48 | 15.9 | 22.3 | 0
108 | 2022-10-07 01:49 | 15.8 | 22.2 | 0
109 | 2022-10-07 01:50 | 16 | 22.2 | 0
110 | 2022-10-07 01:51 | 15.9 | 22.3 | 0
111 | 2022-10-07 01:52 | 15.7 | 22.2 | 0
112 | 2022-10-07 01:53 | 15.5 | 22.1 | 0
113 | 2022-10-07 01:54 | 15.6 | 22.3 | 0
114 | 2022-10-07 01:55 | 15.4 | 22.3 | 0
115 | 2022-10-07 01:56 | 15.2 | 23 | 0
116 | 2022-10-07 01:57 | 15.2 | 22.5 | 0
117 | 2022-10-07 01:58 | 14.9 | 22.1 | 0
118 | 2022-10-07 01:59 | 15 | 22.9 | 0
119 | 2022-10-07 02:00 | 15.2 | 21.7 | 0
120 | 2022-10-07 02:01 | 15 | 22.2 | 0
121 | 2022-10-07 02:02 | 14.8 | 22 | 0
122 | 2022-10-07 02:03 | 15.3 | 22.2 | 0
123 | 2022-10-07 02:04 | 15.9 | 22.4 | 0
124 | 2022-10-07 02:05 | 15.3 | 22.1 | 0
125 | 2022-10-07 02:06 | 15.3 | 21.9 | 0
126 | 2022-10-07 02:07 | 15.2 | 22.2 | 0
127 | 2022-10-07 02:08 | 15 | 21.9 | 0
128 | 2022-10-07 02:09 | 14.7 | 22.1 | 0
129 | 2022-10-07 02:10 | 15.1 | 22.1 | 0
130 | 2022-10-07 02:11 | 15.1 | 22.4 | 0
131 | 2022-10-07 02:12 | 15 | 22.2 | 0
132 | 2022-10-07 02:13 | 14.9 | 21.4 | 0
133 | 2022-10-07 02:14 | 15 | 21.6 | 0
134 | 2022-10-07 02:15 | 15 | 22.2 | 0
135 | 2022-10-07 02:16 | 14.8 | 23.2 | 0
136 | 2022-10-07 02:17 | 14.8 | 21.9 | 0
137 | 2022-10-07 02:18 | 15 | 22.5 | 0
138 | 2022-10-07 02:19 | 14.9 | 21.6 | 0
139 | 2022-10-07 02:20 | 14.9 | 22 | 0
140 | 2022-10-07 02:21 | 14.9 | 21.7 | 0
141 | 2022-10-07 02:22 | 16 | 22.1 | 0
142 | 2022-10-07 02:23 | 16.3 | 23.1 | 0
143 | 2022-10-07 02:24 | 16.5 | 23 | 0
144 | 2022-10-07 02:25 | 16.3 | 22.4 | 0
145 | 2022-10-07 02:26 | 16 | 22.9 | 0
146 | 2022-10-07 02:27 | 15.7 | 22.3 | 0
147 | 2022-10-07 02:28 | 16 | 22.1 | 0
148 | 2022-10-07 02:29 | 15.6 | 22 | 0
149 | 2022-10-07 02:30 | 15.6 | 22.4 | 0
150 | 2022-10-07 02:31 | 15.7 | 21.7 | 0
151 | 2022-10-07 02:32 | 15.8 | 22.5 | 0
152 | 2022-10-07 02:33 | 15.9 | 21.9 | 0
153 | 2022-10-07 02:34 | 16.1 | 22.1 | 0
154 | 2022-10-07 02:35 | 16.4 | 22.1 | 0
155 | 2022-10-07 02:36 | 15.9 | 22.5 | 0
156 | 2022-10-07 02:37 | 15.7 | 21.7 | 0
157 | 2022-10-07 02:38 | 15.4 | 22.6 | 0
158 | 2022-10-07 02:39 | 15.1 | 21.7 | 0
159 | 2022-10-07 02:40 | 15.3 | 21.7 | 0
160 | 2022-10-07 02:41 | 15.4 | 22.3 | 0
161 | 2022-10-07 02:42 | 15.5 | 22.8 | 0
162 | 2022-10-07 02:43 | 15.7 | 22 | 0
163 | 2022-10-07 02:44 | 15.8 | 22.1 | 0
164 | 2022-10-07 02:45 | 15.8 | 22.1 | 0
165 | 2022-10-07 02:46 | 16.1 | 21.9 | 0
166 | 2022-10-07 02:47 | 16.1 | 22.2 | 0
167 | 2022-10-07 02:48 | 16.1 | 22.5 | 0
168 | 2022-10-07 02:49 | 16 | 22.1 | 0
169 | 2022-10-07 02:50 | 15.9 | 22.8 | 0
170 | 2022-10-07 02:51 | 16.1 | 22.5 | 0
171 | 2022-10-07 02:52 | 16 | 21.4 | 0
172 | 2022-10-07 02:53 | 16 | 21.6 | 0
173 | 2022-10-07 02:54 | 16.2 | 22.3 | 0
174 | 2022-10-07 02:55 | 16.1 | 22.3 | 0
175 | 2022-10-07 02:56 | 16.2 | 22.9 | 0
176 | 2022-10-07 02:57 | 16.3 | 21.6 | 0
177 | 2022-10-07 02:58 | 16.8 | 21.3 | 0
178 | 2022-10-07 02:59 | 16.6 | 22.8 | 0
179 | 2022-10-07 03:00 | 16.5 | 22.6 | 0
180 | 2022-10-07 03:01 | 16.7 | 21.9 | 0
181 | 2022-10-07 03:02 | 16.5 | 22.6 | 0
182 | 2022-10-07 03:03 | 16.3 | 21.9 | 0
183 | 2022-10-07 03:04 | 16.6 | 22.3 | 0
184 | 2022-10-07 03:05 | 16.5 | 22.2 | 0
185 | 2022-10-07 03:06 | 16.6 | 22 | 0
186 | 2022-10-07 03:07 | 16.7 | 22.4 | 0
187 | 2022-10-07 03:08 | 16.6 | 22.2 | 0
188 | 2022-10-07 03:09 | 16.4 | 22.2 | 0
189 | 2022-10-07 03:10 | 16.5 | 22.4 | 0
190 | 2022-10-07 03:11 | 16.4 | 21.9 | 0
191 | 2022-10-07 03:12 | 16.4 | 22.1 | 0
192 | 2022-10-07 03:13 | 16.4 | 22.1 | 0
193 | 2022-10-07 03:14 | 16.2 | 22.1 | 0
194 | 2022-10-07 03:15 | 16.2 | 22.4 | 0
195 | 2022-10-07 03:16 | 16.5 | 21.9 | 0
196 | 2022-10-07 03:17 | 16.4 | 22 | 0
197 | 2022-10-07 03:18 | 16 | 21.5 | 0
198 | 2022-10-07 03:19 | 15.9 | 22.7 | 0
199 | 2022-10-07 03:20 | 16.2 | 22.4 | 0
200 | 2022-10-07 03:21 | 16.2 | 21.3 | 0
201 | 2022-10-07 03:22 | 16.3 | 22.1 | 0
202 | 2022-10-07 03:23 | 16.3 | 21.3 | 0
203 | 2022-10-07 03:24 | 16.3 | 22.2 | 0
204 | 2022-10-07 03:25 | 16.4 | 22.2 | 0
205 | 2022-10-07 03:26 | 16.3 | 22.1 | 0
206 | 2022-10-07 03:27 | 16.1 | 21.4 | 0
207 | 2022-10-07 03:28 | 16 | 21.9 | 0
208 | 2022-10-07 03:29 | 16.4 | 21.6 | 0
209 | 2022-10-07 03:30 | 16.4 | 21.9 | 0
210 | 2022-10-07 03:31 | 16.4 | 22.7 | 0
211 | 2022-10-07 03:32 | 16.3 | 22.4 | 0
212 | 2022-10-07 03:33 | 16.5 | 22.4 | 0
213 | 2022-10-07 03:34 | 16.3 | 22.8 | 0
214 | 2022-10-07 03:35 | 16.5 | 22.2 | 0
215 | 2022-10-07 03:36 | 16.2 | 21.9 | 0
216 | 2022-10-07 03:37 | 16.3 | 21.9 | 0
217 | 2022-10-07 03:38 | 16.3 | 22.5 | 0
218 | 2022-10-07 03:39 | 16.3 | 22.7 | 0
219 | 2022-10-07 03:40 | 16.5 | 22 | 0
220 | 2022-10-07 03:41 | 16.1 | 22.6 | 0
221 | 2022-10-07 03:42 | 16.2 | 22.9 | 0
222 | 2022-10-07 03:43 | 16.4 | 21.3 | 0
223 | 2022-10-07 03:44 | 16.3 | 21.2 | 0
224 | 2022-10-07 03:45 | 16.4 | 22.2 | 0
225 | 2022-10-07 03:46 | 16.2 | 21.6 | 0
226 | 2022-10-07 03:47 | 16.5 | 22.8 | 0
227 | 2022-10-07 03:48 | 16.3 | 21.5 | 0
228 | 2022-10-07 03:49 | 16.2 | 22.7 | 0
229 | 2022-10-07 03:50 | 16.2 | 22.2 | 0
230 | 2022-10-07 03:51 | 16.1 | 22.3 | 0
231 | 2022-10-07 03:52 | 16.1 | 21.9 | 0
232 | 2022-10-07 03:53 | 16.1 | 21.6 | 0
233 | 2022-10-07 03:54 | 16.1 | 21.7 | 0
234 | 2022-10-07 03:55 | 16.2 | 21.6 | 0
235 | 2022-10-07 03:56 | 16.3 | 22.3 | 0
236 | 2022-10-07 03:57 | 16.3 | 22.1 | 0
237 | 2022-10-07 03:58 | 16.2 | 21.7 | 0
238 | 2022-10-07 03:59 | 16.4 | 22.1 | 0
239 | 2022-10-07 04:00 | 16.4 | 22.3 | 0
240 | 2022-10-07 04:01 | 16.4 | 21.3 | 0
241 | 2022-10-07 04:02 | 16.5 | 22.3 | 0
242 | 2022-10-07 04:03 | 16.4 | 22.3 | 0
243 | 2022-10-07 04:04 | 16.5 | 21.9 | 0
244 | 2022-10-07 04:05 | 16.5 | 22.2 | 0
245 | 2022-10-07 04:06 | 16.5 | 22.4 | 0
246 | 2022-10-07 04:07 | 16.2 | 22.6 | 0
247 | 2022-10-07 04:08 | 16.1 | 22.7 | 0
248 | 2022-10-07 04:09 | 16.4 | 21.6 | 0
249 | 2022-10-07 04:10 | 16.4 | 22.6 | 0
250 | 2022-10-07 04:11 | 16.3 | 21.9 | 0
251 | 2022-10-07 04:12 | 16.2 | 21.4 | 0
252 | 2022-10-07 04:13 | 16.1 | 21.3 | 0
253 | 2022-10-07 04:14 | 16.3 | 21.4 | 0
254 | 2022-10-07 04:15 | 16.2 | 21.3 | 0
255 | 2022-10-07 04:16 | 16.4 | 22.5 | 0
256 | 2022-10-07 04:17 | 16.3 | 22 | 0
257 | 2022-10-07 04:18 | 16.1 | 21.4 | 0
258 | 2022-10-07 04:19 | 15.9 | 21.3 | 0
259 | 2022-10-07 04:20 | 16.1 | 22.7 | 0
260 | 2022-10-07 04:21 | 15.9 | 21.6 | 0
261 | 2022-10-07 04:22 | 15.7 | 22.2 | 0
262 | 2022-10-07 04:23 | 15.8 | 21.2 | 0
263 | 2022-10-07 04:24 | 16 | 21.2 | 0
264 | 2022-10-07 04:25 | 16 | 21.2 | 0
265 | 2022-10-07 04:26 | 16.1 | 21.5 | 0
266 | 2022-10-07 04:27 | 16 | 21.3 | 0
267 | 2022-10-07 04:28 | 16.2 | 22.1 | 0
268 | 2022-10-07 04:29 | 16.5 | 22.2 | 0
269 | 2022-10-07 04:30 | 16.3 | 22.1 | 0
270 | 2022-10-07 04:31 | 16.3 | 21.5 | 0
271 | 2022-10-07 04:32 | 16.4 | 22.6 | 0
272 | 2022-10-07 04:33 | 16.2 | 22.3 | 0
273 | 2022-10-07 04:34 | 16.4 | 22 | 0
274 | 2022-10-07 04:35 | 16.4 | 21.6 | 0
275 | 2022-10-07 04:36 | 16.4 | 21.4 | 0
276 | 2022-10-07 04:37 | 16.5 | 22.5 | 0
277 | 2022-10-07 04:38 | 16.5 | 23 | 0
278 | 2022-10-07 04:39 | 16.5 | 22 | 0
279 | 2022-10-07 04:40 | 16.4 | 21.6 | 0
280 | 2022-10-07 04:41 | 16.4 | 22.4 | 0
281 | 2022-10-07 04:42 | 16.5 | 21.9 | 0
282 | 2022-10-07 04:43 | 16.5 | 21.8 | 0
283 | 2022-10-07 04:44 | 16.2 | 22.3 | 0
284 | 2022-10-07 04:45 | 16.4 | 21.9 | 0
285 | 2022-10-07 04:46 | 16.4 | 22.1 | 0
286 | 2022-10-07 04:47 | 16.4 | 22.2 | 0
287 | 2022-10-07 04:48 | 16.5 | 21.2 | 0
288 | 2022-10-07 04:49 | 16.3 | 21.3 | 0
289 | 2022-10-07 04:50 | 16.4 | 21.8 | 0
290 | 2022-10-07 04:51 | 16.6 | 22.3 | 0
291 | 2022-10-07 04:52 | 16.8 | 22.8 | 0
292 | 2022-10-07 04:53 | 16.7 | 22.8 | 0
293 | 2022-10-07 04:54 | 16.7 | 23 | 0
294 | 2022-10-07 04:55 | 16.5 | 22.6 | 0
295 | 2022-10-07 04:56 | 16.6 | 21.6 | 0
296 | 2022-10-07 04:57 | 16.5 | 22.7 | 0
297 | 2022-10-07 04:58 | 16.4 | 22.8 | 0
298 | 2022-10-07 04:59 | 16.5 | 22.8 | 0
299 | 2022-10-07 05:00 | 16.5 | 21.9 | 0
300 | 2022-10-07 05:01 | 16.6 | 22.2 | 0
301 | 2022-10-07 05:02 | 16.5 | 22 | 0
302 | 2022-10-07 05:03 | 16.6 | 22.1 | 0
303 | 2022-10-07 05:04 | 16.5 | 21.4 | 0
304 | 2022-10-07 05:05 | 16.5 | 21.4 | 0
305 | 2022-10-07 05:06 | 16.7 | 22.3 | 0
306 | 2022-10-07 05:07 | 16.4 | 21.5 | 0
307 | 2022-10-07 05:08 | 16.7 | 22.4 | 0
308 | 2022-10-07 05:09 | 16.5 | 21.5 | 0
309 | 2022-10-07 05:10 | 16.6 | 22.2 | 0
310 | 2022-10-07 05:11 | 16.4 | 22.4 | 0
311 | 2022-10-07 05:12 | 16.6 | 22.8 | 0
312 | 2022-10-07 05:13 | 16.7 | 21.5 | 0
313 | 2022-10-07 05:14 | 16.6 | 22 | 0
314 | 2022-10-07 05:15 | 16.5 | 22.2 | 0
315 | 2022-10-07 05:16 | 16.7 | 22.7 | 0
316 | 2022-10-07 05:17 | 16.4 | 22.1 | 0
317 | 2022-10-07 05:18 | 16.5 | 21.5 | 0
318 | 2022-10-07 05:19 | 16.7 | 21.3 | 0
319 | 2022-10-07 05:20 | 16.5 | 21.5 | 0
320 | 2022-10-07 05:21 | 16.2 | 22.3 | 0
321 | 2022-10-07 05:22 | 16.3 | 22.9 | 0
322 | 2022-10-07 05:23 | 16.6 | 21.9 | 0
323 | 2022-10-07 05:24 | 16.5 | 21.1 | 0
324 | 2022-10-07 05:25 | 16.4 | 22.3 | 0
325 | 2022-10-07 05:26 | 16.4 | 22.8 | 0
326 | 2022-10-07 05:27 | 16.3 | 22.5 | 0
327 | 2022-10-07 05:28 | 16.4 | 22.6 | 0
328 | 2022-10-07 05:29 | 16.3 | 21.8 | 0
329 | 2022-10-07 05:30 | 16.4 | 21.3 | 0
330 | 2022-10-07 05:31 | 16.4 | 21.4 | 0
331 | 2022-10-07 05:32 | 16.4 | 21.9 | 0
332 | 2022-10-07 05:33 | 16.3 | 21.6 | 0
333 | 2022-10-07 05:34 | 16.3 | 21.9 | 0
334 | 2022-10-07 05:35 | 16.3 | 22.3 | 0
335 | 2022-10-07 05:36 | 16.4 | 22.1 | 0
336 | 2022-10-07 05:37 | 16.4 | 22 | 0
337 | 2022-10-07 05:38 | 16.3 | 21.8 | 0
338 | 2022-10-07 05:39 | 16.7 | 21.9 | 0
339 | 2022-10-07 05:40 | 16.6 | 21 | 0
340 | 2022-10-07 05:41 | 16.6 | 21.4 | 0
341 | 2022-10-07 05:42 | 16.4 | 21.9 | 0
342 | 2022-10-07 05:43 | 16.5 | 22 | 0
343 | 2022-10-07 05:44 | 16.3 | 22.6 | 0
344 | 2022-10-07 05:45 | 16.7 | 21.4 | 0
345 | 2022-10-07 05:46 | 16.4 | 22.3 | 0
346 | 2022-10-07 05:47 | 16.5 | 21.8 | 0
347 | 2022-10-07 05:48 | 16.4 | 21.8 | 0
348 | 2022-10-07 05:49 | 16.3 | 21.9 | 0
349 | 2022-10-07 05:50 | 16.3 | 21.8 | 0
350 | 2022-10-07 05:51 | 16.4 | 22 | 0
351 | 2022-10-07 05:52 | 16.2 | 21.3 | 0
352 | 2022-10-07 05:53 | 16.2 | 21.2 | 0
353 | 2022-10-07 05:54 | 16.1 | 21.7 | 0
354 | 2022-10-07 05:55 | 16.2 | 21.9 | 0
355 | 2022-10-07 05:56 | 16.2 | 22.1 | 0
356 | 2022-10-07 05:57 | 16.3 | 22 | 0
357 | 2022-10-07 05:58 | 16.4 | 21.7 | 0
358 | 2022-10-07 05:59 | 16.4 | 22 | 0
359 | 2022-10-07 06:00 | 16.3 | 21.7 | 0
360 | 2022-10-07 06:01 | 16.4 | 22.3 | 0
361 | 2022-10-07 06:02 | 16.2 | 21.8 | 0
362 | 2022-10-07 06:03 | 16.2 | 21.8 | 0
363 | 2022-10-07 06:04 | 16.2 | 22 | 0
364 | 2022-10-07 06:05 | 16.3 | 22 | 0
365 | 2022-10-07 06:06 | 16.4 | 21.6 | 0
366 | 2022-10-07 06:07 | 16.6 | 22.9 | 0
367 | 2022-10-07 06:08 | 16.5 | 22.1 | 0
368 | 2022-10-07 06:09 | 16.3 | 21.3 | 0
369 | 2022-10-07 06:10 | 16.4 | 22.2 | 0
370 | 2022-10-07 06:11 | 16.4 | 22.1 | 0
371 | 2022-10-07 06:12 | 16.6 | 21.3 | 0
372 | 2022-10-07 06:13 | 16.5 | 22.8 | 0
373 | 2022-10-07 06:14 | 16.3 | 22.8 | 0
374 | 2022-10-07 06:15 | 16.4 | 22.7 | 0
375 | 2022-10-07 06:16 | 16.2 | 21.3 | 0
376 | 2022-10-07 06:17 | 16.3 | 21.7 | 0
377 | 2022-10-07 06:18 | 16.3 | 22 | 0
378 | 2022-10-07 06:19 | 16.3 | 21.9 | 0
379 | 2022-10-07 06:20 | 16.2 | 21.5 | 0
380 | 2022-10-07 06:21 | 16.2 | 22.1 | 0
381 | 2022-10-07 06:22 | 16.3 | 21.5 | 0
382 | 2022-10-07 06:23 | 16.3 | 22.9 | 0
383 | 2022-10-07 06:24 | 16.2 | 22.8 | 0
384 | 2022-10-07 06:25 | 16.2 | 21.8 | 0
385 | 2022-10-07 06:26 | 16.1 | 21.3 | 0
386 | 2022-10-07 06:27 | 16.3 | 22.1 | 0
387 | 2022-10-07 06:28 | 16.1 | 22.2 | 0
388 | 2022-10-07 06:29 | 16 | 22.1 | 0
389 | 2022-10-07 06:30 | 16.1 | 22.6 | 0
390 | 2022-10-07 06:31 | 16.2 | 22.9 | 0
391 | 2022-10-07 06:32 | 16.1 | 21.4 | 0
392 | 2022-10-07 06:33 | 16.3 | 21.5 | 0
393 | 2022-10-07 06:34 | 16.4 | 22 | 0
394 | 2022-10-07 06:35 | 16.2 | 21.8 | 0
395 | 2022-10-07 06:36 | 16.3 | 21.9 | 0
396 | 2022-10-07 06:37 | 16.4 | 21.7 | 0
397 | 2022-10-07 06:38 | 16.2 | 21.8 | 0
398 | 2022-10-07 06:39 | 16.2 | 21.9 | 0
399 | 2022-10-07 06:40 | 16.1 | 21.8 | 0
400 | 2022-10-07 06:41 | 16.1 | 22.1 | 0
401 | 2022-10-07 06:42 | 16.1 | 21.9 | 0
402 | 2022-10-07 06:43 | 16.1 | 21.7 | 0
403 | 2022-10-07 06:44 | 16.2 | 21.8 | 0
404 | 2022-10-07 06:45 | 16.3 | 22.1 | 0
405 | 2022-10-07 06:46 | 16.1 | 21.6 | 0
406 | 2022-10-07 06:47 | 16.3 | 22 | 0
407 | 2022-10-07 06:48 | 16.2 | 21.8 | 0
408 | 2022-10-07 06:49 | 16.2 | 21.6 | 0
409 | 2022-10-07 06:50 | 16.1 | 22.2 | 0
410 | 2022-10-07 06:51 | 16.3 | 21.9 | 0
411 | 2022-10-07 06:52 | 16.1 | 22.3 | 0
412 | 2022-10-07 06:53 | 16.1 | 21.9 | 0
413 | 2022-10-07 06:54 | 16.2 | 21.7 | 0
414 | 2022-10-07 06:55 | 16.3 | 21.4 | 0
415 | 2022-10-07 06:56 | 16.3 | 21.9 | 0
416 | 2022-10-07 06:57 | 16.3 | 21.9 | 0
417 | 2022-10-07 06:58 | 16.3 | 21.4 | 0
418 | 2022-10-07 06:59 | 16.1 | 22 | 0
419 | 2022-10-07 07:00 | 16.2 | 21.8 | 0
420 | 2022-10-07 07:01 | 16.2 | 21.8 | 0
421 | 2022-10-07 07:02 | 16.1 | 21.9 | 0
422 | 2022-10-07 07:03 | 16.1 | 21.8 | 0
423 | 2022-10-07 07:04 | 16 | 21.8 | 0
424 | 2022-10-07 07:05 | 16.1 | 22.1 | 0
425 | 2022-10-07 07:06 | 16.2 | 21.3 | 0
426 | 2022-10-07 07:07 | 16.2 | 21 | 0
427 | 2022-10-07 07:08 | 16.2 | 21.3 | 0
428 | 2022-10-07 07:09 | 16.1 | 22.1 | 0
429 | 2022-10-07 07:10 | 16.2 | 22 | 0
430 | 2022-10-07 07:11 | 16.2 | 22.3 | 0
431 | 2022-10-07 07:12 | 16.3 | 22.3 | 0
432 | 2022-10-07 07:13 | 16.3 | 22 | 0
433 | 2022-10-07 07:14 | 16.1 | 21.9 | 0
434 | 2022-10-07 07:15 | 16.1 | 22.1 | 0
435 | 2022-10-07 07:16 | 16.4 | 21.4 | 0
436 | 2022-10-07 07:17 | 16.3 | 21.8 | 0
437 | 2022-10-07 07:18 | 16.3 | 21.8 | 0
438 | 2022-10-07 07:19 | 16.1 | 21.9 | 0
439 | 2022-10-07 07:20 | 16.2 | 22 | 0
440 | 2022-10-07 07:21 | 16.2 | 22.3 | 0
441 | 2022-10-07 07:22 | 16.2 | 21.3 | 0
442 | 2022-10-07 07:23 | 16.2 | 21.9 | 0
443 | 2022-10-07 07:24 | 15.9 | 22 | 0
444 | 2022-10-07 07:25 | 15.9 | 21.8 | 0
445 | 2022-10-07 07:26 | 15.9 | 22.1 | 1
446 | 2022-10-07 07:27 | 16.1 | 21.8 | 1
447 | 2022-10-07 07:28 | 16.1 | 21.9 | 2
448 | 2022-10-07 07:29 | 16.4 | 21.8 | 2
449 | 2022-10-07 07:30 | 16.4 | 21.9 | 3
450 | 2022-10-07 07:31 | 16.4 | 22 | 3
451 | 2022-10-07 07:32 | 16.3 | 22 | 4
452 | 2022-10-07 07:33 | 16.3 | 21.8 | 5
453 | 2022-10-07 07:34 | 16.4 | 21.7 | 5
454 | 2022-10-07 07:35 | 16.2 | 21.7 | 5
455 | 2022-10-07 07:36 | 16.2 | 21.8 | 6
456 | 2022-10-07 07:37 | 16.4 | 21.7 | 6
457 | 2022-10-07 07:38 | 16.3 | 21.9 | 6
458 | 2022-10-07 07:39 | 16.2 | 21.9 | 7
459 | 2022-10-07 07:40 | 16.2 | 21.9 | 7
460 | 2022-10-07 07:41 | 16.4 | 21.6 | 8
461 | 2022-10-07 07:42 | 16.3 | 22.1 | 8
462 | 2022-10-07 07:43 | 16.2 | 21.9 | 9
463 | 2022-10-07 07:44 | 16.3 | 21.9 | 9
464 | 2022-10-07 07:45 | 16.3 | 21.9 | 10
465 | 2022-10-07 07:46 | 16.5 | 21.6 | 11
466 | 2022-10-07 07:47 | 16.3 | 22 | 12
467 | 2022-10-07 07:48 | 16.3 | 21.7 | 12
468 | 2022-10-07 07:49 | 16.2 | 21.9 | 13
469 | 2022-10-07 07:50 | 16.4 | 21.9 | 14
470 | 2022-10-07 07:51 | 16.2 | 21.9 | 15
471 | 2022-10-07 07:52 | 16.3 | 21.8 | 16
472 | 2022-10-07 07:53 | 16.2 | 22.2 | 16
473 | 2022-10-07 07:54 | 16.1 | 21.7 | 17
474 | 2022-10-07 07:55 | 16.2 | 21.7 | 18
475 | 2022-10-07 07:56 | 16.3 | 21.7 | 23
476 | 2022-10-07 07:57 | 16.3 | 21.8 | 27
477 | 2022-10-07 07:58 | 16.3 | 21.8 | 26
478 | 2022-10-07 07:59 | 16.3 | 21.7 | 27
479 | 2022-10-07 08:00 | 16.4 | 21.6 | 25
480 | 2022-10-07 08:01 | 16.4 | 21.8 | 25
481 | 2022-10-07 08:02 | 16.5 | 21.9 | 27
482 | 2022-10-07 08:03 | 16.5 | 21.8 | 26
483 | 2022-10-07 08:04 | 16.5 | 21.9 | 25
484 | 2022-10-07 08:05 | 16.5 | 21.7 | 28
485 | 2022-10-07 08:06 | 16.5 | 21.7 | 31
486 | 2022-10-07 08:07 | 16.6 | 21.1 | 33
487 | 2022-10-07 08:08 | 16.8 | 22.3 | 37
488 | 2022-10-07 08:09 | 16.8 | 22.7 | 27
489 | 2022-10-07 08:10 | 16.6 | 22.1 | 25
490 | 2022-10-07 08:11 | 16.9 | 21.4 | 29
491 | 2022-10-07 08:12 | 16.8 | 21.8 | 34
492 | 2022-10-07 08:13 | 16.7 | 22.3 | 36
493 | 2022-10-07 08:14 | 16.7 | 22 | 43
494 | 2022-10-07 08:15 | 16.7 | 21 | 56
495 | 2022-10-07 08:16 | 16.7 | 21.1 | 49
496 | 2022-10-07 08:17 | 16.7 | 21.2 | 41
497 | 2022-10-07 08:18 | 16.7 | 22.5 | 33
498 | 2022-10-07 08:19 | 16.9 | 21.8 | 35
499 | 2022-10-07 08:20 | 16.8 | 22 | 41
500 | 2022-10-07 08:21 | 16.9 | 22.3 | 59
501 | 2022-10-07 08:22 | 16.7 | 21.3 | 70
502 | 2022-10-07 08:23 | 16.7 | 21.1 | 65
503 | 2022-10-07 08:24 | 16.7 | 21.2 | 60
504 | 2022-10-07 08:25 | 16.8 | 21.7 | 50
505 | 2022-10-07 08:26 | 16.8 | 22.4 | 48
506 | 2022-10-07 08:27 | 17 | 22.3 | 49
507 | 2022-10-07 08:28 | 16.8 | 21.9 | 43
508 | 2022-10-07 08:29 | 16.8 | 21.1 | 56
509 | 2022-10-07 08:30 | 17 | 22.5 | 50
510 | 2022-10-07 08:31 | 17 | 21.8 | 49
511 | 2022-10-07 08:32 | 17 | 22.2 | 54
512 | 2022-10-07 08:33 | 16.9 | 21.9 | 51
513 | 2022-10-07 08:34 | 17 | 22.6 | 49
514 | 2022-10-07 08:35 | 17 | 21.8 | 53
515 | 2022-10-07 08:36 | 16.9 | 21.5 | 52
516 | 2022-10-07 08:37 | 17.1 | 22.4 | 50
517 | 2022-10-07 08:38 | 17.1 | 22.6 | 51
518 | 2022-10-07 08:39 | 17.1 | 22.3 | 41
519 | 2022-10-07 08:40 | 16.9 | 22.2 | 38
520 | 2022-10-07 08:41 | 16.9 | 21.7 | 37
521 | 2022-10-07 08:42 | 17 | 22.2 | 141
522 | 2022-10-07 08:43 | 17.1 | 22.6 | 190
523 | 2022-10-07 08:44 | 17.1 | 22.1 | 171
524 | 2022-10-07 08:45 | 17.2 | 22.1 | 55
525 | 2022-10-07 08:46 | 17 | 21.7 | 52
526 | 2022-10-07 08:47 | 17.1 | 20.8 | 57
527 | 2022-10-07 08:48 | 17.1 | 21.6 | 61
528 | 2022-10-07 08:49 | 17.1 | 20.1 | 74
529 | 2022-10-07 08:50 | 17.1 | 20.8 | 68
530 | 2022-10-07 08:51 | 16.9 | 21.6 | 57
531 | 2022-10-07 08:52 | 17.1 | 20.3 | 62
532 | 2022-10-07 08:53 | 16.9 | 20.6 | 61
533 | 2022-10-07 08:54 | 17 | 21.7 | 75
534 | 2022-10-07 08:55 | 17.1 | 21.8 | 69
535 | 2022-10-07 08:56 | 17 | 21.1 | 64
536 | 2022-10-07 08:57 | 16.9 | 21.3 | 49
537 | 2022-10-07 08:58 | 17 | 20.3 | 72
538 | 2022-10-07 08:59 | 17.1 | 20.7 | 82
539 | 2022-10-07 09:00 | 17.1 | 20.7 | 77
540 | 2022-10-07 09:01 | 17.1 | 20.3 | 77
541 | 2022-10-07 09:02 | 17 | 21 | 78
542 | 2022-10-07 09:03 | 17 | 21.2 | 85
543 | 2022-10-07 09:04 | 17.3 | 20.3 | 92
544 | 2022-10-07 09:05 | 17.1 | 19.8 | 89
545 | 2022-10-07 09:06 | 17.1 | 21.5 | 70
546 | 2022-10-07 09:07 | 17.2 | 20.5 | 75
547 | 2022-10-07 09:08 | 17 | 20.3 | 83
548 | 2022-10-07 09:09 | 17.1 | 20.5 | 92
549 | 2022-10-07 09:10 | 17.1 | 20.8 | 111
550 | 2022-10-07 09:11 | 17.3 | 20.6 | 123
551 | 2022-10-07 09:12 | 17.3 | 20.3 | 121
552 | 2022-10-07 09:13 | 17.3 | 19.7 | 112
553 | 2022-10-07 09:14 | 17.4 | 20.1 | 134
554 | 2022-10-07 09:15 | 17.4 | 20.7 | 157
555 | 2022-10-07 09:16 | 17.4 | 20.2 | 148
556 | 2022-10-07 09:17 | 17.7 | 20.8 | 483
557 | 2022-10-07 09:18 | 17.6 | 20 | 242
558 | 2022-10-07 09:19 | 17.7 | 21.4 | 149
559 | 2022-10-07 09:20 | 17.8 | 21.3 | 191
560 | 2022-10-07 09:21 | 17.9 | 20 | 164
561 | 2022-10-07 09:22 | 17.7 | 20.2 | 118
562 | 2022-10-07 09:23 | 17.8 | 21 | 325
563 | 2022-10-07 09:24 | 18.1 | 20.3 | 506
564 | 2022-10-07 09:25 | 18.2 | 20.4 | 501
565 | 2022-10-07 09:26 | 18.3 | 20.7 | 489
566 | 2022-10-07 09:27 | 18.2 | 21 | 387
567 | 2022-10-07 09:28 | 18.1 | 20.8 | 146
568 | 2022-10-07 09:29 | 18.1 | 20.8 | 460
569 | 2022-10-07 09:30 | 18.1 | 20.6 | 462
570 | 2022-10-07 09:31 | 18.1 | 20.7 | 501
571 | 2022-10-07 09:32 | 18.4 | 21 | 501
572 | 2022-10-07 09:33 | 18.3 | 20 | 441
573 | 2022-10-07 09:34 | 18.2 | 20.5 | 425
574 | 2022-10-07 09:35 | 18.1 | 20.4 | 506
575 | 2022-10-07 09:36 | 18.1 | 20.2 | 452
576 | 2022-10-07 09:37 | 18 | 20.1 | 192
577 | 2022-10-07 09:38 | 18 | 19.9 | 226
578 | 2022-10-07 09:39 | 18 | 21.1 | 518
579 | 2022-10-07 09:40 | 18 | 20.7 | 520
580 | 2022-10-07 09:41 | 18.5 | 21 | 524
581 | 2022-10-07 09:42 | 18.4 | 20.5 | 493
582 | 2022-10-07 09:43 | 18.8 | 20.9 | 521
583 | 2022-10-07 09:44 | 18.6 | 20.8 | 541
584 | 2022-10-07 09:45 | 18.7 | 21.1 | 542
585 | 2022-10-07 09:46 | 18.7 | 20.8 | 540
586 | 2022-10-07 09:47 | 18.7 | 20.8 | 543
587 | 2022-10-07 09:48 | 18.6 | 20.9 | 548
588 | 2022-10-07 09:49 | 18.8 | 21.3 | 557
589 | 2022-10-07 09:50 | 18.7 | 20.7 | 559
590 | 2022-10-07 09:51 | 18.9 | 20.9 | 562
591 | 2022-10-07 09:52 | 19 | 21.1 | 576
592 | 2022-10-07 09:53 | 18.8 | 20.9 | 586
593 | 2022-10-07 09:54 | 19.1 | 20.4 | 579
594 | 2022-10-07 09:55 | 19 | 20.5 | 578
595 | 2022-10-07 09:56 | 19.2 | 21.4 | 571
596 | 2022-10-07 09:57 | 18.8 | 20.3 | 578
597 | 2022-10-07 09:58 | 18.8 | 21 | 580
598 | 2022-10-07 09:59 | 18.5 | 19.5 | 588
599 | 2022-10-07 10:00 | 18.8 | 19.9 | 593
600 | 2022-10-07 10:01 | 18.6 | 20.3 | 597
601 | 2022-10-07 10:02 | 19 | 20.1 | 600
602 | 2022-10-07 10:03 | 19 | 20.3 | 609
603 | 2022-10-07 10:04 | 19.2 | 20.1 | 604
604 | 2022-10-07 10:05 | 19.3 | 21.1 | 612
605 | 2022-10-07 10:06 | 19.1 | 21.2 | 619
606 | 2022-10-07 10:07 | 19.1 | 19.8 | 622
607 | 2022-10-07 10:08 | 19 | 19.8 | 624
608 | 2022-10-07 10:09 | 19 | 19.8 | 628
609 | 2022-10-07 10:10 | 19.2 | 20 | 634
610 | 2022-10-07 10:11 | 19.2 | 20.5 | 640
611 | 2022-10-07 10:12 | 19.1 | 20.3 | 639
612 | 2022-10-07 10:13 | 19 | 19.5 | 644
613 | 2022-10-07 10:14 | 19.1 | 20.1 | 648
614 | 2022-10-07 10:15 | 19.3 | 20.5 | 651
615 | 2022-10-07 10:16 | 19.4 | 21.1 | 658
616 | 2022-10-07 10:17 | 19.4 | 20.9 | 659
617 | 2022-10-07 10:18 | 19.6 | 20 | 666
618 | 2022-10-07 10:19 | 19.4 | 20.8 | 668
619 | 2022-10-07 10:20 | 19.6 | 20.8 | 670
620 | 2022-10-07 10:21 | 19.5 | 20.6 | 673
621 | 2022-10-07 10:22 | 19.3 | 21.1 | 678
622 | 2022-10-07 10:23 | 19.4 | 20.3 | 681
623 | 2022-10-07 10:24 | 19.4 | 20.6 | 685
624 | 2022-10-07 10:25 | 19.7 | 20.3 | 689
625 | 2022-10-07 10:26 | 19.9 | 20.6 | 691
626 | 2022-10-07 10:27 | 19.8 | 20.7 | 694
627 | 2022-10-07 10:28 | 19.5 | 20.7 | 699
628 | 2022-10-07 10:29 | 19.7 | 20.7 | 703
629 | 2022-10-07 10:30 | 19.9 | 20.7 | 707
630 | 2022-10-07 10:31 | 19.8 | 20.9 | 708
631 | 2022-10-07 10:32 | 19.9 | 20 | 714
632 | 2022-10-07 10:33 | 20.2 | 20.3 | 716
633 | 2022-10-07 10:34 | 20.1 | 21.1 | 718
634 | 2022-10-07 10:35 | 20.3 | 21.2 | 730
635 | 2022-10-07 10:36 | 19.9 | 21.1 | 735
636 | 2022-10-07 10:37 | 19.8 | 21.2 | 729
637 | 2022-10-07 10:38 | 19.8 | 21.1 | 745
638 | 2022-10-07 10:39 | 20 | 21 | 750
639 | 2022-10-07 10:40 | 20.3 | 21.2 | 755
640 | 2022-10-07 10:41 | 20.3 | 21 | 748
641 | 2022-10-07 10:42 | 20.3 | 21.1 | 742
642 | 2022-10-07 10:43 | 20.2 | 21.1 | 739
643 | 2022-10-07 10:44 | 20.4 | 21.1 | 740
644 | 2022-10-07 10:45 | 20.5 | 21.3 | 746
645 | 2022-10-07 10:46 | 20.7 | 21.3 | 750
646 | 2022-10-07 10:47 | 20.9 | 21.3 | 755
647 | 2022-10-07 10:48 | 21.2 | 21.3 | 752
648 | 2022-10-07 10:49 | 21.1 | 21.3 | 759
649 | 2022-10-07 10:50 | 21.1 | 21.3 | 766
650 | 2022-10-07 10:51 | 20.8 | 21.3 | 767
651 | 2022-10-07 10:52 | 20.9 | 21.2 | 780
652 | 2022-10-07 10:53 | 20.8 | 21.3 | 780
653 | 2022-10-07 10:54 | 20.3 | 21.2 | 392
654 | 2022-10-07 10:55 | 20.2 | 21.1 | 793
655 | 2022-10-07 10:56 | 20.1 | 21 | 795
656 | 2022-10-07 10:57 | 19.9 | 21 | 803
657 | 2022-10-07 10:58 | 19.9 | 21 | 803
658 | 2022-10-07 10:59 | 20.2 | 21 | 801
659 | 2022-10-07 11:00 | 20.5 | 21 | 803
660 | 2022-10-07 11:01 | 20.2 | 21.1 | 804
661 | 2022-10-07 11:02 | 20.2 | 21 | 805
662 | 2022-10-07 11:03 | 20.6 | 21.2 | 806
663 | 2022-10-07 11:04 | 20.8 | 21.1 | 805
664 | 2022-10-07 11:05 | 20.8 | 21.4 | 809
665 | 2022-10-07 11:06 | 20.6 | 21.3 | 810
666 | 2022-10-07 11:07 | 21 | 21.1 | 815
667 | 2022-10-07 11:08 | 21.1 | 20.8 | 822
668 | 2022-10-07 11:09 | 20.7 | 21.2 | 820
669 | 2022-10-07 11:10 | 20.9 | 21.6 | 826
670 | 2022-10-07 11:11 | 20.8 | 21.3 | 832
671 | 2022-10-07 11:12 | 21.3 | 20.9 | 835
672 | 2022-10-07 11:13 | 21.3 | 21.1 | 839
673 | 2022-10-07 11:14 | 20.8 | 21.9 | 840
674 | 2022-10-07 11:15 | 21.2 | 20.9 | 844
675 | 2022-10-07 11:16 | 21.1 | 20.5 | 845
676 | 2022-10-07 11:17 | 21 | 21.2 | 849
677 | 2022-10-07 11:18 | 20.9 | 21.5 | 849
678 | 2022-10-07 11:19 | 20.5 | 20.5 | 853
679 | 2022-10-07 11:20 | 21 | 21.2 | 852
680 | 2022-10-07 11:21 | 21 | 21.8 | 856
681 | 2022-10-07 11:22 | 21.2 | 21.3 | 859
682 | 2022-10-07 11:23 | 21.3 | 21.2 | 862
683 | 2022-10-07 11:24 | 21.3 | 21.6 | 863
684 | 2022-10-07 11:25 | 21 | 21.5 | 869
685 | 2022-10-07 11:26 | 20.8 | 21.3 | 872
686 | 2022-10-07 11:27 | 20.8 | 21.1 | 875
687 | 2022-10-07 11:28 | 20.5 | 21.4 | 881
688 | 2022-10-07 11:29 | 20.8 | 21.4 | 881
689 | 2022-10-07 11:30 | 20.8 | 21.3 | 881
690 | 2022-10-07 11:31 | 21.3 | 21.1 | 886
691 | 2022-10-07 11:32 | 21.8 | 20.8 | 891
692 | 2022-10-07 11:33 | 21.9 | 21.4 | 893
693 | 2022-10-07 11:34 | 21.5 | 21.5 | 895
694 | 2022-10-07 11:35 | 22 | 21.3 | 897
695 | 2022-10-07 11:36 | 21.6 | 21.3 | 900
696 | 2022-10-07 11:37 | 22.2 | 21.6 | 906
697 | 2022-10-07 11:38 | 21.5 | 21.4 | 908
698 | 2022-10-07 11:39 | 21.6 | 21.5 | 907
699 | 2022-10-07 11:40 | 21.5 | 21.4 | 908
700 | 2022-10-07 11:41 | 21.6 | 21.3 | 911
701 | 2022-10-07 11:42 | 21 | 21.2 | 907
702 | 2022-10-07 11:43 | 21.4 | 21.3 | 907
703 | 2022-10-07 11:44 | 21.4 | 21.3 | 912
704 | 2022-10-07 11:45 | 21.6 | 21.5 | 912
705 | 2022-10-07 11:46 | 21.6 | 21.6 | 914
706 | 2022-10-07 11:47 | 21.8 | 21.5 | 918
707 | 2022-10-07 11:48 | 22 | 21.5 | 917
708 | 2022-10-07 11:49 | 22.5 | 21.7 | 918
709 | 2022-10-07 11:50 | 22.3 | 21.6 | 919
710 | 2022-10-07 11:51 | 21.6 | 21.6 | 925
711 | 2022-10-07 11:52 | 21.3 | 21.4 | 931
712 | 2022-10-07 11:53 | 21.6 | 21.6 | 944
713 | 2022-10-07 11:54 | 21.5 | 21.3 | 956
714 | 2022-10-07 11:55 | 21.6 | 21.5 | 953
715 | 2022-10-07 11:56 | 21.7 | 21.6 | 945
716 | 2022-10-07 11:57 | 21.4 | 21.6 | 949
717 | 2022-10-07 11:58 | 22 | 21.8 | 950
718 | 2022-10-07 11:59 | 22 | 21.4 | 956
719 | 2022-10-07 12:00 | 22 | 21.5 | 954
720 | 2022-10-07 12:01 | 21.8 | 21.5 | 955
721 | 2022-10-07 12:02 | 22 | 21.4 | 957
722 | 2022-10-07 12:03 | 21.5 | 20.9 | 967
723 | 2022-10-07 12:04 | 21.3 | 21.5 | 956
724 | 2022-10-07 12:05 | 20.9 | 21.1 | 968
725 | 2022-10-07 12:06 | 21.4 | 21.2 | 989
726 | 2022-10-07 12:07 | 21.4 | 20.9 | 996
727 | 2022-10-07 12:08 | 21.7 | 20.5 | 941
728 | 2022-10-07 12:09 | 21.6 | 21 | 972
729 | 2022-10-07 12:10 | 21.7 | 21.5 | 965
730 | 2022-10-07 12:11 | 21.7 | 21.6 | 967
731 | 2022-10-07 12:12 | 21.7 | 21.7 | 975
732 | 2022-10-07 12:13 | 21.7 | 21.4 | 973
733 | 2022-10-07 12:14 | 21.7 | 21.5 | 976
734 | 2022-10-07 12:15 | 21.4 | 21.6 | 977
735 | 2022-10-07 12:16 | 21.6 | 21.4 | 979
736 | 2022-10-07 12:17 | 21.8 | 21.6 | 978
737 | 2022-10-07 12:18 | 21.4 | 21.8 | 979
738 | 2022-10-07 12:19 | 21.4 | 21.1 | 979
739 | 2022-10-07 12:20 | 21.8 | 21.4 | 980
740 | 2022-10-07 12:21 | 21.6 | 22.2 | 981
741 | 2022-10-07 12:22 | 21.7 | 21.6 | 982
742 | 2022-10-07 12:23 | 21.5 | 21.7 | 982
743 | 2022-10-07 12:24 | 21.4 | 21.6 | 986
744 | 2022-10-07 12:25 | 21.1 | 21.4 | 987
745 | 2022-10-07 12:26 | 21.2 | 21.6 | 983
746 | 2022-10-07 12:27 | 21.2 | 21.9 | 982
747 | 2022-10-07 12:28 | 21.1 | 21.7 | 992
748 | 2022-10-07 12:29 | 21.5 | 21.8 | 990
749 | 2022-10-07 12:30 | 22 | 21.7 | 989
750 | 2022-10-07 12:31 | 21.8 | 21.6 | 991
751 | 2022-10-07 12:32 | 21.7 | 21.8 | 989
752 | 2022-10-07 12:33 | 22.3 | 22 | 987
753 | 2022-10-07 12:34 | 22.5 | 21.9 | 988
754 | 2022-10-07 12:35 | 22.5 | 21.6 | 989
755 | 2022-10-07 12:36 | 21.3 | 21.8 | 991
756 | 2022-10-07 12:37 | 21.2 | 21.8 | 990
757 | 2022-10-07 12:38 | 21.7 | 22 | 992
758 | 2022-10-07 12:39 | 22 | 22 | 994
759 | 2022-10-07 12:40 | 22.2 | 22.1 | 996
760 | 2022-10-07 12:41 | 22.1 | 22 | 997
761 | 2022-10-07 12:42 | 22.1 | 22 | 992
762 | 2022-10-07 12:43 | 21.9 | 21.8 | 997
763 | 2022-10-07 12:44 | 22.1 | 21.8 | 988
764 | 2022-10-07 12:45 | 22 | 22 | 995
765 | 2022-10-07 12:46 | 22 | 22.1 | 1000
766 | 2022-10-07 12:47 | 22.5 | 22.2 | 996
767 | 2022-10-07 12:48 | 22.7 | 22.4 | 995
768 | 2022-10-07 12:49 | 22.9 | 21.1 | 998
769 | 2022-10-07 12:50 | 22.6 | 22.1 | 999
770 | 2022-10-07 12:51 | 22.1 | 21.9 | 992
771 | 2022-10-07 12:52 | 22.2 | 22.1 | 998
772 | 2022-10-07 12:53 | 22.7 | 21.8 | 1004
773 | 2022-10-07 12:54 | 22.8 | 22 | 998
774 | 2022-10-07 12:55 | 22.4 | 21.9 | 999
775 | 2022-10-07 12:56 | 22.6 | 22.4 | 999
776 | 2022-10-07 12:57 | 22.5 | 21.8 | 1000
777 | 2022-10-07 12:58 | 22.1 | 22.7 | 996
778 | 2022-10-07 12:59 | 21.4 | 22 | 1000
779 | 2022-10-07 13:00 | 21.6 | 22.3 | 1002
780 | 2022-10-07 13:01 | 22.2 | 21.7 | 998
781 | 2022-10-07 13:02 | 22 | 21.2 | 993
782 | 2022-10-07 13:03 | 22.5 | 21.6 | 992
783 | 2022-10-07 13:04 | 22.7 | 21.8 | 1002
784 | 2022-10-07 13:05 | 23 | 21.4 | 1005
785 | 2022-10-07 13:06 | 22.6 | 21.9 | 1013
786 | 2022-10-07 13:07 | 22.2 | 21.5 | 1013
787 | 2022-10-07 13:08 | 22.1 | 22.1 | 1015
788 | 2022-10-07 13:09 | 22.5 | 21.8 | 1014
789 | 2022-10-07 13:10 | 22.9 | 22.1 | 1015
790 | 2022-10-07 13:11 | 23.3 | 22.2 | 1013
791 | 2022-10-07 13:12 | 23.7 | 22.2 | 1008
792 | 2022-10-07 13:13 | 23.3 | 21.8 | 1009
793 | 2022-10-07 13:14 | 23.7 | 22.1 | 1009
794 | 2022-10-07 13:15 | 23.7 | 22 | 1014
795 | 2022-10-07 13:16 | 23.3 | 22.5 | 1016
796 | 2022-10-07 13:17 | 22.7 | 22.1 | 1019
797 | 2022-10-07 13:18 | 22.8 | 22.6 | 831
798 | 2022-10-07 13:19 | 22.7 | 21.4 | 1031
799 | 2022-10-07 13:20 | 22.8 | 22.1 | 1024
800 | 2022-10-07 13:21 | 22.5 | 22.3 | 1023
801 | 2022-10-07 13:22 | 22.1 | 21.6 | 1014
802 | 2022-10-07 13:23 | 23 | 22.3 | 1014
803 | 2022-10-07 13:24 | 23.6 | 22.3 | 1012
804 | 2022-10-07 13:25 | 23.7 | 22.3 | 1022
805 | 2022-10-07 13:26 | 23.6 | 22.4 | 1053
806 | 2022-10-07 13:27 | 23.5 | 22.4 | 1074
807 | 2022-10-07 13:28 | 23.8 | 22.5 | 1085
808 | 2022-10-07 13:29 | 23.6 | 22.6 | 1099
809 | 2022-10-07 13:30 | 23.2 | 22.9 | 194
810 | 2022-10-07 13:31 | 23.1 | 22 | 1087
811 | 2022-10-07 13:32 | 22.8 | 22.5 | 232
812 | 2022-10-07 13:33 | 23.2 | 21.5 | 1043
813 | 2022-10-07 13:34 | 23.2 | 22 | 792
814 | 2022-10-07 13:35 | 22.7 | 22.2 | 1095
815 | 2022-10-07 13:36 | 23.3 | 21.6 | 1118
816 | 2022-10-07 13:37 | 23.4 | 21.9 | 737
817 | 2022-10-07 13:38 | 23 | 22.2 | 293
818 | 2022-10-07 13:39 | 22.6 | 23.1 | 254
819 | 2022-10-07 13:40 | 22.7 | 21.6 | 1200
820 | 2022-10-07 13:41 | 23.2 | 21.6 | 922
821 | 2022-10-07 13:42 | 23.4 | 22.4 | 1109
822 | 2022-10-07 13:43 | 23 | 22.6 | 214
823 | 2022-10-07 13:44 | 22.5 | 22.5 | 187
824 | 2022-10-07 13:45 | 22.2 | 22.5 | 210
825 | 2022-10-07 13:46 | 22.2 | 23.2 | 225
826 | 2022-10-07 13:47 | 21.7 | 23.3 | 239
827 | 2022-10-07 13:48 | 21.5 | 22.2 | 447
828 | 2022-10-07 13:49 | 21.3 | 22.1 | 264
829 | 2022-10-07 13:50 | 21.3 | 22.4 | 286
830 | 2022-10-07 13:51 | 21.4 | 21.8 | 284
831 | 2022-10-07 13:52 | 21.7 | 22.3 | 337
832 | 2022-10-07 13:53 | 21.7 | 21.9 | 273
833 | 2022-10-07 13:54 | 21.5 | 22 | 215
834 | 2022-10-07 13:55 | 21.3 | 21.9 | 227
835 | 2022-10-07 13:56 | 21.3 | 22.3 | 243
836 | 2022-10-07 13:57 | 21.1 | 22.1 | 349
837 | 2022-10-07 13:58 | 21.1 | 22.2 | 758
838 | 2022-10-07 13:59 | 21.1 | 22.1 | 295
839 | 2022-10-07 14:00 | 21.2 | 21.9 | 255
840 | 2022-10-07 14:01 | 21.1 | 22.1 | 253
841 | 2022-10-07 14:02 | 21.1 | 21.8 | 225
842 | 2022-10-07 14:03 | 21 | 22.9 | 197
843 | 2022-10-07 14:04 | 20.9 | 22.1 | 174
844 | 2022-10-07 14:05 | 20.8 | 21.8 | 183
845 | 2022-10-07 14:06 | 20.8 | 21.7 | 199
846 | 2022-10-07 14:07 | 20.8 | 22.3 | 934
847 | 2022-10-07 14:08 | 20.9 | 21.5 | 214
848 | 2022-10-07 14:09 | 20.8 | 22.7 | 205
849 | 2022-10-07 14:10 | 20.7 | 22.6 | 201
850 | 2022-10-07 14:11 | 20.7 | 22.3 | 177
851 | 2022-10-07 14:12 | 20.7 | 22 | 182
852 | 2022-10-07 14:13 | 20.6 | 22.1 | 175
853 | 2022-10-07 14:14 | 20.8 | 22.7 | 178
854 | 2022-10-07 14:15 | 20.8 | 22.8 | 209
855 | 2022-10-07 14:16 | 20.7 | 22 | 369
856 | 2022-10-07 14:17 | 20.7 | 21.1 | 1141
857 | 2022-10-07 14:18 | 21 | 22.4 | 696
858 | 2022-10-07 14:19 | 21.2 | 21.8 | 1052
859 | 2022-10-07 14:20 | 21.2 | 21.8 | 227
860 | 2022-10-07 14:21 | 21.3 | 22.2 | 192
861 | 2022-10-07 14:22 | 21.2 | 21.7 | 724
862 | 2022-10-07 14:23 | 21.1 | 21.5 | 277
863 | 2022-10-07 14:24 | 21.1 | 21.9 | 366
864 | 2022-10-07 14:25 | 21.2 | 21.7 | 265
865 | 2022-10-07 14:26 | 21.6 | 22 | 1031
866 | 2022-10-07 14:27 | 21.9 | 21.9 | 1024
867 | 2022-10-07 14:28 | 21.9 | 22.2 | 1014
868 | 2022-10-07 14:29 | 22.3 | 21.7 | 1057
869 | 2022-10-07 14:30 | 22.1 | 22.2 | 678
870 | 2022-10-07 14:31 | 21.8 | 22.4 | 1034
871 | 2022-10-07 14:32 | 22.2 | 22.5 | 1020
872 | 2022-10-07 14:33 | 22.5 | 22.4 | 1046
873 | 2022-10-07 14:34 | 22.8 | 22 | 1063
874 | 2022-10-07 14:35 | 22.6 | 21.4 | 626
875 | 2022-10-07 14:36 | 21.8 | 21.8 | 215
876 | 2022-10-07 14:37 | 21.6 | 22.1 | 1092
877 | 2022-10-07 14:38 | 21.5 | 22.2 | 338
878 | 2022-10-07 14:39 | 21.4 | 22.1 | 526
879 | 2022-10-07 14:40 | 21.3 | 21.7 | 302
880 | 2022-10-07 14:41 | 21.3 | 22.1 | 264
881 | 2022-10-07 14:42 | 21.6 | 22.2 | 285
882 | 2022-10-07 14:43 | 21.6 | 22.2 | 260
883 | 2022-10-07 14:44 | 21.7 | 21.7 | 169
884 | 2022-10-07 14:45 | 21.5 | 22.6 | 166
885 | 2022-10-07 14:46 | 21.4 | 22.2 | 183
886 | 2022-10-07 14:47 | 21.2 | 21.6 | 207
887 | 2022-10-07 14:48 | 21.1 | 21 | 363
888 | 2022-10-07 14:49 | 21 | 21.8 | 203
889 | 2022-10-07 14:50 | 21 | 22 | 243
890 | 2022-10-07 14:51 | 21.3 | 22.1 | 815
891 | 2022-10-07 14:52 | 21 | 22 | 292
892 | 2022-10-07 14:53 | 21.1 | 21.8 | 232
893 | 2022-10-07 14:54 | 21.1 | 21.8 | 558
894 | 2022-10-07 14:55 | 20.9 | 22 | 210
895 | 2022-10-07 14:56 | 20.9 | 22 | 213
896 | 2022-10-07 14:57 | 20.7 | 22.1 | 221
897 | 2022-10-07 14:58 | 20.9 | 21.9 | 244
898 | 2022-10-07 14:59 | 20.7 | 22 | 207
899 | 2022-10-07 15:00 | 20.7 | 22.8 | 209
900 | 2022-10-07 15:01 | 20.7 | 22.5 | 214
901 | 2022-10-07 15:02 | 20.9 | 22 | 265
902 | 2022-10-07 15:03 | 20.9 | 22 | 192
903 | 2022-10-07 15:04 | 21 | 22.3 | 201
904 | 2022-10-07 15:05 | 20.7 | 22.3 | 242
905 | 2022-10-07 15:06 | 20.6 | 22.1 | 219
906 | 2022-10-07 15:07 | 20.7 | 22.9 | 193
907 | 2022-10-07 15:08 | 20.9 | 21.3 | 163
908 | 2022-10-07 15:09 | 20.8 | 22.5 | 150
909 | 2022-10-07 15:10 | 20.7 | 21.8 | 150
910 | 2022-10-07 15:11 | 20.2 | 22.5 | 158
911 | 2022-10-07 15:12 | 20.3 | 22.2 | 161
912 | 2022-10-07 15:13 | 20.5 | 22.6 | 161
913 | 2022-10-07 15:14 | 20.5 | 21.8 | 163
914 | 2022-10-07 15:15 | 20.4 | 21 | 772
915 | 2022-10-07 15:16 | 20.6 | 21.7 | 145
916 | 2022-10-07 15:17 | 20.7 | 21.1 | 132
917 | 2022-10-07 15:18 | 20.4 | 22.1 | 135
918 | 2022-10-07 15:19 | 20.2 | 22.1 | 149
919 | 2022-10-07 15:20 | 20.2 | 22.1 | 143
920 | 2022-10-07 15:21 | 20.2 | 21.7 | 118
921 | 2022-10-07 15:22 | 20.1 | 21.9 | 104
922 | 2022-10-07 15:23 | 20.1 | 21.9 | 101
923 | 2022-10-07 15:24 | 20.1 | 22 | 104
924 | 2022-10-07 15:25 | 20 | 22 | 104
925 | 2022-10-07 15:26 | 19.9 | 22.2 | 104
926 | 2022-10-07 15:27 | 19.9 | 22 | 107
927 | 2022-10-07 15:28 | 19.9 | 22.2 | 118
928 | 2022-10-07 15:29 | 20 | 21.6 | 133
929 | 2022-10-07 15:30 | 20.1 | 22.7 | 156
930 | 2022-10-07 15:31 | 20.2 | 22.2 | 180
931 | 2022-10-07 15:32 | 20 | 22.5 | 155
932 | 2022-10-07 15:33 | 19.9 | 21.9 | 150
933 | 2022-10-07 15:34 | 19.8 | 21.8 | 129
934 | 2022-10-07 15:35 | 19.8 | 22.1 | 122
935 | 2022-10-07 15:36 | 19.6 | 22.7 | 142
936 | 2022-10-07 15:37 | 19.6 | 22 | 181
937 | 2022-10-07 15:38 | 19.7 | 22.4 | 205
938 | 2022-10-07 15:39 | 19.7 | 21.5 | 175
939 | 2022-10-07 15:40 | 19.6 | 21.3 | 173
940 | 2022-10-07 15:41 | 19.7 | 22.1 | 211
941 | 2022-10-07 15:42 | 20 | 22.2 | 233
942 | 2022-10-07 15:43 | 20.2 | 23.2 | 219
943 | 2022-10-07 15:44 | 20 | 22.5 | 190
944 | 2022-10-07 15:45 | 20.2 | 21.9 | 165
945 | 2022-10-07 15:46 | 20.1 | 21.9 | 163
946 | 2022-10-07 15:47 | 19.9 | 21.9 | 168
947 | 2022-10-07 15:48 | 19.8 | 21.5 | 164
948 | 2022-10-07 15:49 | 19.8 | 22.3 | 186
949 | 2022-10-07 15:50 | 20 | 22.7 | 137
950 | 2022-10-07 15:51 | 19.8 | 22.1 | 123
951 | 2022-10-07 15:52 | 19.8 | 21.7 | 130
952 | 2022-10-07 15:53 | 19.8 | 21.9 | 138
953 | 2022-10-07 15:54 | 19.6 | 22.7 | 139
954 | 2022-10-07 15:55 | 19.7 | 22.1 | 128
955 | 2022-10-07 15:56 | 19.5 | 21.2 | 126
956 | 2022-10-07 15:57 | 19.5 | 21.4 | 109
957 | 2022-10-07 15:58 | 19.6 | 21.5 | 98
958 | 2022-10-07 15:59 | 19.6 | 21.7 | 91
959 | 2022-10-07 16:00 | 19.5 | 21.9 | 98
960 | 2022-10-07 16:01 | 19.3 | 21.8 | 117
961 | 2022-10-07 16:02 | 19.3 | 22 | 131
962 | 2022-10-07 16:03 | 19.5 | 21.8 | 131
963 | 2022-10-07 16:04 | 19.4 | 21.9 | 154
964 | 2022-10-07 16:05 | 19.5 | 22 | 166
965 | 2022-10-07 16:06 | 19.6 | 22 | 192
966 | 2022-10-07 16:07 | 19.8 | 22.3 | 183
967 | 2022-10-07 16:08 | 19.5 | 22.5 | 168
968 | 2022-10-07 16:09 | 19.7 | 21.9 | 156
969 | 2022-10-07 16:10 | 19.6 | 22.2 | 144
970 | 2022-10-07 16:11 | 19.6 | 22.9 | 139
971 | 2022-10-07 16:12 | 19.4 | 22.3 | 155
972 | 2022-10-07 16:13 | 19.7 | 21.8 | 138
973 | 2022-10-07 16:14 | 19.5 | 22.4 | 148
974 | 2022-10-07 16:15 | 19.7 | 21.5 | 155
975 | 2022-10-07 16:16 | 19.6 | 21.3 | 166
976 | 2022-10-07 16:17 | 19.6 | 22 | 178
977 | 2022-10-07 16:18 | 19.9 | 22 | 402
978 | 2022-10-07 16:19 | 20.3 | 22 | 706
979 | 2022-10-07 16:20 | 20.2 | 22.6 | 205
980 | 2022-10-07 16:21 | 20 | 22.4 | 208
981 | 2022-10-07 16:22 | 20 | 21.9 | 340
982 | 2022-10-07 16:23 | 20.4 | 21.6 | 715
983 | 2022-10-07 16:24 | 20.7 | 21.6 | 704
984 | 2022-10-07 16:25 | 20.4 | 21.5 | 697
985 | 2022-10-07 16:26 | 20.1 | 22.3 | 201
986 | 2022-10-07 16:27 | 20.2 | 21.9 | 669
987 | 2022-10-07 16:28 | 20.2 | 21 | 671
988 | 2022-10-07 16:29 | 20.5 | 21 | 653
989 | 2022-10-07 16:30 | 20.7 | 20.8 | 452
990 | 2022-10-07 16:31 | 20.7 | 21.9 | 662
991 | 2022-10-07 16:32 | 21 | 21.8 | 666
992 | 2022-10-07 16:33 | 21.2 | 22.1 | 680
993 | 2022-10-07 16:34 | 21.1 | 21.6 | 685
994 | 2022-10-07 16:35 | 21.1 | 21.6 | 670
995 | 2022-10-07 16:36 | 21.2 | 22.7 | 647
996 | 2022-10-07 16:37 | 20.9 | 22.2 | 175
997 | 2022-10-07 16:38 | 21.1 | 22.4 | 684
998 | 2022-10-07 16:39 | 21.1 | 22.2 | 668
999 | 2022-10-07 16:40 | 21.4 | 22.1 | 645
1000 | 2022-10-07 16:41 | 21.5 | 22.3 | 628
1001 | 2022-10-07 16:42 | 21.8 | 22.6 | 617
1002 | 2022-10-07 16:43 | 21.6 | 22 | 607
1003 | 2022-10-07 16:44 | 21.6 | 21.9 | 606
1004 | 2022-10-07 16:45 | 21.4 | 22.4 | 603
1005 | 2022-10-07 16:46 | 21.3 | 22.4 | 598
1006 | 2022-10-07 16:47 | 21.4 | 22.2 | 583
1007 | 2022-10-07 16:48 | 21.8 | 22.5 | 574
1008 | 2022-10-07 16:49 | 21.9 | 21.7 | 560
1009 | 2022-10-07 16:50 | 21.9 | 22.4 | 549
1010 | 2022-10-07 16:51 | 22 | 22.3 | 537
1011 | 2022-10-07 16:52 | 21.9 | 22.1 | 532
1012 | 2022-10-07 16:53 | 21.6 | 21.9 | 526
1013 | 2022-10-07 16:54 | 21.7 | 22.3 | 526
1014 | 2022-10-07 16:55 | 21.6 | 21.4 | 525
1015 | 2022-10-07 16:56 | 21.5 | 22.7 | 533
1016 | 2022-10-07 16:57 | 21.4 | 22 | 528
1017 | 2022-10-07 16:58 | 21.8 | 22.6 | 520
1018 | 2022-10-07 16:59 | 21.9 | 22.7 | 511
1019 | 2022-10-07 17:00 | 21.6 | 21.8 | 501
1020 | 2022-10-07 17:01 | 21.3 | 22.6 | 488
1021 | 2022-10-07 17:02 | 21.3 | 22.4 | 481
1022 | 2022-10-07 17:03 | 21.2 | 22.4 | 476
1023 | 2022-10-07 17:04 | 20.9 | 22.1 | 478
1024 | 2022-10-07 17:05 | 21 | 22 | 482
1025 | 2022-10-07 17:06 | 21.1 | 22.3 | 484
1026 | 2022-10-07 17:07 | 21 | 21.8 | 476
1027 | 2022-10-07 17:08 | 20.8 | 22.4 | 463
1028 | 2022-10-07 17:09 | 21.1 | 22.4 | 457
1029 | 2022-10-07 17:10 | 21 | 21.9 | 456
1030 | 2022-10-07 17:11 | 20.7 | 22.2 | 442
1031 | 2022-10-07 17:12 | 20.8 | 22.3 | 434
1032 | 2022-10-07 17:13 | 20.7 | 23 | 428
1033 | 2022-10-07 17:14 | 20.8 | 23.5 | 419
1034 | 2022-10-07 17:15 | 20.8 | 22.8 | 414
1035 | 2022-10-07 17:16 | 20.6 | 23.4 | 415
1036 | 2022-10-07 17:17 | 20.7 | 23.8 | 411
1037 | 2022-10-07 17:18 | 20.9 | 22.6 | 408
1038 | 2022-10-07 17:19 | 20.8 | 22.7 | 406
1039 | 2022-10-07 17:20 | 20.9 | 22.3 | 401
1040 | 2022-10-07 17:21 | 20.6 | 23.6 | 396
1041 | 2022-10-07 17:22 | 20.7 | 23 | 391
1042 | 2022-10-07 17:23 | 20.8 | 22.7 | 387
1043 | 2022-10-07 17:24 | 20.5 | 23.2 | 381
1044 | 2022-10-07 17:25 | 20.8 | 22.6 | 376
1045 | 2022-10-07 17:26 | 20.8 | 23.1 | 371
1046 | 2022-10-07 17:27 | 20.9 | 22.9 | 367
1047 | 2022-10-07 17:28 | 20.7 | 23 | 364
1048 | 2022-10-07 17:29 | 20.5 | 23 | 357
1049 | 2022-10-07 17:30 | 20.4 | 22.6 | 356
1050 | 2022-10-07 17:31 | 20.5 | 22.7 | 350
1051 | 2022-10-07 17:32 | 20.6 | 22.1 | 345
1052 | 2022-10-07 17:33 | 20.3 | 23 | 337
1053 | 2022-10-07 17:34 | 20.2 | 22.9 | 333
1054 | 2022-10-07 17:35 | 20.2 | 22.9 | 330
1055 | 2022-10-07 17:36 | 20.2 | 23 | 326
1056 | 2022-10-07 17:37 | 20.2 | 23.1 | 323
1057 | 2022-10-07 17:38 | 20.5 | 22.9 | 316
1058 | 2022-10-07 17:39 | 20.4 | 23 | 310
1059 | 2022-10-07 17:40 | 20.4 | 23 | 306
1060 | 2022-10-07 17:41 | 20.1 | 23.1 | 301
1061 | 2022-10-07 17:42 | 20.2 | 23 | 299
1062 | 2022-10-07 17:43 | 20.2 | 23 | 292
1063 | 2022-10-07 17:44 | 20.1 | 22.8 | 287
1064 | 2022-10-07 17:45 | 20.2 | 23.2 | 281
1065 | 2022-10-07 17:46 | 20.2 | 23 | 277
1066 | 2022-10-07 17:47 | 19.9 | 23.1 | 272
1067 | 2022-10-07 17:48 | 19.7 | 22.8 | 270
1068 | 2022-10-07 17:49 | 20 | 22.9 | 265
1069 | 2022-10-07 17:50 | 19.9 | 23 | 260
1070 | 2022-10-07 17:51 | 20 | 22.8 | 256
1071 | 2022-10-07 17:52 | 19.8 | 23.5 | 252
1072 | 2022-10-07 17:53 | 19.7 | 23 | 249
1073 | 2022-10-07 17:54 | 20 | 22.5 | 243
1074 | 2022-10-07 17:55 | 19.8 | 22.9 | 238
1075 | 2022-10-07 17:56 | 19.8 | 22.8 | 235
1076 | 2022-10-07 17:57 | 19.9 | 23.4 | 229
1077 | 2022-10-07 17:58 | 19.7 | 23.4 | 225
1078 | 2022-10-07 17:59 | 19.8 | 23.4 | 220
1079 | 2022-10-07 18:00 | 19.8 | 23.2 | 214
1080 | 2022-10-07 18:01 | 19.8 | 23.1 | 210
1081 | 2022-10-07 18:02 | 19.8 | 22.8 | 205
1082 | 2022-10-07 18:03 | 19.6 | 22.6 | 200
1083 | 2022-10-07 18:04 | 19.7 | 22.5 | 196
1084 | 2022-10-07 18:05 | 19.6 | 22.8 | 192
1085 | 2022-10-07 18:06 | 19.5 | 22.7 | 190
1086 | 2022-10-07 18:07 | 19.6 | 22.7 | 187
1087 | 2022-10-07 18:08 | 19.5 | 22.6 | 181
1088 | 2022-10-07 18:09 | 19.6 | 22.7 | 178
1089 | 2022-10-07 18:10 | 19.5 | 22.7 | 172
1090 | 2022-10-07 18:11 | 19.5 | 22.7 | 168
1091 | 2022-10-07 18:12 | 19.3 | 22.9 | 161
1092 | 2022-10-07 18:13 | 19.3 | 22.7 | 157
1093 | 2022-10-07 18:14 | 19.6 | 22.6 | 151
1094 | 2022-10-07 18:15 | 19.5 | 22.9 | 146
1095 | 2022-10-07 18:16 | 19.2 | 22.6 | 141
1096 | 2022-10-07 18:17 | 19.3 | 22.3 | 134
1097 | 2022-10-07 18:18 | 19.2 | 21.8 | 129
1098 | 2022-10-07 18:19 | 19.3 | 22.6 | 124
1099 | 2022-10-07 18:20 | 19.3 | 22.6 | 119
1100 | 2022-10-07 18:21 | 19.2 | 22.5 | 116
1101 | 2022-10-07 18:22 | 19.1 | 22.5 | 112
1102 | 2022-10-07 18:23 | 19.1 | 23 | 108
1103 | 2022-10-07 18:24 | 19 | 22.6 | 106
1104 | 2022-10-07 18:25 | 19.1 | 22.8 | 102
1105 | 2022-10-07 18:26 | 19 | 22.7 | 98
1106 | 2022-10-07 18:27 | 18.9 | 22.7 | 93
1107 | 2022-10-07 18:28 | 19 | 22.9 | 90
1108 | 2022-10-07 18:29 | 19 | 22.5 | 86
1109 | 2022-10-07 18:30 | 18.9 | 22.6 | 81
1110 | 2022-10-07 18:31 | 18.8 | 21.9 | 75
1111 | 2022-10-07 18:32 | 18.7 | 23 | 67
1112 | 2022-10-07 18:33 | 18.6 | 22.4 | 68
1113 | 2022-10-07 18:34 | 18.6 | 22.9 | 61
1114 | 2022-10-07 18:35 | 18.7 | 23.1 | 44
1115 | 2022-10-07 18:36 | 18.7 | 22.6 | 34
1116 | 2022-10-07 18:37 | 18.5 | 22.5 | 30
1117 | 2022-10-07 18:38 | 18.4 | 22.5 | 21
1118 | 2022-10-07 18:39 | 18.4 | 22.5 | 17
1119 | 2022-10-07 18:40 | 18.5 | 22.8 | 17
1120 | 2022-10-07 18:41 | 18.5 | 22.5 | 16
1121 | 2022-10-07 18:42 | 18.4 | 22.5 | 15
1122 | 2022-10-07 18:43 | 18.5 | 22.6 | 13
1123 | 2022-10-07 18:44 | 18.5 | 22.6 | 12
1124 | 2022-10-07 18:45 | 18.3 | 22.6 | 12
1125 | 2022-10-07 18:46 | 18.3 | 22.8 | 11
1126 | 2022-10-07 18:47 | 18.3 | 22.7 | 10
1127 | 2022-10-07 18:48 | 18.2 | 22.6 | 9
1128 | 2022-10-07 18:49 | 18.4 | 22.4 | 9
1129 | 2022-10-07 18:50 | 18.3 | 22.6 | 8
1130 | 2022-10-07 18:51 | 18.3 | 22.3 | 7
1131 | 2022-10-07 18:52 | 18.3 | 22.5 | 6
1132 | 2022-10-07 18:53 | 18.1 | 22.5 | 6
1133 | 2022-10-07 18:54 | 18.2 | 22.7 | 5
1134 | 2022-10-07 18:55 | 18.1 | 22.8 | 4
1135 | 2022-10-07 18:56 | 18.1 | 22.6 | 4
1136 | 2022-10-07 18:57 | 18.2 | 22.4 | 3
1137 | 2022-10-07 18:58 | 18.1 | 22.3 | 2
1138 | 2022-10-07 18:59 | 18.1 | 22.9 | 2
1139 | 2022-10-07 19:00 | 18.1 | 23.1 | 1
1140 | 2022-10-07 19:01 | 18.1 | 22.4 | 1
1141 | 2022-10-07 19:02 | 18 | 22.6 | 0
1142 | 2022-10-07 19:03 | 18.1 | 22.6 | 0
1143 | 2022-10-07 19:04 | 18.1 | 22.4 | 0
1144 | 2022-10-07 19:05 | 18 | 22.4 | 0
1145 | 2022-10-07 19:06 | 18.1 | 22.6 | 0
1146 | 2022-10-07 19:07 | 17.9 | 22.3 | 0
1147 | 2022-10-07 19:08 | 18 | 22.6 | 0
1148 | 2022-10-07 19:09 | 18 | 22.5 | 0
1149 | 2022-10-07 19:10 | 17.9 | 22.6 | 0
1150 | 2022-10-07 19:11 | 17.9 | 23 | 0
1151 | 2022-10-07 19:12 | 18 | 21.9 | 0
1152 | 2022-10-07 19:13 | 17.9 | 22.8 | 0
1153 | 2022-10-07 19:14 | 17.9 | 22.6 | 0
1154 | 2022-10-07 19:15 | 17.8 | 22.6 | 0
1155 | 2022-10-07 19:16 | 17.9 | 22.6 | 0
1156 | 2022-10-07 19:17 | 17.8 | 22.4 | 0
1157 | 2022-10-07 19:18 | 17.8 | 22.3 | 0
1158 | 2022-10-07 19:19 | 17.7 | 22.3 | 0
1159 | 2022-10-07 19:20 | 17.8 | 22.5 | 0
1160 | 2022-10-07 19:21 | 17.8 | 22.7 | 0
1161 | 2022-10-07 19:22 | 17.5 | 22.6 | 0
1162 | 2022-10-07 19:23 | 17.7 | 22.5 | 0
1163 | 2022-10-07 19:24 | 17.6 | 21.9 | 0
1164 | 2022-10-07 19:25 | 17.5 | 22.5 | 0
1165 | 2022-10-07 19:26 | 17.4 | 22.5 | 0
1166 | 2022-10-07 19:27 | 17.6 | 22.3 | 0
1167 | 2022-10-07 19:28 | 17.6 | 22.8 | 0
1168 | 2022-10-07 19:29 | 17.6 | 22.6 | 0
1169 | 2022-10-07 19:30 | 17.4 | 22.5 | 0
1170 | 2022-10-07 19:31 | 17.3 | 22.5 | 0
1171 | 2022-10-07 19:32 | 17.4 | 22.4 | 0
1172 | 2022-10-07 19:33 | 17.5 | 22.5 | 0
1173 | 2022-10-07 19:34 | 17.5 | 22.5 | 0
1174 | 2022-10-07 19:35 | 17.5 | 22.6 | 0
1175 | 2022-10-07 19:36 | 17.5 | 22.6 | 0
1176 | 2022-10-07 19:37 | 17.5 | 22.6 | 0
1177 | 2022-10-07 19:38 | 17.5 | 22.4 | 0
1178 | 2022-10-07 19:39 | 17.5 | 22.5 | 0
1179 | 2022-10-07 19:40 | 17.6 | 22.3 | 0
1180 | 2022-10-07 19:41 | 17.6 | 22.3 | 0
1181 | 2022-10-07 19:42 | 17.5 | 22.6 | 0
1182 | 2022-10-07 19:43 | 17.3 | 22.5 | 0
1183 | 2022-10-07 19:44 | 17.3 | 22.5 | 0
1184 | 2022-10-07 19:45 | 17.2 | 22.5 | 0
1185 | 2022-10-07 19:46 | 17.1 | 22.4 | 0
1186 | 2022-10-07 19:47 | 17 | 22.3 | 0
1187 | 2022-10-07 19:48 | 17 | 22.3 | 0
1188 | 2022-10-07 19:49 | 17.1 | 22.5 | 0
1189 | 2022-10-07 19:50 | 17.1 | 22.5 | 0
1190 | 2022-10-07 19:51 | 17.2 | 22.3 | 0
1191 | 2022-10-07 19:52 | 17.2 | 22.4 | 0
1192 | 2022-10-07 19:53 | 17.3 | 22.3 | 0
1193 | 2022-10-07 19:54 | 17.1 | 22.4 | 0
1194 | 2022-10-07 19:55 | 17 | 22.6 | 0
1195 | 2022-10-07 19:56 | 17.1 | 22.3 | 0
1196 | 2022-10-07 19:57 | 17.1 | 22.4 | 0
1197 | 2022-10-07 19:58 | 17.4 | 22.3 | 0
1198 | 2022-10-07 19:59 | 17.4 | 22.3 | 0
1199 | 2022-10-07 20:00 | 17.2 | 22 | 0
1200 | 2022-10-07 20:01 | 17 | 21.6 | 0
1201 | 2022-10-07 20:02 | 16.7 | 22.6 | 0
1202 | 2022-10-07 20:03 | 16.6 | 22.4 | 0
1203 | 2022-10-07 20:04 | 16.3 | 22.6 | 0
1204 | 2022-10-07 20:05 | 16.5 | 22.3 | 0
1205 | 2022-10-07 20:06 | 16.5 | 22.3 | 0
1206 | 2022-10-07 20:07 | 16.6 | 22.3 | 0
1207 | 2022-10-07 20:08 | 16.4 | 22.4 | 0
1208 | 2022-10-07 20:09 | 16.4 | 22.4 | 0
1209 | 2022-10-07 20:10 | 16.2 | 22.6 | 0
1210 | 2022-10-07 20:11 | 16.4 | 21.9 | 0
1211 | 2022-10-07 20:12 | 16.2 | 22.2 | 0
1212 | 2022-10-07 20:13 | 16.5 | 21.7 | 0
1213 | 2022-10-07 20:14 | 16.6 | 22 | 0
1214 | 2022-10-07 20:15 | 16.9 | 22.1 | 0
1215 | 2022-10-07 20:16 | 16.7 | 22 | 0
1216 | 2022-10-07 20:17 | 16.6 | 22.2 | 0
1217 | 2022-10-07 20:18 | 16.8 | 23 | 0
1218 | 2022-10-07 20:19 | 16.6 | 22 | 0
1219 | 2022-10-07 20:20 | 16.6 | 22.9 | 0
1220 | 2022-10-07 20:21 | 16.8 | 22.4 | 0
1221 | 2022-10-07 20:22 | 16.7 | 22.9 | 0
1222 | 2022-10-07 20:23 | 16.5 | 22.5 | 0
1223 | 2022-10-07 20:24 | 16.4 | 22.5 | 0
1224 | 2022-10-07 20:25 | 16.5 | 22 | 0
1225 | 2022-10-07 20:26 | 16.6 | 21.5 | 0
1226 | 2022-10-07 20:27 | 16.5 | 21.7 | 0
1227 | 2022-10-07 20:28 | 16.3 | 22.5 | 0
1228 | 2022-10-07 20:29 | 16.4 | 22.8 | 0
1229 | 2022-10-07 20:30 | 16.6 | 22.1 | 0
1230 | 2022-10-07 20:31 | 16.7 | 23 | 0
1231 | 2022-10-07 20:32 | 16.8 | 21.7 | 0
1232 | 2022-10-07 20:33 | 16.8 | 22.4 | 0
1233 | 2022-10-07 20:34 | 16.7 | 22.4 | 0
1234 | 2022-10-07 20:35 | 16.8 | 23 | 0
1235 | 2022-10-07 20:36 | 16.7 | 22.1 | 0
1236 | 2022-10-07 20:37 | 16.4 | 22.4 | 0
1237 | 2022-10-07 20:38 | 16.4 | 22.7 | 0
1238 | 2022-10-07 20:39 | 16.2 | 23 | 0
1239 | 2022-10-07 20:40 | 16.3 | 22.2 | 0
1240 | 2022-10-07 20:41 | 16.6 | 22.4 | 0
1241 | 2022-10-07 20:42 | 16.6 | 22.8 | 0
1242 | 2022-10-07 20:43 | 16.9 | 22.2 | 0
1243 | 2022-10-07 20:44 | 17.1 | 22.6 | 0
1244 | 2022-10-07 20:45 | 17.1 | 22.1 | 0
1245 | 2022-10-07 20:46 | 17 | 22.2 | 0
1246 | 2022-10-07 20:47 | 16.9 | 22.3 | 0
1247 | 2022-10-07 20:48 | 17.2 | 22.4 | 0
1248 | 2022-10-07 20:49 | 17 | 22.1 | 0
1249 | 2022-10-07 20:50 | 17.3 | 22.8 | 0
1250 | 2022-10-07 20:51 | 17 | 21.8 | 0
1251 | 2022-10-07 20:52 | 17.1 | 22.6 | 0
1252 | 2022-10-07 20:53 | 16.9 | 22.1 | 0
1253 | 2022-10-07 20:54 | 17.1 | 22.5 | 0
1254 | 2022-10-07 20:55 | 17.2 | 22.2 | 0
1255 | 2022-10-07 20:56 | 17.1 | 22.3 | 0
1256 | 2022-10-07 20:57 | 17 | 22.2 | 0
1257 | 2022-10-07 20:58 | 17.2 | 22.3 | 0
1258 | 2022-10-07 20:59 | 17.3 | 23 | 0
1259 | 2022-10-07 21:00 | 17.3 | 22.6 | 0
1260 | 2022-10-07 21:01 | 17.4 | 22.3 | 0
1261 | 2022-10-07 21:02 | 17.2 | 22.5 | 0
1262 | 2022-10-07 21:03 | 17.2 | 22.4 | 0
1263 | 2022-10-07 21:04 | 17.2 | 22.5 | 0
1264 | 2022-10-07 21:05 | 17.5 | 22.5 | 0
1265 | 2022-10-07 21:06 | 17.4 | 22.4 | 0
1266 | 2022-10-07 21:07 | 17.4 | 21.5 | 0
1267 | 2022-10-07 21:08 | 17.5 | 21.6 | 0
1268 | 2022-10-07 21:09 | 17.4 | 22.6 | 0
1269 | 2022-10-07 21:10 | 17.5 | 22.1 | 0
1270 | 2022-10-07 21:11 | 17.2 | 22.2 | 0
1271 | 2022-10-07 21:12 | 17.2 | 22.1 | 0
1272 | 2022-10-07 21:13 | 17.4 | 22.6 | 0
1273 | 2022-10-07 21:14 | 17.3 | 22.4 | 0
1274 | 2022-10-07 21:15 | 17.3 | 22.3 | 0
1275 | 2022-10-07 21:16 | 17.1 | 22.5 | 0
1276 | 2022-10-07 21:17 | 17 | 22.7 | 0
1277 | 2022-10-07 21:18 | 16.8 | 22.5 | 0
1278 | 2022-10-07 21:19 | 16.9 | 23.1 | 0
1279 | 2022-10-07 21:20 | 17.2 | 22 | 0
1280 | 2022-10-07 21:21 | 17.2 | 22.5 | 0
1281 | 2022-10-07 21:22 | 17.2 | 21.4 | 0
1282 | 2022-10-07 21:23 | 17.4 | 22.6 | 0
1283 | 2022-10-07 21:24 | 17.4 | 22.5 | 0
1284 | 2022-10-07 21:25 | 17.4 | 22.4 | 0
1285 | 2022-10-07 21:26 | 17.4 | 22.1 | 0
1286 | 2022-10-07 21:27 | 17.3 | 22.2 | 0
1287 | 2022-10-07 21:28 | 17.4 | 22.5 | 0
1288 | 2022-10-07 21:29 | 17.3 | 22.4 | 0
1289 | 2022-10-07 21:30 | 17.2 | 22.2 | 0
1290 | 2022-10-07 21:31 | 17.5 | 22.1 | 0
1291 | 2022-10-07 21:32 | 17.4 | 22.2 | 0
1292 | 2022-10-07 21:33 | 17.1 | 22.5 | 0
1293 | 2022-10-07 21:34 | 17.1 | 21.7 | 0
1294 | 2022-10-07 21:35 | 17.2 | 21.7 | 0
1295 | 2022-10-07 21:36 | 17.2 | 22.3 | 0
1296 | 2022-10-07 21:37 | 17.3 | 22.3 | 0
1297 | 2022-10-07 21:38 | 17.3 | 22.4 | 0
1298 | 2022-10-07 21:39 | 17.4 | 22.4 | 0
1299 | 2022-10-07 21:40 | 17.4 | 22.6 | 0
1300 | 2022-10-07 21:41 | 17.3 | 22.5 | 0
1301 | 2022-10-07 21:42 | 17.2 | 22.1 | 0
1302 | 2022-10-07 21:43 | 17.5 | 22.4 | 0
1303 | 2022-10-07 21:44 | 17.5 | 22.4 | 0
1304 | 2022-10-07 21:45 | 17.6 | 22.3 | 0
1305 | 2022-10-07 21:46 | 17.5 | 22.1 | 0
1306 | 2022-10-07 21:47 | 17.5 | 21.8 | 0
1307 | 2022-10-07 21:48 | 17.5 | 22.4 | 0
1308 | 2022-10-07 21:49 | 17.6 | 22.6 | 0
1309 | 2022-10-07 21:50 | 17.3 | 22.6 | 0
1310 | 2022-10-07 21:51 | 17.5 | 22 | 0
1311 | 2022-10-07 21:52 | 17.6 | 22.3 | 0
1312 | 2022-10-07 21:53 | 17.4 | 22.2 | 0
1313 | 2022-10-07 21:54 | 17.5 | 22.3 | 0
1314 | 2022-10-07 21:55 | 17.5 | 22.3 | 0
1315 | 2022-10-07 21:56 | 17.4 | 22.4 | 0
1316 | 2022-10-07 21:57 | 17.5 | 22.3 | 0
1317 | 2022-10-07 21:58 | 17.5 | 22.2 | 0
1318 | 2022-10-07 21:59 | 17.5 | 22.1 | 0
1319 | 2022-10-07 22:00 | 17.3 | 22.2 | 0
1320 | 2022-10-07 22:01 | 17.2 | 22.3 | 0
1321 | 2022-10-07 22:02 | 17.3 | 22.3 | 0
1322 | 2022-10-07 22:03 | 17.2 | 22.4 | 0
1323 | 2022-10-07 22:04 | 17.2 | 22.3 | 0
1324 | 2022-10-07 22:05 | 17.4 | 22.3 | 0
1325 | 2022-10-07 22:06 | 17.5 | 22.3 | 0
1326 | 2022-10-07 22:07 | 17.7 | 22.4 | 0
1327 | 2022-10-07 22:08 | 17.6 | 22.5 | 0
1328 | 2022-10-07 22:09 | 17.7 | 22.2 | 0
1329 | 2022-10-07 22:10 | 17.6 | 22.1 | 0
1330 | 2022-10-07 22:11 | 17.6 | 23.2 | 0
1331 | 2022-10-07 22:12 | 17.7 | 23 | 0
1332 | 2022-10-07 22:13 | 17.7 | 22.2 | 0
1333 | 2022-10-07 22:14 | 17.4 | 22.1 | 0
1334 | 2022-10-07 22:15 | 17.6 | 22.3 | 0
1335 | 2022-10-07 22:16 | 17.6 | 22.4 | 0
1336 | 2022-10-07 22:17 | 17.8 | 21.7 | 0
1337 | 2022-10-07 22:18 | 17.9 | 21.8 | 0
1338 | 2022-10-07 22:19 | 17.7 | 22.4 | 0
1339 | 2022-10-07 22:20 | 17.9 | 22.4 | 0
1340 | 2022-10-07 22:21 | 17.9 | 22 | 0
1341 | 2022-10-07 22:22 | 17.7 | 23 | 0
1342 | 2022-10-07 22:23 | 17.7 | 22.3 | 0
1343 | 2022-10-07 22:24 | 17.9 | 22.3 | 0
1344 | 2022-10-07 22:25 | 17.9 | 22.5 | 0
1345 | 2022-10-07 22:26 | 17.8 | 22.4 | 0
1346 | 2022-10-07 22:27 | 17.9 | 22.2 | 0
1347 | 2022-10-07 22:28 | 18 | 22.2 | 0
1348 | 2022-10-07 22:29 | 17.9 | 22.1 | 0
1349 | 2022-10-07 22:30 | 17.8 | 22.5 | 0
1350 | 2022-10-07 22:31 | 18 | 22.4 | 0
1351 | 2022-10-07 22:32 | 18 | 22.5 | 0
1352 | 2022-10-07 22:33 | 17.9 | 22.1 | 0
1353 | 2022-10-07 22:34 | 17.9 | 22.3 | 0
1354 | 2022-10-07 22:35 | 17.8 | 22.3 | 0
1355 | 2022-10-07 22:36 | 18 | 23.1 | 0
1356 | 2022-10-07 22:37 | 18.1 | 21.7 | 0
1357 | 2022-10-07 22:38 | 17.9 | 22.2 | 0
1358 | 2022-10-07 22:39 | 17.9 | 22.4 | 0
1359 | 2022-10-07 22:40 | 17.9 | 22.2 | 0
1360 | 2022-10-07 22:41 | 18 | 22.3 | 0
1361 | 2022-10-07 22:42 | 18.1 | 22.3 | 0
1362 | 2022-10-07 22:43 | 18 | 22.2 | 0
1363 | 2022-10-07 22:44 | 17.9 | 22.2 | 0
1364 | 2022-10-07 22:45 | 17.9 | 22.2 | 0
1365 | 2022-10-07 22:46 | 18.1 | 22 | 0
1366 | 2022-10-07 22:47 | 18.1 | 22.3 | 0
1367 | 2022-10-07 22:48 | 18.1 | 22.2 | 0
1368 | 2022-10-07 22:49 | 18.1 | 22.7 | 0
1369 | 2022-10-07 22:50 | 18 | 22.1 | 0
1370 | 2022-10-07 22:51 | 18.1 | 22.4 | 0
1371 | 2022-10-07 22:52 | 18.2 | 22.4 | 0
1372 | 2022-10-07 22:53 | 18.1 | 22.4 | 0
1373 | 2022-10-07 22:54 | 18.1 | 22.2 | 0
1374 | 2022-10-07 22:55 | 18 | 22.5 | 0
1375 | 2022-10-07 22:56 | 18.1 | 22.4 | 0
1376 | 2022-10-07 22:57 | 17.9 | 22.3 | 0
1377 | 2022-10-07 22:58 | 18.1 | 22.3 | 0
1378 | 2022-10-07 22:59 | 17.8 | 22.2 | 0
1379 | 2022-10-07 23:00 | 18 | 22.3 | 0
1380 | 2022-10-07 23:01 | 18 | 22.3 | 0
1381 | 2022-10-07 23:02 | 18.1 | 22.4 | 0
1382 | 2022-10-07 23:03 | 18 | 22.2 | 0
1383 | 2022-10-07 23:04 | 18.1 | 22.4 | 0
1384 | 2022-10-07 23:05 | 18.2 | 22.3 | 0
1385 | 2022-10-07 23:06 | 18 | 22.4 | 0
1386 | 2022-10-07 23:07 | 18.2 | 22.3 | 0
1387 | 2022-10-07 23:08 | 18 | 22.3 | 0
1388 | 2022-10-07 23:09 | 18.2 | 22.3 | 0
1389 | 2022-10-07 23:10 | 18.1 | 22.4 | 0
1390 | 2022-10-07 23:11 | 18.2 | 22.2 | 0
1391 | 2022-10-07 23:12 | 18.2 | 22 | 0
1392 | 2022-10-07 23:13 | 18.3 | 21.8 | 0
1393 | 2022-10-07 23:14 | 18.1 | 21.9 | 0
1394 | 2022-10-07 23:15 | 18 | 22.3 | 0
1395 | 2022-10-07 23:16 | 18 | 22.2 | 0
1396 | 2022-10-07 23:17 | 18 | 22.2 | 0
1397 | 2022-10-07 23:18 | 18.3 | 22 | 0
1398 | 2022-10-07 23:19 | 18.1 | 22.5 | 0
1399 | 2022-10-07 23:20 | 18.3 | 21.9 | 0
1400 | 2022-10-07 23:21 | 18.2 | 22.8 | 0
1401 | 2022-10-07 23:22 | 18.3 | 22.5 | 0
1402 | 2022-10-07 23:23 | 18.1 | 22.8 | 0
1403 | 2022-10-07 23:24 | 18.1 | 21.5 | 0
1404 | 2022-10-07 23:25 | 18.3 | 22.4 | 0
1405 | 2022-10-07 23:26 | 18.3 | 22.6 | 0
1406 | 2022-10-07 23:27 | 18.3 | 21.7 | 0
1407 | 2022-10-07 23:28 | 18.1 | 22.2 | 0
1408 | 2022-10-07 23:29 | 18.4 | 22.6 | 0
1409 | 2022-10-07 23:30 | 18.4 | 22.9 | 0
1410 | 2022-10-07 23:31 | 18.4 | 22.8 | 0
1411 | 2022-10-07 23:32 | 18.2 | 22.4 | 0
1412 | 2022-10-07 23:33 | 18.4 | 22.2 | 0
1413 | 2022-10-07 23:34 | 18.3 | 22.2 | 0
1414 | 2022-10-07 23:35 | 18.3 | 22.5 | 0
1415 | 2022-10-07 23:36 | 18.4 | 22.2 | 0
1416 | 2022-10-07 23:37 | 18.3 | 22.4 | 0
1417 | 2022-10-07 23:38 | 18.3 | 21.5 | 0
1418 | 2022-10-07 23:39 | 18.3 | 21.4 | 0
1419 | 2022-10-07 23:40 | 18.3 | 22.4 | 0
1420 | 2022-10-07 23:41 | 18.5 | 22.2 | 0
1421 | 2022-10-07 23:42 | 18.5 | 22.5 | 0
1422 | 2022-10-07 23:43 | 18.6 | 22.5 | 0
1423 | 2022-10-07 23:44 | 18.5 | 22.3 | 0
1424 | 2022-10-07 23:45 | 18.4 | 22.4 | 0
1425 | 2022-10-07 23:46 | 18.6 | 22.7 | 0
1426 | 2022-10-07 23:47 | 18.4 | 22.8 | 0
1427 | 2022-10-07 23:48 | 18.5 | 22.6 | 0
1428 | 2022-10-07 23:49 | 18.6 | 22.4 | 0
1429 | 2022-10-07 23:50 | 18.5 | 23.1 | 0
1430 | 2022-10-07 23:51 | 18.6 | 23.2 | 0
1431 | 2022-10-07 23:52 | 18.5 | 22.5 | 0
1432 | 2022-10-07 23:53 | 18.3 | 22.5 | 0
1433 | 2022-10-07 23:54 | 18.5 | 21.9 | 0
1434 | 2022-10-07 23:55 | 18.4 | 22.6 | 0
1435 | 2022-10-07 23:56 | 18.4 | 22.3 | 0
1436 | 2022-10-07 23:57 | 18.4 | 22.6 | 0
1437 | 2022-10-07 23:58 | 18.4 | 22.4 | 0
1438 | 2022-10-07 23:59 | 18.3 | 22.1 | 0
1439 | 2022-10-08 | 18.3 | 22.4 | 0

## 08-10-2022_NO HEAT
| Date&time_x | OUTDOOR_TEMP | INDOOR_TEMP | PYRANOMETER
0 | 2022-10-08 00:01 | 18.3 | 22.3 | 0
1 | 2022-10-08 00:02 | 18.1 | 22.5 | 0
2 | 2022-10-08 00:03 | 18.2 | 22.4 | 0
3 | 2022-10-08 00:04 | 18.2 | 22.4 | 0
4 | 2022-10-08 00:05 | 18.2 | 22.5 | 0
5 | 2022-10-08 00:06 | 18.2 | 22 | 0
6 | 2022-10-08 00:07 | 18.2 | 22.4 | 0
7 | 2022-10-08 00:08 | 18.1 | 22.1 | 0
8 | 2022-10-08 00:09 | 18.1 | 21.5 | 0
9 | 2022-10-08 00:10 | 18.1 | 21.4 | 0
10 | 2022-10-08 00:11 | 18 | 21.6 | 0
11 | 2022-10-08 00:12 | 18.2 | 22.9 | 0
12 | 2022-10-08 00:13 | 17.9 | 22.6 | 0
13 | 2022-10-08 00:14 | 17.9 | 22 | 0
14 | 2022-10-08 00:15 | 18.1 | 22 | 0
15 | 2022-10-08 00:16 | 18 | 22.2 | 0
16 | 2022-10-08 00:17 | 17.8 | 22.1 | 0
17 | 2022-10-08 00:18 | 18 | 22.1 | 0
18 | 2022-10-08 00:19 | 18 | 22.6 | 0
19 | 2022-10-08 00:20 | 17.9 | 22.2 | 0
20 | 2022-10-08 00:21 | 17.9 | 21.6 | 0
21 | 2022-10-08 00:22 | 18 | 21.7 | 0
22 | 2022-10-08 00:23 | 18 | 22.4 | 0
23 | 2022-10-08 00:24 | 17.9 | 22 | 0
24 | 2022-10-08 00:25 | 17.7 | 22.3 | 0
25 | 2022-10-08 00:26 | 18.1 | 22 | 0
26 | 2022-10-08 00:27 | 17.8 | 22 | 0
27 | 2022-10-08 00:28 | 18 | 21.8 | 0
28 | 2022-10-08 00:29 | 18.1 | 22.5 | 0
29 | 2022-10-08 00:30 | 17.8 | 21.8 | 0
30 | 2022-10-08 00:31 | 18 | 22.6 | 0
31 | 2022-10-08 00:32 | 17.9 | 22.4 | 0
32 | 2022-10-08 00:33 | 17.7 | 22.3 | 0
33 | 2022-10-08 00:34 | 17.8 | 22.1 | 0
34 | 2022-10-08 00:35 | 17.8 | 22.1 | 0
35 | 2022-10-08 00:36 | 17.8 | 22.4 | 0
36 | 2022-10-08 00:37 | 17.7 | 22.9 | 0
37 | 2022-10-08 00:38 | 17.8 | 23.1 | 0
38 | 2022-10-08 00:39 | 17.8 | 22.9 | 0
39 | 2022-10-08 00:40 | 17.8 | 21.8 | 0
40 | 2022-10-08 00:41 | 17.7 | 21.4 | 0
41 | 2022-10-08 00:42 | 17.6 | 22.4 | 0
42 | 2022-10-08 00:43 | 17.6 | 22.3 | 0
43 | 2022-10-08 00:44 | 17.4 | 22 | 0
44 | 2022-10-08 00:45 | 17.6 | 22.2 | 0
45 | 2022-10-08 00:46 | 17.6 | 21.7 | 0
46 | 2022-10-08 00:47 | 17.6 | 21.4 | 0
47 | 2022-10-08 00:48 | 17.3 | 21.7 | 0
48 | 2022-10-08 00:49 | 17.2 | 22.3 | 0
49 | 2022-10-08 00:50 | 17.2 | 22.3 | 0
50 | 2022-10-08 00:51 | 17.2 | 22.1 | 0
51 | 2022-10-08 00:52 | 17.2 | 21.9 | 0
52 | 2022-10-08 00:53 | 17.2 | 21.5 | 0
53 | 2022-10-08 00:54 | 17.3 | 21.3 | 0
54 | 2022-10-08 00:55 | 17.1 | 21.5 | 0
55 | 2022-10-08 00:56 | 17 | 22.2 | 0
56 | 2022-10-08 00:57 | 17.1 | 22.6 | 0
57 | 2022-10-08 00:58 | 16.9 | 22.1 | 0
58 | 2022-10-08 00:59 | 17 | 22.2 | 0
59 | 2022-10-08 01:00 | 17 | 22.3 | 0
60 | 2022-10-08 01:01 | 16.9 | 22 | 0
61 | 2022-10-08 01:02 | 16.9 | 22.2 | 0
62 | 2022-10-08 01:03 | 16.9 | 22.4 | 0
63 | 2022-10-08 01:04 | 16.7 | 22.3 | 0
64 | 2022-10-08 01:05 | 16.7 | 22.3 | 0
65 | 2022-10-08 01:06 | 16.6 | 22.1 | 0
66 | 2022-10-08 01:07 | 16.5 | 22.3 | 0
67 | 2022-10-08 01:08 | 16.4 | 22.1 | 0
68 | 2022-10-08 01:09 | 16.6 | 22.3 | 0
69 | 2022-10-08 01:10 | 16.7 | 22.2 | 0
70 | 2022-10-08 01:11 | 16.6 | 22.2 | 0
71 | 2022-10-08 01:12 | 16.6 | 22.2 | 0
72 | 2022-10-08 01:13 | 16.5 | 22.2 | 0
73 | 2022-10-08 01:14 | 16.6 | 22.2 | 0
74 | 2022-10-08 01:15 | 16.3 | 22.2 | 0
75 | 2022-10-08 01:16 | 16.5 | 22.1 | 0
76 | 2022-10-08 01:17 | 16.4 | 22.3 | 0
77 | 2022-10-08 01:18 | 16.1 | 22.4 | 0
78 | 2022-10-08 01:19 | 16 | 22 | 0
79 | 2022-10-08 01:20 | 16 | 22.3 | 0
80 | 2022-10-08 01:21 | 15.9 | 22.2 | 0
81 | 2022-10-08 01:22 | 15.8 | 22.4 | 0
82 | 2022-10-08 01:23 | 15.9 | 21.9 | 0
83 | 2022-10-08 01:24 | 15.7 | 22.6 | 0
84 | 2022-10-08 01:25 | 15.4 | 22.6 | 0
85 | 2022-10-08 01:26 | 15.5 | 22.4 | 0
86 | 2022-10-08 01:27 | 15.6 | 22.3 | 0
87 | 2022-10-08 01:28 | 15.5 | 22.2 | 0
88 | 2022-10-08 01:29 | 15.3 | 22.3 | 0
89 | 2022-10-08 01:30 | 15.3 | 22.2 | 0
90 | 2022-10-08 01:31 | 15.3 | 21.9 | 0
91 | 2022-10-08 01:32 | 15.2 | 22.8 | 0
92 | 2022-10-08 01:33 | 15.1 | 21.9 | 0
93 | 2022-10-08 01:34 | 15.1 | 21.5 | 0
94 | 2022-10-08 01:35 | 15.1 | 22.7 | 0
95 | 2022-10-08 01:36 | 15 | 22.2 | 0
96 | 2022-10-08 01:37 | 14.9 | 22.1 | 0
97 | 2022-10-08 01:38 | 15 | 21.9 | 0
98 | 2022-10-08 01:39 | 15.1 | 22.2 | 0
99 | 2022-10-08 01:40 | 15.2 | 23 | 0
100 | 2022-10-08 01:41 | 15.5 | 22 | 0
101 | 2022-10-08 01:42 | 15.6 | 22 | 0
102 | 2022-10-08 01:43 | 15.9 | 21.4 | 0
103 | 2022-10-08 01:44 | 16.1 | 21.9 | 0
104 | 2022-10-08 01:45 | 15.7 | 21.5 | 0
105 | 2022-10-08 01:46 | 15.8 | 22.2 | 0
106 | 2022-10-08 01:47 | 15.4 | 22.8 | 0
107 | 2022-10-08 01:48 | 15.5 | 21.6 | 0
108 | 2022-10-08 01:49 | 15.2 | 22.5 | 0
109 | 2022-10-08 01:50 | 15.2 | 21.8 | 0
110 | 2022-10-08 01:51 | 15.1 | 21.4 | 0
111 | 2022-10-08 01:52 | 15.2 | 22.1 | 0
112 | 2022-10-08 01:53 | 15.2 | 22.5 | 0
113 | 2022-10-08 01:54 | 15 | 22.2 | 0
114 | 2022-10-08 01:55 | 14.9 | 22.2 | 0
115 | 2022-10-08 01:56 | 15.2 | 21.7 | 0
116 | 2022-10-08 01:57 | 14.9 | 22.6 | 0
117 | 2022-10-08 01:58 | 14.9 | 22.3 | 0
118 | 2022-10-08 01:59 | 15 | 21.9 | 0
119 | 2022-10-08 02:00 | 14.8 | 22.5 | 0
120 | 2022-10-08 02:01 | 14.8 | 22.3 | 0
121 | 2022-10-08 02:02 | 14.8 | 22.3 | 0
122 | 2022-10-08 02:03 | 14.7 | 22.2 | 0
123 | 2022-10-08 02:04 | 14.5 | 22.3 | 0
124 | 2022-10-08 02:05 | 14.5 | 22.4 | 0
125 | 2022-10-08 02:06 | 14.4 | 22.4 | 0
126 | 2022-10-08 02:07 | 14.4 | 22.3 | 0
127 | 2022-10-08 02:08 | 14.4 | 22.1 | 0
128 | 2022-10-08 02:09 | 14.2 | 21.5 | 0
129 | 2022-10-08 02:10 | 14.4 | 22.3 | 0
130 | 2022-10-08 02:11 | 14.4 | 22.4 | 0
131 | 2022-10-08 02:12 | 14.3 | 22.1 | 0
132 | 2022-10-08 02:13 | 14.6 | 22.2 | 0
133 | 2022-10-08 02:14 | 14.3 | 22.4 | 0
134 | 2022-10-08 02:15 | 14.3 | 22.9 | 0
135 | 2022-10-08 02:16 | 14.4 | 21.4 | 0
136 | 2022-10-08 02:17 | 14.2 | 21.9 | 0
137 | 2022-10-08 02:18 | 14.2 | 23.1 | 0
138 | 2022-10-08 02:19 | 14 | 22.6 | 0
139 | 2022-10-08 02:20 | 14.3 | 22.8 | 0
140 | 2022-10-08 02:21 | 14.2 | 21.8 | 0
141 | 2022-10-08 02:22 | 13.9 | 22.2 | 0
142 | 2022-10-08 02:23 | 14.6 | 22.1 | 0
143 | 2022-10-08 02:24 | 14.7 | 22 | 0
144 | 2022-10-08 02:25 | 14.3 | 22.9 | 0
145 | 2022-10-08 02:26 | 14 | 22.9 | 0
146 | 2022-10-08 02:27 | 14.1 | 22.4 | 0
147 | 2022-10-08 02:28 | 14.1 | 21.3 | 0
148 | 2022-10-08 02:29 | 14.1 | 22.4 | 0
149 | 2022-10-08 02:30 | 14 | 22.3 | 0
150 | 2022-10-08 02:31 | 13.8 | 21.9 | 0
151 | 2022-10-08 02:32 | 13.8 | 22.8 | 0
152 | 2022-10-08 02:33 | 14.3 | 22.5 | 0
153 | 2022-10-08 02:34 | 14.5 | 22.1 | 0
154 | 2022-10-08 02:35 | 14.7 | 22.1 | 0
155 | 2022-10-08 02:36 | 14.5 | 21.3 | 0
156 | 2022-10-08 02:37 | 14.2 | 22 | 0
157 | 2022-10-08 02:38 | 14.2 | 22.2 | 0
158 | 2022-10-08 02:39 | 14.6 | 21.8 | 0
159 | 2022-10-08 02:40 | 14.9 | 22.3 | 0
160 | 2022-10-08 02:41 | 14.4 | 21.8 | 0
161 | 2022-10-08 02:42 | 14.4 | 22.3 | 0
162 | 2022-10-08 02:43 | 14.1 | 22.6 | 0
163 | 2022-10-08 02:44 | 14.4 | 22.6 | 0
164 | 2022-10-08 02:45 | 14.3 | 21.6 | 0
165 | 2022-10-08 02:46 | 14.2 | 21.8 | 0
166 | 2022-10-08 02:47 | 14.4 | 22.6 | 0
167 | 2022-10-08 02:48 | 14.1 | 22.3 | 0
168 | 2022-10-08 02:49 | 14.2 | 22 | 0
169 | 2022-10-08 02:50 | 14.4 | 22.7 | 0
170 | 2022-10-08 02:51 | 14.6 | 22.3 | 0
171 | 2022-10-08 02:52 | 14.7 | 22.5 | 0
172 | 2022-10-08 02:53 | 15.4 | 21.9 | 0
173 | 2022-10-08 02:54 | 15.2 | 21.9 | 0
174 | 2022-10-08 02:55 | 15.4 | 22.8 | 0
175 | 2022-10-08 02:56 | 15.4 | 21.8 | 0
176 | 2022-10-08 02:57 | 15.4 | 22.4 | 0
177 | 2022-10-08 02:58 | 15.6 | 22.2 | 0
178 | 2022-10-08 02:59 | 16 | 22 | 0
179 | 2022-10-08 03:00 | 15.8 | 22.3 | 0
180 | 2022-10-08 03:01 | 16.1 | 22.7 | 0
181 | 2022-10-08 03:02 | 16.2 | 21.9 | 0
182 | 2022-10-08 03:03 | 15.9 | 22.6 | 0
183 | 2022-10-08 03:04 | 15.6 | 22.6 | 0
184 | 2022-10-08 03:05 | 15.9 | 22.2 | 0
185 | 2022-10-08 03:06 | 16 | 22.4 | 0
186 | 2022-10-08 03:07 | 15.9 | 21.9 | 0
187 | 2022-10-08 03:08 | 16 | 21.9 | 0
188 | 2022-10-08 03:09 | 15.9 | 23.1 | 0
189 | 2022-10-08 03:10 | 15.9 | 22.5 | 0
190 | 2022-10-08 03:11 | 16.1 | 22.2 | 0
191 | 2022-10-08 03:12 | 16.1 | 22.1 | 0
192 | 2022-10-08 03:13 | 16.2 | 22.3 | 0
193 | 2022-10-08 03:14 | 16.6 | 22.1 | 0
194 | 2022-10-08 03:15 | 16.6 | 22.1 | 0
195 | 2022-10-08 03:16 | 16.4 | 21.6 | 0
196 | 2022-10-08 03:17 | 16.6 | 21.4 | 0
197 | 2022-10-08 03:18 | 16.4 | 22.3 | 0
198 | 2022-10-08 03:19 | 16.4 | 21.9 | 0
199 | 2022-10-08 03:20 | 16.3 | 22 | 0
200 | 2022-10-08 03:21 | 16.4 | 22.5 | 0
201 | 2022-10-08 03:22 | 16.1 | 22.5 | 0
202 | 2022-10-08 03:23 | 16 | 22.7 | 0
203 | 2022-10-08 03:24 | 15.8 | 22.5 | 0
204 | 2022-10-08 03:25 | 15.2 | 21.9 | 0
205 | 2022-10-08 03:26 | 15.2 | 21.9 | 0
206 | 2022-10-08 03:27 | 15 | 22.4 | 0
207 | 2022-10-08 03:28 | 14.8 | 22.2 | 0
208 | 2022-10-08 03:29 | 14.7 | 21.5 | 0
209 | 2022-10-08 03:30 | 14.5 | 21.5 | 0
210 | 2022-10-08 03:31 | 14.4 | 21.3 | 0
211 | 2022-10-08 03:32 | 14.4 | 22.2 | 0
212 | 2022-10-08 03:33 | 14.3 | 21.6 | 0
213 | 2022-10-08 03:34 | 14.1 | 21.4 | 0
214 | 2022-10-08 03:35 | 14.3 | 22.2 | 0
215 | 2022-10-08 03:36 | 14 | 22 | 0
216 | 2022-10-08 03:37 | 14.2 | 21.8 | 0
217 | 2022-10-08 03:38 | 14.1 | 22.7 | 0
218 | 2022-10-08 03:39 | 14.1 | 21.9 | 0
219 | 2022-10-08 03:40 | 14 | 22.3 | 0
220 | 2022-10-08 03:41 | 14.1 | 21.3 | 0
221 | 2022-10-08 03:42 | 14.2 | 21.9 | 0
222 | 2022-10-08 03:43 | 13.9 | 22.9 | 0
223 | 2022-10-08 03:44 | 13.8 | 22.4 | 0
224 | 2022-10-08 03:45 | 13.9 | 22 | 0
225 | 2022-10-08 03:46 | 13.9 | 21.9 | 0
226 | 2022-10-08 03:47 | 13.8 | 21.4 | 0
227 | 2022-10-08 03:48 | 13.7 | 22.4 | 0
228 | 2022-10-08 03:49 | 13.6 | 22.5 | 0
229 | 2022-10-08 03:50 | 13.6 | 21.7 | 0
230 | 2022-10-08 03:51 | 13.5 | 22.5 | 0
231 | 2022-10-08 03:52 | 13.5 | 21.9 | 0
232 | 2022-10-08 03:53 | 13.2 | 22.1 | 0
233 | 2022-10-08 03:54 | 13.3 | 22 | 0
234 | 2022-10-08 03:55 | 13.4 | 21.8 | 0
235 | 2022-10-08 03:56 | 13.6 | 22.1 | 0
236 | 2022-10-08 03:57 | 14.1 | 22 | 0
237 | 2022-10-08 03:58 | 14.9 | 21.8 | 0
238 | 2022-10-08 03:59 | 14.5 | 21.2 | 0
239 | 2022-10-08 04:00 | 14.4 | 21.3 | 0
240 | 2022-10-08 04:01 | 13.7 | 21.6 | 0
241 | 2022-10-08 04:02 | 13.6 | 22 | 0
242 | 2022-10-08 04:03 | 13.6 | 22.3 | 0
243 | 2022-10-08 04:04 | 13.3 | 21.9 | 0
244 | 2022-10-08 04:05 | 13.8 | 22 | 0
245 | 2022-10-08 04:06 | 14.1 | 21.9 | 0
246 | 2022-10-08 04:07 | 14.2 | 22.8 | 0
247 | 2022-10-08 04:08 | 13.8 | 21.9 | 0
248 | 2022-10-08 04:09 | 13.9 | 22.1 | 0
249 | 2022-10-08 04:10 | 13.5 | 21.6 | 0
250 | 2022-10-08 04:11 | 13.5 | 22.3 | 0
251 | 2022-10-08 04:12 | 13.7 | 22.1 | 0
252 | 2022-10-08 04:13 | 13.4 | 21.8 | 0
253 | 2022-10-08 04:14 | 13.2 | 22.8 | 0
254 | 2022-10-08 04:15 | 13.4 | 22.1 | 0
255 | 2022-10-08 04:16 | 14.2 | 22.3 | 0
256 | 2022-10-08 04:17 | 14 | 22.3 | 0
257 | 2022-10-08 04:18 | 13.5 | 22.1 | 0
258 | 2022-10-08 04:19 | 13.6 | 22.1 | 0
259 | 2022-10-08 04:20 | 13.4 | 22 | 0
260 | 2022-10-08 04:21 | 13.8 | 21.8 | 0
261 | 2022-10-08 04:22 | 14.3 | 22.4 | 0
262 | 2022-10-08 04:23 | 14.1 | 21.2 | 0
263 | 2022-10-08 04:24 | 13.8 | 21.2 | 0
264 | 2022-10-08 04:25 | 13.8 | 22.1 | 0
265 | 2022-10-08 04:26 | 14 | 22.3 | 0
266 | 2022-10-08 04:27 | 13.9 | 22 | 0
267 | 2022-10-08 04:28 | 13.6 | 22 | 0
268 | 2022-10-08 04:29 | 13.6 | 21.9 | 0
269 | 2022-10-08 04:30 | 13.6 | 22.2 | 0
270 | 2022-10-08 04:31 | 13.6 | 22.2 | 0
271 | 2022-10-08 04:32 | 13.5 | 22.2 | 0
272 | 2022-10-08 04:33 | 13.5 | 22.1 | 0
273 | 2022-10-08 04:34 | 13.2 | 21.9 | 0
274 | 2022-10-08 04:35 | 14 | 22.3 | 0
275 | 2022-10-08 04:36 | 14.2 | 21.9 | 0
276 | 2022-10-08 04:37 | 13.8 | 21.9 | 0
277 | 2022-10-08 04:38 | 13.5 | 22.1 | 0
278 | 2022-10-08 04:39 | 13.6 | 22.4 | 0
279 | 2022-10-08 04:40 | 13.5 | 22 | 0
280 | 2022-10-08 04:41 | 13.4 | 22.1 | 0
281 | 2022-10-08 04:42 | 13.5 | 22 | 0
282 | 2022-10-08 04:43 | 13.3 | 21.4 | 0
283 | 2022-10-08 04:44 | 13.3 | 22.2 | 0
284 | 2022-10-08 04:45 | 13.2 | 21.8 | 0
285 | 2022-10-08 04:46 | 13.2 | 22 | 0
286 | 2022-10-08 04:47 | 13.1 | 22 | 0
287 | 2022-10-08 04:48 | 14 | 22 | 0
288 | 2022-10-08 04:49 | 14 | 21.3 | 0
289 | 2022-10-08 04:50 | 14.2 | 22.6 | 0
290 | 2022-10-08 04:51 | 13.8 | 22.3 | 0
291 | 2022-10-08 04:52 | 13.6 | 21.4 | 0
292 | 2022-10-08 04:53 | 13.8 | 21.8 | 0
293 | 2022-10-08 04:54 | 13.6 | 22 | 0
294 | 2022-10-08 04:55 | 13.4 | 21.8 | 0
295 | 2022-10-08 04:56 | 13.4 | 22.4 | 0
296 | 2022-10-08 04:57 | 13.4 | 22 | 0
297 | 2022-10-08 04:58 | 13.3 | 22 | 0
298 | 2022-10-08 04:59 | 13.3 | 21.5 | 0
299 | 2022-10-08 05:00 | 13.7 | 22.9 | 0
300 | 2022-10-08 05:01 | 13.5 | 22.1 | 0
301 | 2022-10-08 05:02 | 13.3 | 22.1 | 0
302 | 2022-10-08 05:03 | 13.4 | 21.8 | 0
303 | 2022-10-08 05:04 | 13.5 | 21.9 | 0
304 | 2022-10-08 05:05 | 13.4 | 22 | 0
305 | 2022-10-08 05:06 | 13.2 | 22.1 | 0
306 | 2022-10-08 05:07 | 13.2 | 22.2 | 0
307 | 2022-10-08 05:08 | 13.1 | 21.9 | 0
308 | 2022-10-08 05:09 | 13.3 | 21.9 | 0
309 | 2022-10-08 05:10 | 13.2 | 22.2 | 0
310 | 2022-10-08 05:11 | 14 | 21.7 | 0
311 | 2022-10-08 05:12 | 14 | 22.2 | 0
312 | 2022-10-08 05:13 | 13.8 | 22.8 | 0
313 | 2022-10-08 05:14 | 13.6 | 21.8 | 0
314 | 2022-10-08 05:15 | 13.8 | 21.9 | 0
315 | 2022-10-08 05:16 | 13.8 | 22.8 | 0
316 | 2022-10-08 05:17 | 13.7 | 22.5 | 0
317 | 2022-10-08 05:18 | 13.5 | 22.1 | 0
318 | 2022-10-08 05:19 | 13.6 | 22.3 | 0
319 | 2022-10-08 05:20 | 13.6 | 22.3 | 0
320 | 2022-10-08 05:21 | 13.4 | 22 | 0
321 | 2022-10-08 05:22 | 13.5 | 22.7 | 0
322 | 2022-10-08 05:23 | 13.3 | 22.8 | 0
323 | 2022-10-08 05:24 | 13.1 | 22.2 | 0
324 | 2022-10-08 05:25 | 13.1 | 21.4 | 0
325 | 2022-10-08 05:26 | 13.2 | 22.4 | 0
326 | 2022-10-08 05:27 | 13 | 22.5 | 0
327 | 2022-10-08 05:28 | 13 | 21.3 | 0
328 | 2022-10-08 05:29 | 13.6 | 21.6 | 0
329 | 2022-10-08 05:30 | 13.7 | 22.1 | 0
330 | 2022-10-08 05:31 | 13.5 | 22.9 | 0
331 | 2022-10-08 05:32 | 13.3 | 21.2 | 0
332 | 2022-10-08 05:33 | 13.4 | 21.8 | 0
333 | 2022-10-08 05:34 | 13.1 | 21.8 | 0
334 | 2022-10-08 05:35 | 13.1 | 21.8 | 0
335 | 2022-10-08 05:36 | 13 | 21.8 | 0
336 | 2022-10-08 05:37 | 13.1 | 22.3 | 0
337 | 2022-10-08 05:38 | 13 | 21.9 | 0
338 | 2022-10-08 05:39 | 13 | 22.1 | 0
339 | 2022-10-08 05:40 | 12.8 | 22.8 | 0
340 | 2022-10-08 05:41 | 12.9 | 22 | 0
341 | 2022-10-08 05:42 | 12.8 | 22 | 0
342 | 2022-10-08 05:43 | 13 | 22.2 | 0
343 | 2022-10-08 05:44 | 12.8 | 22.3 | 0
344 | 2022-10-08 05:45 | 12.8 | 22.4 | 0
345 | 2022-10-08 05:46 | 12.9 | 22.2 | 0
346 | 2022-10-08 05:47 | 12.8 | 21.9 | 0
347 | 2022-10-08 05:48 | 12.8 | 22.6 | 0
348 | 2022-10-08 05:49 | 13 | 21.4 | 0
349 | 2022-10-08 05:50 | 12.8 | 22.4 | 0
350 | 2022-10-08 05:51 | 12.8 | 21.8 | 0
351 | 2022-10-08 05:52 | 12.8 | 21.6 | 0
352 | 2022-10-08 05:53 | 12.8 | 21.8 | 0
353 | 2022-10-08 05:54 | 12.8 | 22.1 | 0
354 | 2022-10-08 05:55 | 12.6 | 22.2 | 0
355 | 2022-10-08 05:56 | 12.8 | 22 | 0
356 | 2022-10-08 05:57 | 13 | 21.7 | 0
357 | 2022-10-08 05:58 | 13.2 | 22.5 | 0
358 | 2022-10-08 05:59 | 13.3 | 21.4 | 0
359 | 2022-10-08 06:00 | 13 | 21.9 | 0
360 | 2022-10-08 06:01 | 12.8 | 21.9 | 0
361 | 2022-10-08 06:02 | 12.8 | 22.6 | 0
362 | 2022-10-08 06:03 | 12.9 | 21.4 | 0
363 | 2022-10-08 06:04 | 12.8 | 22.2 | 0
364 | 2022-10-08 06:05 | 12.6 | 22.1 | 0
365 | 2022-10-08 06:06 | 12.6 | 21.8 | 0
366 | 2022-10-08 06:07 | 12.8 | 22 | 0
367 | 2022-10-08 06:08 | 12.8 | 21.7 | 0
368 | 2022-10-08 06:09 | 12.8 | 22.6 | 0
369 | 2022-10-08 06:10 | 13 | 21.8 | 0
370 | 2022-10-08 06:11 | 12.9 | 21.9 | 0
371 | 2022-10-08 06:12 | 12.9 | 21.9 | 0
372 | 2022-10-08 06:13 | 12.8 | 22.7 | 0
373 | 2022-10-08 06:14 | 12.7 | 21.7 | 0
374 | 2022-10-08 06:15 | 12.8 | 22.7 | 0
375 | 2022-10-08 06:16 | 12.5 | 21.7 | 0
376 | 2022-10-08 06:17 | 12.7 | 22.2 | 0
377 | 2022-10-08 06:18 | 12.6 | 22.2 | 0
378 | 2022-10-08 06:19 | 12.7 | 21.3 | 0
379 | 2022-10-08 06:20 | 12.7 | 21.8 | 0
380 | 2022-10-08 06:21 | 12.7 | 21.4 | 0
381 | 2022-10-08 06:22 | 12.6 | 22.4 | 0
382 | 2022-10-08 06:23 | 12.7 | 22.2 | 0
383 | 2022-10-08 06:24 | 12.5 | 22.7 | 0
384 | 2022-10-08 06:25 | 12.7 | 21.5 | 0
385 | 2022-10-08 06:26 | 12.7 | 22 | 0
386 | 2022-10-08 06:27 | 12.6 | 21.4 | 0
387 | 2022-10-08 06:28 | 12.6 | 22.1 | 0
388 | 2022-10-08 06:29 | 12.5 | 22.3 | 0
389 | 2022-10-08 06:30 | 12.8 | 21.5 | 0
390 | 2022-10-08 06:31 | 12.5 | 22.1 | 0
391 | 2022-10-08 06:32 | 12.6 | 22 | 0
392 | 2022-10-08 06:33 | 12.4 | 21.7 | 0
393 | 2022-10-08 06:34 | 12.7 | 22.1 | 0
394 | 2022-10-08 06:35 | 12.8 | 21.5 | 0
395 | 2022-10-08 06:36 | 12.5 | 21.6 | 0
396 | 2022-10-08 06:37 | 12.5 | 22.7 | 0
397 | 2022-10-08 06:38 | 12.4 | 21.7 | 0
398 | 2022-10-08 06:39 | 12.6 | 21.8 | 0
399 | 2022-10-08 06:40 | 12.4 | 22 | 0
400 | 2022-10-08 06:41 | 12.4 | 21.6 | 0
401 | 2022-10-08 06:42 | 12.7 | 22.3 | 0
402 | 2022-10-08 06:43 | 12.6 | 22.1 | 0
403 | 2022-10-08 06:44 | 12.4 | 22.4 | 0
404 | 2022-10-08 06:45 | 12.7 | 21.4 | 0
405 | 2022-10-08 06:46 | 12.6 | 21.5 | 0
406 | 2022-10-08 06:47 | 12.5 | 21.2 | 0
407 | 2022-10-08 06:48 | 12.5 | 21.8 | 0
408 | 2022-10-08 06:49 | 12.6 | 22.1 | 0
409 | 2022-10-08 06:50 | 12.6 | 21.8 | 0
410 | 2022-10-08 06:51 | 12.5 | 22 | 0
411 | 2022-10-08 06:52 | 12.5 | 21.6 | 0
412 | 2022-10-08 06:53 | 12.6 | 22.1 | 0
413 | 2022-10-08 06:54 | 12.7 | 22 | 0
414 | 2022-10-08 06:55 | 12.6 | 22.1 | 0
415 | 2022-10-08 06:56 | 12.6 | 21.7 | 0
416 | 2022-10-08 06:57 | 12.5 | 22.6 | 0
417 | 2022-10-08 06:58 | 12.6 | 22.7 | 0
418 | 2022-10-08 06:59 | 12.6 | 22.5 | 0
419 | 2022-10-08 07:00 | 12.6 | 21.8 | 0
420 | 2022-10-08 07:01 | 12.6 | 21.6 | 0
421 | 2022-10-08 07:02 | 12.5 | 21.7 | 0
422 | 2022-10-08 07:03 | 12.5 | 21.9 | 0
423 | 2022-10-08 07:04 | 12.7 | 21.9 | 0
424 | 2022-10-08 07:05 | 12.5 | 22 | 0
425 | 2022-10-08 07:06 | 12.4 | 21.4 | 0
426 | 2022-10-08 07:07 | 12.5 | 21.9 | 0
427 | 2022-10-08 07:08 | 12.5 | 21.5 | 0
428 | 2022-10-08 07:09 | 12.4 | 22.1 | 0
429 | 2022-10-08 07:10 | 12.6 | 21.7 | 0
430 | 2022-10-08 07:11 | 12.5 | 22.5 | 0
431 | 2022-10-08 07:12 | 12.3 | 21.6 | 0
432 | 2022-10-08 07:13 | 12.6 | 22.5 | 0
433 | 2022-10-08 07:14 | 12.4 | 22.4 | 0
434 | 2022-10-08 07:15 | 12.2 | 21.6 | 0
435 | 2022-10-08 07:16 | 12.2 | 21.3 | 0
436 | 2022-10-08 07:17 | 12.4 | 21.8 | 0
437 | 2022-10-08 07:18 | 12.4 | 22.6 | 0
438 | 2022-10-08 07:19 | 12.3 | 22.3 | 0
439 | 2022-10-08 07:20 | 12.2 | 21.3 | 0
440 | 2022-10-08 07:21 | 12.1 | 22 | 0
441 | 2022-10-08 07:22 | 12.1 | 21.9 | 0
442 | 2022-10-08 07:23 | 12.2 | 21.8 | 0
443 | 2022-10-08 07:24 | 12 | 21.9 | 0
444 | 2022-10-08 07:25 | 12.1 | 21.9 | 0
445 | 2022-10-08 07:26 | 12.1 | 21.8 | 1
446 | 2022-10-08 07:27 | 12 | 22.3 | 1
447 | 2022-10-08 07:28 | 12 | 22.3 | 2
448 | 2022-10-08 07:29 | 12.1 | 22.4 | 2
449 | 2022-10-08 07:30 | 12 | 22.5 | 2
450 | 2022-10-08 07:31 | 12.1 | 22.3 | 3
451 | 2022-10-08 07:32 | 12 | 21.7 | 3
452 | 2022-10-08 07:33 | 12 | 21.1 | 4
453 | 2022-10-08 07:34 | 11.9 | 21.1 | 5
454 | 2022-10-08 07:35 | 12 | 21.1 | 5
455 | 2022-10-08 07:36 | 12.1 | 21.7 | 6
456 | 2022-10-08 07:37 | 12.2 | 21.8 | 6
457 | 2022-10-08 07:38 | 12 | 21.7 | 7
458 | 2022-10-08 07:39 | 12 | 21.8 | 7
459 | 2022-10-08 07:40 | 12.1 | 21.9 | 8
460 | 2022-10-08 07:41 | 11.8 | 21.8 | 8
461 | 2022-10-08 07:42 | 11.8 | 21.8 | 9
462 | 2022-10-08 07:43 | 11.8 | 21.8 | 9
463 | 2022-10-08 07:44 | 12.1 | 21.3 | 10
464 | 2022-10-08 07:45 | 12 | 21.8 | 10
465 | 2022-10-08 07:46 | 11.9 | 21.3 | 11
466 | 2022-10-08 07:47 | 12 | 22 | 12
467 | 2022-10-08 07:48 | 11.8 | 21.5 | 12
468 | 2022-10-08 07:49 | 11.9 | 21.9 | 13
469 | 2022-10-08 07:50 | 12 | 21.4 | 14
470 | 2022-10-08 07:51 | 11.8 | 22.4 | 14
471 | 2022-10-08 07:52 | 12.1 | 21.4 | 15
472 | 2022-10-08 07:53 | 12.1 | 21.5 | 15
473 | 2022-10-08 07:54 | 11.9 | 21.1 | 15
474 | 2022-10-08 07:55 | 12.1 | 21.3 | 16
475 | 2022-10-08 07:56 | 12.1 | 21.1 | 17
476 | 2022-10-08 07:57 | 12.1 | 22 | 17
477 | 2022-10-08 07:58 | 12.2 | 22.5 | 18
478 | 2022-10-08 07:59 | 12.4 | 22 | 19
479 | 2022-10-08 08:00 | 12.4 | 20.9 | 19
480 | 2022-10-08 08:01 | 12.2 | 21.7 | 20
481 | 2022-10-08 08:02 | 12.3 | 21.8 | 20
482 | 2022-10-08 08:03 | 12.3 | 21.6 | 21
483 | 2022-10-08 08:04 | 12.3 | 21.7 | 21
484 | 2022-10-08 08:05 | 12.4 | 21.8 | 22
485 | 2022-10-08 08:06 | 12.5 | 21.6 | 23
486 | 2022-10-08 08:07 | 12.3 | 21.7 | 23
487 | 2022-10-08 08:08 | 12.4 | 22 | 23
488 | 2022-10-08 08:09 | 12.5 | 21.5 | 23
489 | 2022-10-08 08:10 | 12.8 | 22.3 | 23
490 | 2022-10-08 08:11 | 12.8 | 21.3 | 24
491 | 2022-10-08 08:12 | 12.7 | 21.1 | 24
492 | 2022-10-08 08:13 | 12.7 | 22.3 | 25
493 | 2022-10-08 08:14 | 12.6 | 22.2 | 25
494 | 2022-10-08 08:15 | 12.6 | 22.6 | 25
495 | 2022-10-08 08:16 | 12.8 | 22 | 25
496 | 2022-10-08 08:17 | 12.6 | 21.6 | 26
497 | 2022-10-08 08:18 | 12.8 | 21.8 | 26
498 | 2022-10-08 08:19 | 12.8 | 21.8 | 26
499 | 2022-10-08 08:20 | 12.8 | 20.8 | 27
500 | 2022-10-08 08:21 | 12.7 | 21.5 | 27
501 | 2022-10-08 08:22 | 12.8 | 21.3 | 28
502 | 2022-10-08 08:23 | 12.6 | 21.7 | 28
503 | 2022-10-08 08:24 | 12.6 | 21.6 | 29
504 | 2022-10-08 08:25 | 12.7 | 22.3 | 29
505 | 2022-10-08 08:26 | 12.6 | 21.8 | 30
506 | 2022-10-08 08:27 | 12.9 | 22.3 | 30
507 | 2022-10-08 08:28 | 12.7 | 21.3 | 30
508 | 2022-10-08 08:29 | 12.9 | 21.9 | 31
509 | 2022-10-08 08:30 | 12.7 | 21.6 | 31
510 | 2022-10-08 08:31 | 12.8 | 21.8 | 32
511 | 2022-10-08 08:32 | 12.8 | 21.9 | 32
512 | 2022-10-08 08:33 | 12.7 | 21.8 | 33
513 | 2022-10-08 08:34 | 12.7 | 21.7 | 33
514 | 2022-10-08 08:35 | 12.7 | 21.7 | 34
515 | 2022-10-08 08:36 | 12.9 | 21.8 | 34
516 | 2022-10-08 08:37 | 12.9 | 21.7 | 35
517 | 2022-10-08 08:38 | 12.7 | 21 | 36
518 | 2022-10-08 08:39 | 12.7 | 21.4 | 36
519 | 2022-10-08 08:40 | 12.7 | 22 | 43
520 | 2022-10-08 08:41 | 12.7 | 21.8 | 98
521 | 2022-10-08 08:42 | 12.8 | 21.7 | 174
522 | 2022-10-08 08:43 | 12.7 | 20.9 | 191
523 | 2022-10-08 08:44 | 12.8 | 21.8 | 214
524 | 2022-10-08 08:45 | 12.8 | 21.7 | 254
525 | 2022-10-08 08:46 | 12.9 | 21.9 | 279
526 | 2022-10-08 08:47 | 12.8 | 21.9 | 286
527 | 2022-10-08 08:48 | 13 | 22.3 | 290
528 | 2022-10-08 08:49 | 12.8 | 21.6 | 295
529 | 2022-10-08 08:50 | 13.2 | 22.3 | 300
530 | 2022-10-08 08:51 | 13.6 | 22.1 | 305
531 | 2022-10-08 08:52 | 13.2 | 22.3 | 311
532 | 2022-10-08 08:53 | 13.2 | 21.3 | 315
533 | 2022-10-08 08:54 | 13.7 | 22 | 321
534 | 2022-10-08 08:55 | 13.8 | 20.9 | 325
535 | 2022-10-08 08:56 | 14.2 | 21.9 | 330
536 | 2022-10-08 08:57 | 14.1 | 21.9 | 335
537 | 2022-10-08 08:58 | 14 | 21.9 | 339
538 | 2022-10-08 08:59 | 14.3 | 21.9 | 343
539 | 2022-10-08 09:00 | 15 | 21.7 | 347
540 | 2022-10-08 09:01 | 15 | 22.3 | 351
541 | 2022-10-08 09:02 | 15.3 | 21.1 | 357
542 | 2022-10-08 09:03 | 14.8 | 21 | 363
543 | 2022-10-08 09:04 | 14.9 | 21.1 | 364
544 | 2022-10-08 09:05 | 15.2 | 22 | 368
545 | 2022-10-08 09:06 | 15.1 | 22.4 | 372
546 | 2022-10-08 09:07 | 15.1 | 22 | 375
547 | 2022-10-08 09:08 | 15.2 | 22.1 | 380
548 | 2022-10-08 09:09 | 15.8 | 22.1 | 383
549 | 2022-10-08 09:10 | 15.9 | 21.1 | 386
550 | 2022-10-08 09:11 | 15.8 | 21.5 | 390
551 | 2022-10-08 09:12 | 16.3 | 21 | 395
552 | 2022-10-08 09:13 | 16.1 | 22 | 402
553 | 2022-10-08 09:14 | 16.1 | 21.9 | 406
554 | 2022-10-08 09:15 | 16.5 | 21.7 | 410
555 | 2022-10-08 09:16 | 16.8 | 21.8 | 414
556 | 2022-10-08 09:17 | 16.8 | 21.6 | 418
557 | 2022-10-08 09:18 | 16.8 | 21.5 | 424
558 | 2022-10-08 09:19 | 16.8 | 21.2 | 428
559 | 2022-10-08 09:20 | 16.7 | 21.7 | 431
560 | 2022-10-08 09:21 | 16.7 | 21.9 | 435
561 | 2022-10-08 09:22 | 17 | 22.2 | 440
562 | 2022-10-08 09:23 | 17.5 | 21.9 | 444
563 | 2022-10-08 09:24 | 17.9 | 21.9 | 450
564 | 2022-10-08 09:25 | 18 | 21.4 | 451
565 | 2022-10-08 09:26 | 18.4 | 22.4 | 456
566 | 2022-10-08 09:27 | 18.6 | 22.4 | 461
567 | 2022-10-08 09:28 | 18.9 | 21.8 | 465
568 | 2022-10-08 09:29 | 19 | 22.2 | 469
569 | 2022-10-08 09:30 | 19.1 | 22 | 472
570 | 2022-10-08 09:31 | 19.3 | 21.7 | 473
571 | 2022-10-08 09:32 | 19.6 | 22.4 | 477
572 | 2022-10-08 09:33 | 19.9 | 21.3 | 489
573 | 2022-10-08 09:34 | 19.6 | 21.7 | 491
574 | 2022-10-08 09:35 | 19.8 | 21.7 | 494
575 | 2022-10-08 09:36 | 19.8 | 21.9 | 497
576 | 2022-10-08 09:37 | 19.7 | 21.2 | 502
577 | 2022-10-08 09:38 | 19.6 | 21.4 | 501
578 | 2022-10-08 09:39 | 20 | 21.8 | 504
579 | 2022-10-08 09:40 | 20.3 | 21.8 | 514
580 | 2022-10-08 09:41 | 20.4 | 22 | 518
581 | 2022-10-08 09:42 | 20.4 | 21.8 | 521
582 | 2022-10-08 09:43 | 20.7 | 21.9 | 526
583 | 2022-10-08 09:44 | 20.3 | 22.5 | 527
584 | 2022-10-08 09:45 | 20.4 | 22.5 | 534
585 | 2022-10-08 09:46 | 20.3 | 22.2 | 537
586 | 2022-10-08 09:47 | 20.6 | 22 | 540
587 | 2022-10-08 09:48 | 20.8 | 21.8 | 546
588 | 2022-10-08 09:49 | 20.9 | 21.6 | 554
589 | 2022-10-08 09:50 | 20.8 | 22.5 | 560
590 | 2022-10-08 09:51 | 20.9 | 21.7 | 562
591 | 2022-10-08 09:52 | 20.7 | 22 | 566
592 | 2022-10-08 09:53 | 20.5 | 21.5 | 567
593 | 2022-10-08 09:54 | 20.7 | 21.9 | 571
594 | 2022-10-08 09:55 | 20.6 | 21.4 | 575
595 | 2022-10-08 09:56 | 20.7 | 21.9 | 582
596 | 2022-10-08 09:57 | 20.7 | 22.7 | 583
597 | 2022-10-08 09:58 | 20.9 | 21.9 | 590
598 | 2022-10-08 09:59 | 21.2 | 22 | 588
599 | 2022-10-08 10:00 | 21.3 | 21.2 | 593
600 | 2022-10-08 10:01 | 21 | 22.3 | 601
601 | 2022-10-08 10:02 | 21.1 | 21.6 | 602
602 | 2022-10-08 10:03 | 21 | 22.5 | 608
603 | 2022-10-08 10:04 | 21.5 | 21.3 | 611
604 | 2022-10-08 10:05 | 21.6 | 21 | 613
605 | 2022-10-08 10:06 | 21.2 | 21.9 | 618
606 | 2022-10-08 10:07 | 21.1 | 21.9 | 622
607 | 2022-10-08 10:08 | 21.1 | 21.3 | 621
608 | 2022-10-08 10:09 | 20.8 | 22.2 | 628
609 | 2022-10-08 10:10 | 21.1 | 22.5 | 633
610 | 2022-10-08 10:11 | 21.1 | 21.6 | 639
611 | 2022-10-08 10:12 | 21 | 21.1 | 643
612 | 2022-10-08 10:13 | 21 | 22.2 | 642
613 | 2022-10-08 10:14 | 20.9 | 21.7 | 647
614 | 2022-10-08 10:15 | 20.4 | 21.7 | 655
615 | 2022-10-08 10:16 | 20.9 | 21.4 | 657
616 | 2022-10-08 10:17 | 20.7 | 21.7 | 659
617 | 2022-10-08 10:18 | 20.9 | 21.2 | 660
618 | 2022-10-08 10:19 | 21.4 | 21.8 | 664
619 | 2022-10-08 10:20 | 21.5 | 22.2 | 668
620 | 2022-10-08 10:21 | 21.5 | 21.7 | 672
621 | 2022-10-08 10:22 | 21.2 | 22 | 675
622 | 2022-10-08 10:23 | 21.3 | 21.8 | 677
623 | 2022-10-08 10:24 | 21.3 | 22.2 | 675
624 | 2022-10-08 10:25 | 21.3 | 21.9 | 678
625 | 2022-10-08 10:26 | 21.4 | 21.8 | 685
626 | 2022-10-08 10:27 | 21.9 | 21.8 | 693
627 | 2022-10-08 10:28 | 21.5 | 21.9 | 691
628 | 2022-10-08 10:29 | 21.1 | 21.7 | 696
629 | 2022-10-08 10:30 | 20.9 | 21.8 | 701
630 | 2022-10-08 10:31 | 20.9 | 21.6 | 701
631 | 2022-10-08 10:32 | 20.7 | 21.7 | 704
632 | 2022-10-08 10:33 | 21 | 21.7 | 712
633 | 2022-10-08 10:34 | 20.9 | 21.7 | 717
634 | 2022-10-08 10:35 | 21.5 | 21.7 | 709
635 | 2022-10-08 10:36 | 21.3 | 21.5 | 722
636 | 2022-10-08 10:37 | 21.4 | 22.1 | 726
637 | 2022-10-08 10:38 | 21.8 | 22 | 731
638 | 2022-10-08 10:39 | 22 | 21.9 | 729
639 | 2022-10-08 10:40 | 21.9 | 21.9 | 732
640 | 2022-10-08 10:41 | 21.6 | 21.6 | 740
641 | 2022-10-08 10:42 | 21.4 | 21.9 | 739
642 | 2022-10-08 10:43 | 21.8 | 21.9 | 743
643 | 2022-10-08 10:44 | 21.7 | 21.8 | 748
644 | 2022-10-08 10:45 | 21.4 | 21.8 | 749
645 | 2022-10-08 10:46 | 21.9 | 21.9 | 754
646 | 2022-10-08 10:47 | 22 | 21.7 | 754
647 | 2022-10-08 10:48 | 22.6 | 21.7 | 762
648 | 2022-10-08 10:49 | 22.7 | 21.9 | 762
649 | 2022-10-08 10:50 | 22.3 | 21.9 | 775
650 | 2022-10-08 10:51 | 22.1 | 21.7 | 777
651 | 2022-10-08 10:52 | 22.2 | 21.7 | 778
652 | 2022-10-08 10:53 | 22.1 | 21.8 | 782
653 | 2022-10-08 10:54 | 22.6 | 21.9 | 788
654 | 2022-10-08 10:55 | 22.8 | 21.7 | 790
655 | 2022-10-08 10:56 | 22.9 | 22 | 794
656 | 2022-10-08 10:57 | 22.8 | 21.9 | 794
657 | 2022-10-08 10:58 | 23.1 | 21.8 | 799
658 | 2022-10-08 10:59 | 23 | 22.1 | 805
659 | 2022-10-08 11:00 | 22.6 | 21.2 | 808
660 | 2022-10-08 11:01 | 22.9 | 21.1 | 811
661 | 2022-10-08 11:02 | 23.1 | 21.8 | 821
662 | 2022-10-08 11:03 | 22.9 | 22.1 | 824
663 | 2022-10-08 11:04 | 22.8 | 21.8 | 834
664 | 2022-10-08 11:05 | 22.7 | 21.9 | 832
665 | 2022-10-08 11:06 | 22.8 | 21.8 | 838
666 | 2022-10-08 11:07 | 22.4 | 21.9 | 850
667 | 2022-10-08 11:08 | 22.9 | 22 | 845
668 | 2022-10-08 11:09 | 22.9 | 22 | 841
669 | 2022-10-08 11:10 | 22.5 | 21.9 | 838
670 | 2022-10-08 11:11 | 22.7 | 22 | 851
671 | 2022-10-08 11:12 | 23.1 | 21.8 | 839
672 | 2022-10-08 11:13 | 22.8 | 21.8 | 837
673 | 2022-10-08 11:14 | 22.6 | 21.8 | 856
674 | 2022-10-08 11:15 | 22.7 | 21.4 | 859
675 | 2022-10-08 11:16 | 22.5 | 21.6 | 859
676 | 2022-10-08 11:17 | 22.6 | 22.4 | 858
677 | 2022-10-08 11:18 | 22.6 | 21.3 | 863
678 | 2022-10-08 11:19 | 23.1 | 22 | 898
679 | 2022-10-08 11:20 | 22.9 | 21.5 | 179
680 | 2022-10-08 11:21 | 22.7 | 21.3 | 922
681 | 2022-10-08 11:22 | 21.7 | 22 | 146
682 | 2022-10-08 11:23 | 22.1 | 21.7 | 931
683 | 2022-10-08 11:24 | 21.9 | 22.3 | 238
684 | 2022-10-08 11:25 | 21.5 | 21.9 | 160
685 | 2022-10-08 11:26 | 21.4 | 22.1 | 177
686 | 2022-10-08 11:27 | 21.5 | 21.7 | 513
687 | 2022-10-08 11:28 | 21.4 | 22.1 | 973
688 | 2022-10-08 11:29 | 22 | 22 | 986
689 | 2022-10-08 11:30 | 22.5 | 22 | 1004
690 | 2022-10-08 11:31 | 22.6 | 22.2 | 761
691 | 2022-10-08 11:32 | 22.8 | 22.1 | 978
692 | 2022-10-08 11:33 | 22.4 | 21.6 | 967
693 | 2022-10-08 11:34 | 22.4 | 22.2 | 723
694 | 2022-10-08 11:35 | 22.6 | 22 | 962
695 | 2022-10-08 11:36 | 22.6 | 22.3 | 947
696 | 2022-10-08 11:37 | 23.1 | 22.2 | 781
697 | 2022-10-08 11:38 | 22.7 | 22.2 | 924
698 | 2022-10-08 11:39 | 22.8 | 21.9 | 930
699 | 2022-10-08 11:40 | 23.1 | 22 | 935
700 | 2022-10-08 11:41 | 22.8 | 22 | 898
701 | 2022-10-08 11:42 | 22.7 | 22 | 568
702 | 2022-10-08 11:43 | 22.6 | 22 | 363
703 | 2022-10-08 11:44 | 22.6 | 21.9 | 943
704 | 2022-10-08 11:45 | 22.6 | 21.9 | 932
705 | 2022-10-08 11:46 | 23 | 22 | 928
706 | 2022-10-08 11:47 | 23 | 21.7 | 926
707 | 2022-10-08 11:48 | 23 | 21.9 | 931
708 | 2022-10-08 11:49 | 23.2 | 21.9 | 939
709 | 2022-10-08 11:50 | 23.4 | 21.6 | 940
710 | 2022-10-08 11:51 | 23.5 | 21.6 | 486
711 | 2022-10-08 11:52 | 23.4 | 22 | 957
712 | 2022-10-08 11:53 | 23.5 | 21.6 | 955
713 | 2022-10-08 11:54 | 23.6 | 21.9 | 954
714 | 2022-10-08 11:55 | 23.7 | 22.1 | 951
715 | 2022-10-08 11:56 | 23.8 | 22.1 | 951
716 | 2022-10-08 11:57 | 23.8 | 21.8 | 951
717 | 2022-10-08 11:58 | 23.6 | 21.6 | 951
718 | 2022-10-08 11:59 | 23.8 | 22.1 | 958
719 | 2022-10-08 12:00 | 23.5 | 22.2 | 971
720 | 2022-10-08 12:01 | 23.5 | 21.1 | 957
721 | 2022-10-08 12:02 | 23.3 | 22.4 | 952
722 | 2022-10-08 12:03 | 23.5 | 22.8 | 964
723 | 2022-10-08 12:04 | 23.9 | 22.2 | 959
724 | 2022-10-08 12:05 | 23.7 | 22.1 | 968
725 | 2022-10-08 12:06 | 23.6 | 21.7 | 971
726 | 2022-10-08 12:07 | 23.4 | 21.4 | 970
727 | 2022-10-08 12:08 | 23.2 | 21.8 | 968
728 | 2022-10-08 12:09 | 23.2 | 21.6 | 961
729 | 2022-10-08 12:10 | 23.3 | 22.4 | 968
730 | 2022-10-08 12:11 | 23.5 | 21.9 | 963
731 | 2022-10-08 12:12 | 23.5 | 22 | 966
732 | 2022-10-08 12:13 | 23.3 | 22 | 962
733 | 2022-10-08 12:14 | 22.9 | 22.2 | 965
734 | 2022-10-08 12:15 | 23.5 | 21.4 | 953
735 | 2022-10-08 12:16 | 23.3 | 21.8 | 966
736 | 2022-10-08 12:17 | 23.7 | 21.9 | 957
737 | 2022-10-08 12:18 | 23.4 | 22 | 951
738 | 2022-10-08 12:19 | 23.5 | 22.4 | 960
739 | 2022-10-08 12:20 | 23.8 | 21.3 | 967
740 | 2022-10-08 12:21 | 23.8 | 22 | 963
741 | 2022-10-08 12:22 | 23.6 | 22.1 | 972
742 | 2022-10-08 12:23 | 23.6 | 21.7 | 973
743 | 2022-10-08 12:24 | 23.6 | 21.7 | 971
744 | 2022-10-08 12:25 | 23.8 | 22.1 | 960
745 | 2022-10-08 12:26 | 23.5 | 22.8 | 979
746 | 2022-10-08 12:27 | 23.7 | 22.4 | 973
747 | 2022-10-08 12:28 | 23.8 | 22.1 | 982
748 | 2022-10-08 12:29 | 24 | 22 | 976
749 | 2022-10-08 12:30 | 23.6 | 22 | 981
750 | 2022-10-08 12:31 | 23.3 | 22.1 | 985
751 | 2022-10-08 12:32 | 23.3 | 22.1 | 990
752 | 2022-10-08 12:33 | 23.3 | 21.9 | 990
753 | 2022-10-08 12:34 | 23.5 | 22.8 | 981
754 | 2022-10-08 12:35 | 23.5 | 21.6 | 974
755 | 2022-10-08 12:36 | 23.4 | 21.3 | 993
756 | 2022-10-08 12:37 | 23.9 | 22.1 | 995
757 | 2022-10-08 12:38 | 23.8 | 22 | 993
758 | 2022-10-08 12:39 | 23.9 | 22.8 | 990
759 | 2022-10-08 12:40 | 23.9 | 21.9 | 978
760 | 2022-10-08 12:41 | 24.2 | 22.2 | 984
761 | 2022-10-08 12:42 | 24.2 | 22.1 | 991
762 | 2022-10-08 12:43 | 24.2 | 21.9 | 985
763 | 2022-10-08 12:44 | 23.8 | 21.8 | 987
764 | 2022-10-08 12:45 | 23.9 | 22.3 | 987
765 | 2022-10-08 12:46 | 23.8 | 22 | 980
766 | 2022-10-08 12:47 | 24 | 22 | 988
767 | 2022-10-08 12:48 | 24.2 | 22.1 | 538
768 | 2022-10-08 12:49 | 23.8 | 21.9 | 1001
769 | 2022-10-08 12:50 | 24.3 | 22.1 | 988
770 | 2022-10-08 12:51 | 24.3 | 22.3 | 980
771 | 2022-10-08 12:52 | 24.6 | 22.2 | 987
772 | 2022-10-08 12:53 | 24.4 | 22.2 | 982
773 | 2022-10-08 12:54 | 23.7 | 22.1 | 988
774 | 2022-10-08 12:55 | 23.8 | 21.8 | 995
775 | 2022-10-08 12:56 | 24.1 | 21.9 | 1008
776 | 2022-10-08 12:57 | 24.2 | 21.7 | 1014
777 | 2022-10-08 12:58 | 24.2 | 22.6 | 1006
778 | 2022-10-08 12:59 | 24 | 22.6 | 1005
779 | 2022-10-08 13:00 | 24.2 | 21.4 | 1005
780 | 2022-10-08 13:01 | 24.2 | 22 | 993
781 | 2022-10-08 13:02 | 23.8 | 22.3 | 1001
782 | 2022-10-08 13:03 | 24.1 | 21.8 | 1009
783 | 2022-10-08 13:04 | 23.9 | 21.2 | 1005
784 | 2022-10-08 13:05 | 24.1 | 22 | 1003
785 | 2022-10-08 13:06 | 23.5 | 22.4 | 1012
786 | 2022-10-08 13:07 | 23.5 | 22.5 | 999
787 | 2022-10-08 13:08 | 23.6 | 21.2 | 1001
788 | 2022-10-08 13:09 | 23.3 | 21.9 | 995
789 | 2022-10-08 13:10 | 23.5 | 21.7 | 1001
790 | 2022-10-08 13:11 | 24 | 21.7 | 1000
791 | 2022-10-08 13:12 | 24 | 22 | 1005
792 | 2022-10-08 13:13 | 24.2 | 22.4 | 997
793 | 2022-10-08 13:14 | 23.9 | 21.9 | 997
794 | 2022-10-08 13:15 | 24.1 | 21.8 | 990
795 | 2022-10-08 13:16 | 23.9 | 22 | 1005
796 | 2022-10-08 13:17 | 23.7 | 22.2 | 997
797 | 2022-10-08 13:18 | 23.8 | 21.9 | 1003
798 | 2022-10-08 13:19 | 24.3 | 22 | 1013
799 | 2022-10-08 13:20 | 24 | 22.7 | 1015
800 | 2022-10-08 13:21 | 24 | 22.5 | 1010
801 | 2022-10-08 13:22 | 24.3 | 22 | 1010
802 | 2022-10-08 13:23 | 24 | 21.9 | 1008
803 | 2022-10-08 13:24 | 24.4 | 21.8 | 1011
804 | 2022-10-08 13:25 | 24.2 | 22.3 | 1008
805 | 2022-10-08 13:26 | 24.3 | 21.4 | 1012
806 | 2022-10-08 13:27 | 24.2 | 22.1 | 1008
807 | 2022-10-08 13:28 | 23.7 | 22.9 | 1008
808 | 2022-10-08 13:29 | 24.1 | 22.2 | 1010
809 | 2022-10-08 13:30 | 23.5 | 22.3 | 1009
810 | 2022-10-08 13:31 | 23.4 | 21.8 | 1007
811 | 2022-10-08 13:32 | 23.7 | 21.8 | 1007
812 | 2022-10-08 13:33 | 23.8 | 22.1 | 1009
813 | 2022-10-08 13:34 | 24.1 | 21.4 | 1004
814 | 2022-10-08 13:35 | 23.8 | 21.4 | 1004
815 | 2022-10-08 13:36 | 23.7 | 22.3 | 1007
816 | 2022-10-08 13:37 | 23.6 | 22.9 | 1001
817 | 2022-10-08 13:38 | 23.9 | 22.3 | 998
818 | 2022-10-08 13:39 | 23.8 | 21.9 | 994
819 | 2022-10-08 13:40 | 24 | 22 | 991
820 | 2022-10-08 13:41 | 23.7 | 21.8 | 1001
821 | 2022-10-08 13:42 | 24.4 | 22.4 | 1002
822 | 2022-10-08 13:43 | 24.6 | 22.3 | 1003
823 | 2022-10-08 13:44 | 23.9 | 21.5 | 1001
824 | 2022-10-08 13:45 | 24.4 | 22.8 | 999
825 | 2022-10-08 13:46 | 24.6 | 22.1 | 994
826 | 2022-10-08 13:47 | 24.7 | 22.3 | 993
827 | 2022-10-08 13:48 | 24.7 | 21.8 | 992
828 | 2022-10-08 13:49 | 24.7 | 21.9 | 992
829 | 2022-10-08 13:50 | 24.4 | 21.9 | 990
830 | 2022-10-08 13:51 | 24.5 | 21.9 | 993
831 | 2022-10-08 13:52 | 24.3 | 22 | 994
832 | 2022-10-08 13:53 | 24 | 22.2 | 1001
833 | 2022-10-08 13:54 | 24.3 | 22.3 | 997
834 | 2022-10-08 13:55 | 24.1 | 22.2 | 994
835 | 2022-10-08 13:56 | 24.3 | 22.3 | 992
836 | 2022-10-08 13:57 | 24.5 | 22.3 | 992
837 | 2022-10-08 13:58 | 24.4 | 22.1 | 989
838 | 2022-10-08 13:59 | 24.6 | 22.2 | 983
839 | 2022-10-08 14:00 | 24.7 | 21.7 | 981
840 | 2022-10-08 14:01 | 24.2 | 22.1 | 980
841 | 2022-10-08 14:02 | 24.8 | 22.3 | 971
842 | 2022-10-08 14:03 | 24.9 | 22.4 | 968
843 | 2022-10-08 14:04 | 25 | 22.1 | 966
844 | 2022-10-08 14:05 | 24.6 | 22.1 | 969
845 | 2022-10-08 14:06 | 24.3 | 22.2 | 966
846 | 2022-10-08 14:07 | 24.1 | 22.6 | 967
847 | 2022-10-08 14:08 | 24.1 | 22.4 | 982
848 | 2022-10-08 14:09 | 24.2 | 22.5 | 980
849 | 2022-10-08 14:10 | 24.5 | 21.6 | 980
850 | 2022-10-08 14:11 | 24.4 | 21.6 | 977
851 | 2022-10-08 14:12 | 24.7 | 22.6 | 977
852 | 2022-10-08 14:13 | 24.7 | 21.6 | 975
853 | 2022-10-08 14:14 | 24.9 | 22.6 | 972
854 | 2022-10-08 14:15 | 24.8 | 22.3 | 974
855 | 2022-10-08 14:16 | 24.5 | 22.3 | 971
856 | 2022-10-08 14:17 | 24.6 | 22.1 | 969
857 | 2022-10-08 14:18 | 24.7 | 22.2 | 968
858 | 2022-10-08 14:19 | 24.9 | 22 | 964
859 | 2022-10-08 14:20 | 25 | 22.2 | 964
860 | 2022-10-08 14:21 | 25 | 22.9 | 964
861 | 2022-10-08 14:22 | 24.9 | 22 | 958
862 | 2022-10-08 14:23 | 24.4 | 21.8 | 956
863 | 2022-10-08 14:24 | 24.5 | 22.2 | 956
864 | 2022-10-08 14:25 | 24.5 | 22.5 | 955
865 | 2022-10-08 14:26 | 24.9 | 22.3 | 952
866 | 2022-10-08 14:27 | 25.2 | 21.7 | 948
867 | 2022-10-08 14:28 | 25.4 | 22.8 | 946
868 | 2022-10-08 14:29 | 24.7 | 22.1 | 946
869 | 2022-10-08 14:30 | 25 | 22.7 | 947
870 | 2022-10-08 14:31 | 24.8 | 21.6 | 944
871 | 2022-10-08 14:32 | 25 | 22.2 | 941
872 | 2022-10-08 14:33 | 24.7 | 22.3 | 937
873 | 2022-10-08 14:34 | 24.8 | 21.4 | 936
874 | 2022-10-08 14:35 | 24.9 | 22.3 | 934
875 | 2022-10-08 14:36 | 25.2 | 22.2 | 931
876 | 2022-10-08 14:37 | 25 | 22.3 | 928
877 | 2022-10-08 14:38 | 25.1 | 22.5 | 921
878 | 2022-10-08 14:39 | 25.4 | 22.1 | 921
879 | 2022-10-08 14:40 | 25.5 | 22.6 | 918
880 | 2022-10-08 14:41 | 25.2 | 22.1 | 922
881 | 2022-10-08 14:42 | 25 | 22.4 | 922
882 | 2022-10-08 14:43 | 24.7 | 22.6 | 924
883 | 2022-10-08 14:44 | 24.3 | 22 | 921
884 | 2022-10-08 14:45 | 24.5 | 22.1 | 924
885 | 2022-10-08 14:46 | 23.7 | 21.9 | 916
886 | 2022-10-08 14:47 | 23.8 | 21.8 | 913
887 | 2022-10-08 14:48 | 24.1 | 22 | 919
888 | 2022-10-08 14:49 | 24.4 | 22.7 | 915
889 | 2022-10-08 14:50 | 24.4 | 22.1 | 914
890 | 2022-10-08 14:51 | 24.5 | 22.5 | 906
891 | 2022-10-08 14:52 | 24.7 | 22.2 | 899
892 | 2022-10-08 14:53 | 24.3 | 21.9 | 897
893 | 2022-10-08 14:54 | 24.4 | 21.4 | 896
894 | 2022-10-08 14:55 | 24.6 | 21.8 | 895
895 | 2022-10-08 14:56 | 24.6 | 22 | 898
896 | 2022-10-08 14:57 | 24.5 | 23.1 | 896
897 | 2022-10-08 14:58 | 24.8 | 23.1 | 898
898 | 2022-10-08 14:59 | 24.9 | 21.9 | 892
899 | 2022-10-08 15:00 | 25.1 | 21.8 | 887
900 | 2022-10-08 15:01 | 24.8 | 22.8 | 889
901 | 2022-10-08 15:02 | 25 | 21.9 | 886
902 | 2022-10-08 15:03 | 24.8 | 22.3 | 882
903 | 2022-10-08 15:04 | 24.3 | 21.9 | 882
904 | 2022-10-08 15:05 | 24.5 | 22.4 | 877
905 | 2022-10-08 15:06 | 24.3 | 22.1 | 877
906 | 2022-10-08 15:07 | 24.7 | 21.5 | 877
907 | 2022-10-08 15:08 | 25 | 22.6 | 866
908 | 2022-10-08 15:09 | 24.7 | 23 | 863
909 | 2022-10-08 15:10 | 24.8 | 22.1 | 861
910 | 2022-10-08 15:11 | 25.2 | 22.9 | 861
911 | 2022-10-08 15:12 | 25 | 23.1 | 860
912 | 2022-10-08 15:13 | 25 | 23.2 | 857
913 | 2022-10-08 15:14 | 25.1 | 23 | 855
914 | 2022-10-08 15:15 | 25.3 | 22.1 | 852
915 | 2022-10-08 15:16 | 25.1 | 21.6 | 848
916 | 2022-10-08 15:17 | 24.8 | 22.1 | 846
917 | 2022-10-08 15:18 | 24.8 | 22.1 | 840
918 | 2022-10-08 15:19 | 25.1 | 22.4 | 839
919 | 2022-10-08 15:20 | 25.5 | 22.1 | 837
920 | 2022-10-08 15:21 | 25.6 | 22.2 | 833
921 | 2022-10-08 15:22 | 25.4 | 22 | 831
922 | 2022-10-08 15:23 | 24.4 | 22.5 | 829
923 | 2022-10-08 15:24 | 24.5 | 22.6 | 827
924 | 2022-10-08 15:25 | 24.5 | 22.1 | 820
925 | 2022-10-08 15:26 | 24.7 | 22.2 | 815
926 | 2022-10-08 15:27 | 24.6 | 21.6 | 813
927 | 2022-10-08 15:28 | 25.1 | 22.4 | 808
928 | 2022-10-08 15:29 | 24.9 | 22.2 | 805
929 | 2022-10-08 15:30 | 24.8 | 22.4 | 802
930 | 2022-10-08 15:31 | 24.7 | 21.7 | 807
931 | 2022-10-08 15:32 | 25 | 22.2 | 808
932 | 2022-10-08 15:33 | 25.2 | 22.5 | 803
933 | 2022-10-08 15:34 | 24.9 | 22 | 796
934 | 2022-10-08 15:35 | 24.6 | 22.8 | 795
935 | 2022-10-08 15:36 | 24.8 | 22.9 | 791
936 | 2022-10-08 15:37 | 24.8 | 23.2 | 787
937 | 2022-10-08 15:38 | 24.3 | 22.5 | 782
938 | 2022-10-08 15:39 | 24.1 | 21.7 | 778
939 | 2022-10-08 15:40 | 24.3 | 22.6 | 773
940 | 2022-10-08 15:41 | 24.2 | 22.1 | 768
941 | 2022-10-08 15:42 | 24.2 | 22.4 | 769
942 | 2022-10-08 15:43 | 24.7 | 21.6 | 762
943 | 2022-10-08 15:44 | 25 | 21.6 | 760
944 | 2022-10-08 15:45 | 24.8 | 22.2 | 756
945 | 2022-10-08 15:46 | 24.8 | 23 | 750
946 | 2022-10-08 15:47 | 24.8 | 23.1 | 745
947 | 2022-10-08 15:48 | 24.6 | 22.9 | 743
948 | 2022-10-08 15:49 | 25 | 22 | 740
949 | 2022-10-08 15:50 | 25.1 | 22.5 | 733
950 | 2022-10-08 15:51 | 24.8 | 22.6 | 733
951 | 2022-10-08 15:52 | 24.7 | 22.6 | 732
952 | 2022-10-08 15:53 | 24.6 | 22.4 | 730
953 | 2022-10-08 15:54 | 24.6 | 21.8 | 730
954 | 2022-10-08 15:55 | 24.1 | 22.1 | 728
955 | 2022-10-08 15:56 | 24.3 | 22.3 | 726
956 | 2022-10-08 15:57 | 24.5 | 21.6 | 719
957 | 2022-10-08 15:58 | 24.1 | 22.9 | 715
958 | 2022-10-08 15:59 | 24.3 | 22.7 | 711
959 | 2022-10-08 16:00 | 24.4 | 22.3 | 706
960 | 2022-10-08 16:01 | 24.6 | 22.4 | 704
961 | 2022-10-08 16:02 | 24.1 | 22 | 700
962 | 2022-10-08 16:03 | 24.1 | 22.2 | 696
963 | 2022-10-08 16:04 | 24.3 | 22.4 | 690
964 | 2022-10-08 16:05 | 24.4 | 22.2 | 684
965 | 2022-10-08 16:06 | 24.2 | 21.7 | 680
966 | 2022-10-08 16:07 | 24.1 | 22.6 | 674
967 | 2022-10-08 16:08 | 24.5 | 22.7 | 673
968 | 2022-10-08 16:09 | 24.4 | 22.3 | 672
969 | 2022-10-08 16:10 | 24.2 | 22.4 | 670
970 | 2022-10-08 16:11 | 24.4 | 22.6 | 666
971 | 2022-10-08 16:12 | 24.3 | 21.7 | 663
972 | 2022-10-08 16:13 | 24.7 | 22.5 | 659
973 | 2022-10-08 16:14 | 24.5 | 22.3 | 657
974 | 2022-10-08 16:15 | 24.5 | 22 | 656
975 | 2022-10-08 16:16 | 24.5 | 22.7 | 653
976 | 2022-10-08 16:17 | 24.3 | 23.2 | 645
977 | 2022-10-08 16:18 | 24.1 | 21.9 | 640
978 | 2022-10-08 16:19 | 24.4 | 22.2 | 633
979 | 2022-10-08 16:20 | 24.1 | 22.2 | 630
980 | 2022-10-08 16:21 | 23.8 | 22.4 | 629
981 | 2022-10-08 16:22 | 23.9 | 22.4 | 626
982 | 2022-10-08 16:23 | 23.5 | 22.2 | 621
983 | 2022-10-08 16:24 | 23.6 | 22.3 | 614
984 | 2022-10-08 16:25 | 23.5 | 22.3 | 607
985 | 2022-10-08 16:26 | 23.4 | 22 | 604
986 | 2022-10-08 16:27 | 23.8 | 22.9 | 601
987 | 2022-10-08 16:28 | 24.1 | 21.8 | 599
988 | 2022-10-08 16:29 | 24.5 | 22.9 | 594
989 | 2022-10-08 16:30 | 24.6 | 23 | 591
990 | 2022-10-08 16:31 | 24.5 | 22.8 | 586
991 | 2022-10-08 16:32 | 24.1 | 22.9 | 581
992 | 2022-10-08 16:33 | 24.1 | 21.9 | 577
993 | 2022-10-08 16:34 | 24 | 22.9 | 572
994 | 2022-10-08 16:35 | 23.8 | 22.2 | 568
995 | 2022-10-08 16:36 | 24.1 | 22.3 | 565
996 | 2022-10-08 16:37 | 24 | 22 | 561
997 | 2022-10-08 16:38 | 24 | 22.4 | 559
998 | 2022-10-08 16:39 | 24 | 22.3 | 557
999 | 2022-10-08 16:40 | 23.9 | 22.3 | 553
1000 | 2022-10-08 16:41 | 24.1 | 22.4 | 548
1001 | 2022-10-08 16:42 | 24.4 | 22.3 | 542
1002 | 2022-10-08 16:43 | 23.9 | 22 | 537
1003 | 2022-10-08 16:44 | 24.1 | 22 | 532
1004 | 2022-10-08 16:45 | 24.5 | 22.2 | 527
1005 | 2022-10-08 16:46 | 24.8 | 22.7 | 522
1006 | 2022-10-08 16:47 | 24.6 | 23.2 | 517
1007 | 2022-10-08 16:48 | 24.3 | 22.5 | 514
1008 | 2022-10-08 16:49 | 24.5 | 22.5 | 510
1009 | 2022-10-08 16:50 | 24.6 | 22.6 | 507
1010 | 2022-10-08 16:51 | 24.4 | 22.2 | 503
1011 | 2022-10-08 16:52 | 24.1 | 22.4 | 500
1012 | 2022-10-08 16:53 | 24.1 | 22.5 | 495
1013 | 2022-10-08 16:54 | 23.9 | 21.9 | 491
1014 | 2022-10-08 16:55 | 24.1 | 22.3 | 486
1015 | 2022-10-08 16:56 | 24.2 | 22.1 | 482
1016 | 2022-10-08 16:57 | 24.3 | 22.3 | 478
1017 | 2022-10-08 16:58 | 24.1 | 23.2 | 474
1018 | 2022-10-08 16:59 | 24 | 22.5 | 470
1019 | 2022-10-08 17:00 | 24 | 21.8 | 464
1020 | 2022-10-08 17:01 | 23.8 | 22.4 | 459
1021 | 2022-10-08 17:02 | 23.7 | 22.4 | 455
1022 | 2022-10-08 17:03 | 23.4 | 22.3 | 451
1023 | 2022-10-08 17:04 | 23.6 | 22.3 | 449
1024 | 2022-10-08 17:05 | 23.8 | 22.4 | 445
1025 | 2022-10-08 17:06 | 24.2 | 22.5 | 441
1026 | 2022-10-08 17:07 | 24.2 | 22.3 | 438
1027 | 2022-10-08 17:08 | 24.2 | 22.2 | 431
1028 | 2022-10-08 17:09 | 23.8 | 22.3 | 427
1029 | 2022-10-08 17:10 | 24.1 | 22.1 | 423
1030 | 2022-10-08 17:11 | 24 | 21.8 | 420
1031 | 2022-10-08 17:12 | 23.4 | 22.4 | 416
1032 | 2022-10-08 17:13 | 23.6 | 22.9 | 413
1033 | 2022-10-08 17:14 | 23.8 | 22.7 | 409
1034 | 2022-10-08 17:15 | 23.7 | 21.9 | 406
1035 | 2022-10-08 17:16 | 24 | 22.4 | 400
1036 | 2022-10-08 17:17 | 24 | 22.3 | 395
1037 | 2022-10-08 17:18 | 23.6 | 23 | 390
1038 | 2022-10-08 17:19 | 23.8 | 22.3 | 385
1039 | 2022-10-08 17:20 | 23.1 | 22 | 382
1040 | 2022-10-08 17:21 | 23.1 | 22.3 | 377
1041 | 2022-10-08 17:22 | 23.4 | 22.4 | 373
1042 | 2022-10-08 17:23 | 23.1 | 22.3 | 369
1043 | 2022-10-08 17:24 | 23.4 | 22.5 | 364
1044 | 2022-10-08 17:25 | 23.3 | 22.2 | 358
1045 | 2022-10-08 17:26 | 23.1 | 22.1 | 354
1046 | 2022-10-08 17:27 | 23.3 | 22.3 | 350
1047 | 2022-10-08 17:28 | 23.5 | 22.4 | 342
1048 | 2022-10-08 17:29 | 23.4 | 22.1 | 338
1049 | 2022-10-08 17:30 | 23.5 | 22.2 | 334
1050 | 2022-10-08 17:31 | 23.5 | 22.4 | 329
1051 | 2022-10-08 17:32 | 23 | 22.9 | 325
1052 | 2022-10-08 17:33 | 23.3 | 22.8 | 321
1053 | 2022-10-08 17:34 | 22.8 | 23.1 | 317
1054 | 2022-10-08 17:35 | 22.8 | 22.3 | 312
1055 | 2022-10-08 17:36 | 22.6 | 22.1 | 308
1056 | 2022-10-08 17:37 | 22.5 | 22.2 | 302
1057 | 2022-10-08 17:38 | 22.7 | 22 | 297
1058 | 2022-10-08 17:39 | 22.9 | 22.2 | 292
1059 | 2022-10-08 17:40 | 22.9 | 22.6 | 288
1060 | 2022-10-08 17:41 | 22.7 | 22.5 | 282
1061 | 2022-10-08 17:42 | 22.9 | 22.4 | 279
1062 | 2022-10-08 17:43 | 22.9 | 22.4 | 273
1063 | 2022-10-08 17:44 | 22.9 | 22.4 | 269
1064 | 2022-10-08 17:45 | 22.7 | 22.2 | 266
1065 | 2022-10-08 17:46 | 22.4 | 22.6 | 261
1066 | 2022-10-08 17:47 | 22.6 | 23 | 256
1067 | 2022-10-08 17:48 | 22.7 | 22.4 | 249
1068 | 2022-10-08 17:49 | 22.5 | 22.1 | 243
1069 | 2022-10-08 17:50 | 22.5 | 21.4 | 238
1070 | 2022-10-08 17:51 | 22.6 | 21.7 | 235
1071 | 2022-10-08 17:52 | 22.5 | 22.1 | 226
1072 | 2022-10-08 17:53 | 22.5 | 22.2 | 225
1073 | 2022-10-08 17:54 | 22.4 | 22.5 | 223
1074 | 2022-10-08 17:55 | 22.7 | 22.2 | 206
1075 | 2022-10-08 17:56 | 22.6 | 22.4 | 205
1076 | 2022-10-08 17:57 | 22.6 | 22.1 | 214
1077 | 2022-10-08 17:58 | 22.6 | 21.6 | 211
1078 | 2022-10-08 17:59 | 22.6 | 22.4 | 206
1079 | 2022-10-08 18:00 | 22.3 | 22.6 | 200
1080 | 2022-10-08 18:01 | 22.5 | 22.6 | 193
1081 | 2022-10-08 18:02 | 22.6 | 22.4 | 190
1082 | 2022-10-08 18:03 | 22.5 | 22.3 | 184
1083 | 2022-10-08 18:04 | 22.3 | 22.7 | 177
1084 | 2022-10-08 18:05 | 22.3 | 22.3 | 173
1085 | 2022-10-08 18:06 | 22.2 | 22.5 | 169
1086 | 2022-10-08 18:07 | 22.4 | 22.9 | 165
1087 | 2022-10-08 18:08 | 22 | 23 | 161
1088 | 2022-10-08 18:09 | 22 | 22 | 156
1089 | 2022-10-08 18:10 | 22.1 | 21.6 | 155
1090 | 2022-10-08 18:11 | 22 | 22.2 | 150
1091 | 2022-10-08 18:12 | 21.8 | 22.6 | 148
1092 | 2022-10-08 18:13 | 21.7 | 22.2 | 145
1093 | 2022-10-08 18:14 | 21.9 | 22.4 | 140
1094 | 2022-10-08 18:15 | 21.6 | 22.9 | 137
1095 | 2022-10-08 18:16 | 21.7 | 21.8 | 133
1096 | 2022-10-08 18:17 | 21.8 | 22.2 | 130
1097 | 2022-10-08 18:18 | 21.7 | 23.2 | 126
1098 | 2022-10-08 18:19 | 21.7 | 22.8 | 122
1099 | 2022-10-08 18:20 | 21.5 | 22.1 | 117
1100 | 2022-10-08 18:21 | 21.7 | 22.2 | 114
1101 | 2022-10-08 18:22 | 21.6 | 22.5 | 109
1102 | 2022-10-08 18:23 | 21.5 | 22.3 | 104
1103 | 2022-10-08 18:24 | 21.6 | 21.9 | 101
1104 | 2022-10-08 18:25 | 21.4 | 21.9 | 97
1105 | 2022-10-08 18:26 | 21.4 | 21.4 | 93
1106 | 2022-10-08 18:27 | 21.3 | 22 | 89
1107 | 2022-10-08 18:28 | 21.3 | 22.3 | 86
1108 | 2022-10-08 18:29 | 21.1 | 22.3 | 82
1109 | 2022-10-08 18:30 | 21.1 | 22.3 | 78
1110 | 2022-10-08 18:31 | 21.1 | 22.5 | 66
1111 | 2022-10-08 18:32 | 20.9 | 22.3 | 42
1112 | 2022-10-08 18:33 | 21 | 22.4 | 32
1113 | 2022-10-08 18:34 | 20.9 | 22.1 | 32
1114 | 2022-10-08 18:35 | 20.7 | 22.4 | 29
1115 | 2022-10-08 18:36 | 20.6 | 22.3 | 21
1116 | 2022-10-08 18:37 | 20.6 | 22.1 | 23
1117 | 2022-10-08 18:38 | 20.7 | 22.4 | 19
1118 | 2022-10-08 18:39 | 20.7 | 22.4 | 17
1119 | 2022-10-08 18:40 | 20.5 | 22.3 | 16
1120 | 2022-10-08 18:41 | 20.3 | 22.3 | 12
1121 | 2022-10-08 18:42 | 20.4 | 22.4 | 11
1122 | 2022-10-08 18:43 | 20.2 | 22.2 | 11
1123 | 2022-10-08 18:44 | 20.3 | 22.3 | 10
1124 | 2022-10-08 18:45 | 20.2 | 22.4 | 8
1125 | 2022-10-08 18:46 | 20.2 | 22.6 | 7
1126 | 2022-10-08 18:47 | 20.2 | 21.7 | 5
1127 | 2022-10-08 18:48 | 20.2 | 21.8 | 5
1128 | 2022-10-08 18:49 | 20 | 22 | 5
1129 | 2022-10-08 18:50 | 19.9 | 22.2 | 5
1130 | 2022-10-08 18:51 | 19.9 | 22.4 | 4
1131 | 2022-10-08 18:52 | 19.8 | 22.2 | 4
1132 | 2022-10-08 18:53 | 20 | 22.3 | 3
1133 | 2022-10-08 18:54 | 19.8 | 22.3 | 2
1134 | 2022-10-08 18:55 | 19.9 | 22.3 | 2
1135 | 2022-10-08 18:56 | 19.7 | 22.2 | 1
1136 | 2022-10-08 18:57 | 19.8 | 22.4 | 0
1137 | 2022-10-08 18:58 | 19.7 | 22.3 | 0
1138 | 2022-10-08 18:59 | 19.6 | 22 | 0
1139 | 2022-10-08 19:00 | 19.6 | 22.8 | 0
1140 | 2022-10-08 19:01 | 19.4 | 22.4 | 0
1141 | 2022-10-08 19:02 | 19.3 | 22.4 | 0
1142 | 2022-10-08 19:03 | 19 | 22.3 | 0
1143 | 2022-10-08 19:04 | 19 | 22.1 | 0
1144 | 2022-10-08 19:05 | 18.8 | 22.2 | 0
1145 | 2022-10-08 19:06 | 18.7 | 22.3 | 0
1146 | 2022-10-08 19:07 | 18.7 | 22.2 | 0
1147 | 2022-10-08 19:08 | 18.6 | 22.2 | 0
1148 | 2022-10-08 19:09 | 18.4 | 22.3 | 0
1149 | 2022-10-08 19:10 | 18.4 | 22.2 | 0
1150 | 2022-10-08 19:11 | 18.3 | 21.7 | 0
1151 | 2022-10-08 19:12 | 18 | 21.6 | 0
1152 | 2022-10-08 19:13 | 18.1 | 22.5 | 0
1153 | 2022-10-08 19:14 | 17.9 | 22.8 | 0
1154 | 2022-10-08 19:15 | 17.8 | 22.6 | 0
1155 | 2022-10-08 19:16 | 17.7 | 22 | 0
1156 | 2022-10-08 19:17 | 17.6 | 22.6 | 0
1157 | 2022-10-08 19:18 | 17.7 | 22.5 | 0
1158 | 2022-10-08 19:19 | 17.7 | 21.8 | 0
1159 | 2022-10-08 19:20 | 17.5 | 22.1 | 0
1160 | 2022-10-08 19:21 | 17.5 | 22.3 | 0
1161 | 2022-10-08 19:22 | 17.4 | 22.2 | 0
1162 | 2022-10-08 19:23 | 17.4 | 22.8 | 0
1163 | 2022-10-08 19:24 | 17.3 | 22.2 | 0
1164 | 2022-10-08 19:25 | 17.2 | 22.9 | 0
1165 | 2022-10-08 19:26 | 17.2 | 22.3 | 0
1166 | 2022-10-08 19:27 | 17.2 | 22.2 | 0
1167 | 2022-10-08 19:28 | 17.1 | 21.9 | 0
1168 | 2022-10-08 19:29 | 17.1 | 22.2 | 0
1169 | 2022-10-08 19:30 | 17 | 22.4 | 0
1170 | 2022-10-08 19:31 | 17 | 21.9 | 0
1171 | 2022-10-08 19:32 | 17 | 22.2 | 0
1172 | 2022-10-08 19:33 | 16.9 | 22.5 | 0
1173 | 2022-10-08 19:34 | 16.8 | 21.7 | 0
1174 | 2022-10-08 19:35 | 16.6 | 22.4 | 0
1175 | 2022-10-08 19:36 | 16.8 | 22 | 0
1176 | 2022-10-08 19:37 | 16.6 | 22.2 | 0
1177 | 2022-10-08 19:38 | 16.6 | 22.4 | 0
1178 | 2022-10-08 19:39 | 16.7 | 22.4 | 0
1179 | 2022-10-08 19:40 | 16.8 | 22.4 | 0
1180 | 2022-10-08 19:41 | 16.7 | 22.3 | 0
1181 | 2022-10-08 19:42 | 16.7 | 22.4 | 0
1182 | 2022-10-08 19:43 | 16.6 | 22.4 | 0
1183 | 2022-10-08 19:44 | 16.7 | 22.2 | 0
1184 | 2022-10-08 19:45 | 16.5 | 22.4 | 0
1185 | 2022-10-08 19:46 | 16.5 | 22.3 | 0
1186 | 2022-10-08 19:47 | 16.5 | 22.2 | 0
1187 | 2022-10-08 19:48 | 16.3 | 22.4 | 0
1188 | 2022-10-08 19:49 | 16.3 | 22.4 | 0
1189 | 2022-10-08 19:50 | 16.2 | 22.3 | 0
1190 | 2022-10-08 19:51 | 16.2 | 22.4 | 0
1191 | 2022-10-08 19:52 | 16.2 | 22.3 | 0
1192 | 2022-10-08 19:53 | 16.1 | 22.3 | 0
1193 | 2022-10-08 19:54 | 16.1 | 22.3 | 0
1194 | 2022-10-08 19:55 | 16.1 | 22.1 | 0
1195 | 2022-10-08 19:56 | 16 | 22.3 | 0
1196 | 2022-10-08 19:57 | 15.9 | 22.3 | 0
1197 | 2022-10-08 19:58 | 15.9 | 22.2 | 0
1198 | 2022-10-08 19:59 | 16 | 22.2 | 0
1199 | 2022-10-08 20:00 | 16 | 22.4 | 0
1200 | 2022-10-08 20:01 | 16 | 22 | 0
1201 | 2022-10-08 20:02 | 16 | 22.2 | 0
1202 | 2022-10-08 20:03 | 15.8 | 22.3 | 0
1203 | 2022-10-08 20:04 | 15.8 | 22.2 | 0
1204 | 2022-10-08 20:05 | 15.8 | 22.3 | 0
1205 | 2022-10-08 20:06 | 15.9 | 22.2 | 0
1206 | 2022-10-08 20:07 | 15.8 | 22.4 | 0
1207 | 2022-10-08 20:08 | 15.9 | 22.2 | 0
1208 | 2022-10-08 20:09 | 15.7 | 22.5 | 0
1209 | 2022-10-08 20:10 | 15.6 | 21.7 | 0
1210 | 2022-10-08 20:11 | 15.7 | 22.6 | 0
1211 | 2022-10-08 20:12 | 15.8 | 22.7 | 0
1212 | 2022-10-08 20:13 | 15.7 | 21.7 | 0
1213 | 2022-10-08 20:14 | 15.6 | 22.3 | 0
1214 | 2022-10-08 20:15 | 15.6 | 22.3 | 0
1215 | 2022-10-08 20:16 | 15.6 | 22.4 | 0
1216 | 2022-10-08 20:17 | 15.6 | 22.9 | 0
1217 | 2022-10-08 20:18 | 15.6 | 22.8 | 0
1218 | 2022-10-08 20:19 | 15.5 | 21.8 | 0
1219 | 2022-10-08 20:20 | 15.7 | 22.9 | 0
1220 | 2022-10-08 20:21 | 15.6 | 22.3 | 0
1221 | 2022-10-08 20:22 | 15.5 | 22.2 | 0
1222 | 2022-10-08 20:23 | 15.5 | 22.3 | 0
1223 | 2022-10-08 20:24 | 15.7 | 22.8 | 0
1224 | 2022-10-08 20:25 | 15.7 | 22 | 0
1225 | 2022-10-08 20:26 | 15.6 | 21.9 | 0
1226 | 2022-10-08 20:27 | 15.7 | 22 | 0
1227 | 2022-10-08 20:28 | 15.7 | 22 | 0
1228 | 2022-10-08 20:29 | 15.9 | 22.7 | 0
1229 | 2022-10-08 20:30 | 15.8 | 22.4 | 0
1230 | 2022-10-08 20:31 | 15.7 | 22 | 0
1231 | 2022-10-08 20:32 | 15.8 | 22.4 | 0
1232 | 2022-10-08 20:33 | 15.9 | 22 | 0
1233 | 2022-10-08 20:34 | 15.7 | 21.8 | 0
1234 | 2022-10-08 20:35 | 15.8 | 22.4 | 0
1235 | 2022-10-08 20:36 | 15.7 | 22.9 | 0
1236 | 2022-10-08 20:37 | 15.8 | 22.5 | 0
1237 | 2022-10-08 20:38 | 15.8 | 22.4 | 0
1238 | 2022-10-08 20:39 | 15.7 | 22.9 | 0
1239 | 2022-10-08 20:40 | 15.7 | 22.8 | 0
1240 | 2022-10-08 20:41 | 15.7 | 22.1 | 0
1241 | 2022-10-08 20:42 | 15.8 | 22 | 0
1242 | 2022-10-08 20:43 | 15.8 | 22.3 | 0
1243 | 2022-10-08 20:44 | 15.8 | 22.2 | 0
1244 | 2022-10-08 20:45 | 15.7 | 22 | 0
1245 | 2022-10-08 20:46 | 15.7 | 21.7 | 0
1246 | 2022-10-08 20:47 | 15.7 | 22.9 | 0
1247 | 2022-10-08 20:48 | 15.8 | 21.9 | 0
1248 | 2022-10-08 20:49 | 15.7 | 22.4 | 0
1249 | 2022-10-08 20:50 | 15.6 | 22.2 | 0
1250 | 2022-10-08 20:51 | 15.6 | 22 | 0
1251 | 2022-10-08 20:52 | 15.7 | 21.6 | 0
1252 | 2022-10-08 20:53 | 15.5 | 22.4 | 0
1253 | 2022-10-08 20:54 | 15.4 | 22.2 | 0
1254 | 2022-10-08 20:55 | 15.5 | 22.4 | 0
1255 | 2022-10-08 20:56 | 15.6 | 22.3 | 0
1256 | 2022-10-08 20:57 | 15.5 | 22.4 | 0
1257 | 2022-10-08 20:58 | 15.4 | 22.2 | 0
1258 | 2022-10-08 20:59 | 15.5 | 21.9 | 0
1259 | 2022-10-08 21:00 | 15.5 | 22.7 | 0
1260 | 2022-10-08 21:01 | 15.7 | 22.8 | 0
1261 | 2022-10-08 21:02 | 15.8 | 22.3 | 0
1262 | 2022-10-08 21:03 | 15.6 | 22.3 | 0
1263 | 2022-10-08 21:04 | 15.5 | 22.2 | 0
1264 | 2022-10-08 21:05 | 15.5 | 22.3 | 0
1265 | 2022-10-08 21:06 | 15.5 | 21.5 | 0
1266 | 2022-10-08 21:07 | 15.7 | 22.4 | 0
1267 | 2022-10-08 21:08 | 15.4 | 22.5 | 0
1268 | 2022-10-08 21:09 | 15.5 | 22.6 | 0
1269 | 2022-10-08 21:10 | 15.4 | 22.7 | 0
1270 | 2022-10-08 21:11 | 15.3 | 22 | 0
1271 | 2022-10-08 21:12 | 15.2 | 22.4 | 0
1272 | 2022-10-08 21:13 | 15.2 | 22.4 | 0
1273 | 2022-10-08 21:14 | 15.2 | 22.1 | 0
1274 | 2022-10-08 21:15 | 15.4 | 22.3 | 0
1275 | 2022-10-08 21:16 | 15.2 | 22 | 0
1276 | 2022-10-08 21:17 | 15.3 | 21.8 | 0
1277 | 2022-10-08 21:18 | 15.3 | 21.6 | 0
1278 | 2022-10-08 21:19 | 15.2 | 22.3 | 0
1279 | 2022-10-08 21:20 | 15.3 | 21.8 | 0
1280 | 2022-10-08 21:21 | 15.3 | 22.1 | 0
1281 | 2022-10-08 21:22 | 15.4 | 22.4 | 0
1282 | 2022-10-08 21:23 | 15.2 | 22 | 0
1283 | 2022-10-08 21:24 | 15.1 | 22.3 | 0
1284 | 2022-10-08 21:25 | 15.1 | 22.2 | 0
1285 | 2022-10-08 21:26 | 15 | 22.1 | 0
1286 | 2022-10-08 21:27 | 15.1 | 22.3 | 0
1287 | 2022-10-08 21:28 | 15.2 | 22.1 | 0
1288 | 2022-10-08 21:29 | 15 | 22 | 0
1289 | 2022-10-08 21:30 | 15 | 22.2 | 0
1290 | 2022-10-08 21:31 | 14.9 | 22.5 | 0
1291 | 2022-10-08 21:32 | 14.9 | 22.9 | 0
1292 | 2022-10-08 21:33 | 14.8 | 22.4 | 0
1293 | 2022-10-08 21:34 | 14.9 | 21.4 | 0
1294 | 2022-10-08 21:35 | 14.9 | 22.3 | 0
1295 | 2022-10-08 21:36 | 14.8 | 22.1 | 0
1296 | 2022-10-08 21:37 | 14.8 | 22.1 | 0
1297 | 2022-10-08 21:38 | 14.8 | 22.2 | 0
1298 | 2022-10-08 21:39 | 14.7 | 22.1 | 0
1299 | 2022-10-08 21:40 | 14.6 | 22.2 | 0
1300 | 2022-10-08 21:41 | 14.7 | 22 | 0
1301 | 2022-10-08 21:42 | 14.6 | 22.1 | 0
1302 | 2022-10-08 21:43 | 14.7 | 22.2 | 0
1303 | 2022-10-08 21:44 | 14.5 | 22.3 | 0
1304 | 2022-10-08 21:45 | 14.5 | 22.1 | 0
1305 | 2022-10-08 21:46 | 14.5 | 22.2 | 0
1306 | 2022-10-08 21:47 | 14.3 | 22.5 | 0
1307 | 2022-10-08 21:48 | 14.4 | 22.1 | 0
1308 | 2022-10-08 21:49 | 14.3 | 22 | 0
1309 | 2022-10-08 21:50 | 14.2 | 22.3 | 0
1310 | 2022-10-08 21:51 | 14.3 | 22.2 | 0
1311 | 2022-10-08 21:52 | 14.3 | 22.2 | 0
1312 | 2022-10-08 21:53 | 14.4 | 22.2 | 0
1313 | 2022-10-08 21:54 | 14.3 | 22.1 | 0
1314 | 2022-10-08 21:55 | 14.1 | 22 | 0
1315 | 2022-10-08 21:56 | 14.4 | 22.1 | 0
1316 | 2022-10-08 21:57 | 14.4 | 22.3 | 0
1317 | 2022-10-08 21:58 | 14.4 | 22 | 0
1318 | 2022-10-08 21:59 | 14.1 | 22.6 | 0
1319 | 2022-10-08 22:00 | 14.2 | 22.1 | 0
1320 | 2022-10-08 22:01 | 14.1 | 22.3 | 0
1321 | 2022-10-08 22:02 | 14.1 | 22.1 | 0
1322 | 2022-10-08 22:03 | 14.1 | 22.1 | 0
1323 | 2022-10-08 22:04 | 14.2 | 22.1 | 0
1324 | 2022-10-08 22:05 | 14.2 | 22.1 | 0
1325 | 2022-10-08 22:06 | 14.1 | 22 | 0
1326 | 2022-10-08 22:07 | 14.2 | 22.2 | 0
1327 | 2022-10-08 22:08 | 14.3 | 21.9 | 0
1328 | 2022-10-08 22:09 | 14.2 | 22.1 | 0
1329 | 2022-10-08 22:10 | 14.1 | 22.2 | 0
1330 | 2022-10-08 22:11 | 14.1 | 22.1 | 0
1331 | 2022-10-08 22:12 | 14.1 | 22.4 | 0
1332 | 2022-10-08 22:13 | 14.2 | 22.8 | 0
1333 | 2022-10-08 22:14 | 14.3 | 22.7 | 0
1334 | 2022-10-08 22:15 | 14.1 | 21.3 | 0
1335 | 2022-10-08 22:16 | 14 | 21.4 | 0
1336 | 2022-10-08 22:17 | 14.2 | 22.2 | 0
1337 | 2022-10-08 22:18 | 14.1 | 22.9 | 0
1338 | 2022-10-08 22:19 | 14.1 | 22.5 | 0
1339 | 2022-10-08 22:20 | 14.1 | 22.7 | 0
1340 | 2022-10-08 22:21 | 14.1 | 22.1 | 0
1341 | 2022-10-08 22:22 | 14.3 | 22 | 0
1342 | 2022-10-08 22:23 | 14.1 | 21.9 | 0
1343 | 2022-10-08 22:24 | 14.1 | 22 | 0
1344 | 2022-10-08 22:25 | 14.1 | 22.2 | 0
1345 | 2022-10-08 22:26 | 14 | 22.3 | 0
1346 | 2022-10-08 22:27 | 13.9 | 22.7 | 0
1347 | 2022-10-08 22:28 | 14 | 22.1 | 0
1348 | 2022-10-08 22:29 | 14 | 22.7 | 0
1349 | 2022-10-08 22:30 | 14 | 22.1 | 0
1350 | 2022-10-08 22:31 | 14.1 | 22.2 | 0
1351 | 2022-10-08 22:32 | 14 | 22 | 0
1352 | 2022-10-08 22:33 | 14.1 | 22.4 | 0
1353 | 2022-10-08 22:34 | 14 | 22.4 | 0
1354 | 2022-10-08 22:35 | 14.2 | 22.4 | 0
1355 | 2022-10-08 22:36 | 14.2 | 21.3 | 0
1356 | 2022-10-08 22:37 | 14 | 22.6 | 0
1357 | 2022-10-08 22:38 | 14.2 | 21.8 | 0
1358 | 2022-10-08 22:39 | 14.2 | 22.2 | 0
1359 | 2022-10-08 22:40 | 14.1 | 21.9 | 0
1360 | 2022-10-08 22:41 | 14.3 | 22.2 | 0
1361 | 2022-10-08 22:42 | 14.3 | 21.9 | 0
1362 | 2022-10-08 22:43 | 14.1 | 21.8 | 0
1363 | 2022-10-08 22:44 | 14 | 22.4 | 0
1364 | 2022-10-08 22:45 | 14.3 | 22.3 | 0
1365 | 2022-10-08 22:46 | 14.1 | 21.8 | 0
1366 | 2022-10-08 22:47 | 14 | 22.3 | 0
1367 | 2022-10-08 22:48 | 14 | 22.1 | 0
1368 | 2022-10-08 22:49 | 14.3 | 22.4 | 0
1369 | 2022-10-08 22:50 | 14.1 | 21.8 | 0
1370 | 2022-10-08 22:51 | 14.2 | 22.9 | 0
1371 | 2022-10-08 22:52 | 14.2 | 22.3 | 0
1372 | 2022-10-08 22:53 | 14.1 | 22 | 0
1373 | 2022-10-08 22:54 | 14.1 | 22.1 | 0
1374 | 2022-10-08 22:55 | 14.1 | 22.3 | 0
1375 | 2022-10-08 22:56 | 14.3 | 22.3 | 0
1376 | 2022-10-08 22:57 | 14.3 | 22 | 0
1377 | 2022-10-08 22:58 | 14.3 | 22.2 | 0
1378 | 2022-10-08 22:59 | 14.1 | 21.8 | 0
1379 | 2022-10-08 23:00 | 14.2 | 22.2 | 0
1380 | 2022-10-08 23:01 | 14.1 | 21.9 | 0
1381 | 2022-10-08 23:02 | 14.1 | 22.1 | 0
1382 | 2022-10-08 23:03 | 14.1 | 21.9 | 0
1383 | 2022-10-08 23:04 | 14.1 | 22.3 | 0
1384 | 2022-10-08 23:05 | 13.9 | 22.2 | 0
1385 | 2022-10-08 23:06 | 13.9 | 21.9 | 0
1386 | 2022-10-08 23:07 | 13.9 | 22.3 | 0
1387 | 2022-10-08 23:08 | 14 | 21.7 | 0
1388 | 2022-10-08 23:09 | 13.9 | 22.2 | 0
1389 | 2022-10-08 23:10 | 14 | 22 | 0
1390 | 2022-10-08 23:11 | 14 | 22.2 | 0
1391 | 2022-10-08 23:12 | 14.2 | 21.8 | 0
1392 | 2022-10-08 23:13 | 14 | 22.2 | 0
1393 | 2022-10-08 23:14 | 14 | 22.2 | 0
1394 | 2022-10-08 23:15 | 14.3 | 21.9 | 0
1395 | 2022-10-08 23:16 | 14.3 | 22.1 | 0
1396 | 2022-10-08 23:17 | 14.3 | 22.1 | 0
1397 | 2022-10-08 23:18 | 14.2 | 22.1 | 0
1398 | 2022-10-08 23:19 | 14.3 | 22.2 | 0
1399 | 2022-10-08 23:20 | 14.1 | 22.1 | 0
1400 | 2022-10-08 23:21 | 14.1 | 22 | 0
1401 | 2022-10-08 23:22 | 14 | 22.1 | 0
1402 | 2022-10-08 23:23 | 14.2 | 21.9 | 0
1403 | 2022-10-08 23:24 | 14.2 | 22 | 0
1404 | 2022-10-08 23:25 | 14.3 | 22.1 | 0
1405 | 2022-10-08 23:26 | 14.1 | 21.9 | 0
1406 | 2022-10-08 23:27 | 14.3 | 22.4 | 0
1407 | 2022-10-08 23:28 | 14.6 | 22.6 | 0
1408 | 2022-10-08 23:29 | 14.5 | 22.7 | 0
1409 | 2022-10-08 23:30 | 14.3 | 21.8 | 0
1410 | 2022-10-08 23:31 | 14.3 | 21.8 | 0
1411 | 2022-10-08 23:32 | 14.4 | 22 | 0
1412 | 2022-10-08 23:33 | 14.3 | 22.1 | 0
1413 | 2022-10-08 23:34 | 14.4 | 22.5 | 0
1414 | 2022-10-08 23:35 | 14.5 | 22.4 | 0
1415 | 2022-10-08 23:36 | 14.9 | 21.9 | 0
1416 | 2022-10-08 23:37 | 14.9 | 21.4 | 0
1417 | 2022-10-08 23:38 | 14.7 | 22.3 | 0
1418 | 2022-10-08 23:39 | 14.6 | 22 | 0
1419 | 2022-10-08 23:40 | 14.8 | 21.9 | 0
1420 | 2022-10-08 23:41 | 14.8 | 22.1 | 0
1421 | 2022-10-08 23:42 | 15.5 | 22.1 | 0
1422 | 2022-10-08 23:43 | 15.6 | 22.1 | 0
1423 | 2022-10-08 23:44 | 15.7 | 21.8 | 0
1424 | 2022-10-08 23:45 | 15.9 | 22.4 | 0
1425 | 2022-10-08 23:46 | 15.9 | 22.4 | 0
1426 | 2022-10-08 23:47 | 15.5 | 21.9 | 0
1427 | 2022-10-08 23:48 | 15.7 | 22.5 | 0
1428 | 2022-10-08 23:49 | 15.6 | 22.9 | 0
1429 | 2022-10-08 23:50 | 15.5 | 22.4 | 0
1430 | 2022-10-08 23:51 | 15.8 | 22.2 | 0
1431 | 2022-10-08 23:52 | 15.8 | 22 | 0
1432 | 2022-10-08 23:53 | 15.7 | 22.6 | 0
1433 | 2022-10-08 23:54 | 15.4 | 22.4 | 0
1434 | 2022-10-08 23:55 | 15.4 | 22 | 0
1435 | 2022-10-08 23:56 | 15.2 | 22.1 | 0
1436 | 2022-10-08 23:57 | 15.2 | 22.1 | 0
1437 | 2022-10-08 23:58 | 15.3 | 22.1 | 0
1438 | 2022-10-08 23:59 | 15.4 | 21.6 | 0
1439 | 2022-10-09 | 15.5 | 22.3 | 0

## 09-10-2022_NO HEAT
| Date&time_x | OUTDOOR_TEMP | INDOOR_TEMP | PYRANOMETER
0 | 2022-10-09 00:01 | 15.5 | 21.8 | 0
1 | 2022-10-09 00:02 | 15.3 | 22.1 | 0
2 | 2022-10-09 00:03 | 15.2 | 21.8 | 0
3 | 2022-10-09 00:04 | 15 | 22.1 | 0
4 | 2022-10-09 00:05 | 14.9 | 21.9 | 0
5 | 2022-10-09 00:06 | 14.9 | 21.9 | 0
6 | 2022-10-09 00:07 | 14.8 | 22 | 0
7 | 2022-10-09 00:08 | 15 | 22.3 | 0
8 | 2022-10-09 00:09 | 14.9 | 22.1 | 0
9 | 2022-10-09 00:10 | 15.1 | 21.9 | 0
10 | 2022-10-09 00:11 | 15.4 | 21.9 | 0
11 | 2022-10-09 00:12 | 15.4 | 21.4 | 0
12 | 2022-10-09 00:13 | 15.2 | 22.6 | 0
13 | 2022-10-09 00:14 | 15.4 | 22.7 | 0
14 | 2022-10-09 00:15 | 15.3 | 22 | 0
15 | 2022-10-09 00:16 | 15.3 | 22.4 | 0
16 | 2022-10-09 00:17 | 15 | 22.6 | 0
17 | 2022-10-09 00:18 | 15.3 | 22.3 | 0
18 | 2022-10-09 00:19 | 15.2 | 21.9 | 0
19 | 2022-10-09 00:20 | 14.9 | 22.1 | 0
20 | 2022-10-09 00:21 | 14.8 | 23 | 0
21 | 2022-10-09 00:22 | 14.9 | 21.9 | 0
22 | 2022-10-09 00:23 | 14.9 | 22.1 | 0
23 | 2022-10-09 00:24 | 14.8 | 21.8 | 0
24 | 2022-10-09 00:25 | 14.7 | 21.8 | 0
25 | 2022-10-09 00:26 | 14.7 | 22.9 | 0
26 | 2022-10-09 00:27 | 14.7 | 22.8 | 0
27 | 2022-10-09 00:28 | 14.9 | 22.3 | 0
28 | 2022-10-09 00:29 | 14.7 | 21.9 | 0
29 | 2022-10-09 00:30 | 14.6 | 22.2 | 0
30 | 2022-10-09 00:31 | 14.5 | 22.3 | 0
31 | 2022-10-09 00:32 | 14.7 | 21.5 | 0
32 | 2022-10-09 00:33 | 14.5 | 22.1 | 0
33 | 2022-10-09 00:34 | 14.6 | 21.5 | 0
34 | 2022-10-09 00:35 | 14.5 | 22.7 | 0
35 | 2022-10-09 00:36 | 14.5 | 22.6 | 0
36 | 2022-10-09 00:37 | 14.7 | 22.2 | 0
37 | 2022-10-09 00:38 | 14.5 | 21.8 | 0
38 | 2022-10-09 00:39 | 14.4 | 22.4 | 0
39 | 2022-10-09 00:40 | 14.2 | 22.1 | 0
40 | 2022-10-09 00:41 | 14.2 | 22.1 | 0
41 | 2022-10-09 00:42 | 14.2 | 22 | 0
42 | 2022-10-09 00:43 | 14.1 | 22.2 | 0
43 | 2022-10-09 00:44 | 14.1 | 22.3 | 0
44 | 2022-10-09 00:45 | 14.1 | 22.1 | 0
45 | 2022-10-09 00:46 | 14 | 22.1 | 0
46 | 2022-10-09 00:47 | 14.1 | 22 | 0
47 | 2022-10-09 00:48 | 14 | 22.1 | 0
48 | 2022-10-09 00:49 | 14.1 | 22.1 | 0
49 | 2022-10-09 00:50 | 14.1 | 22 | 0
50 | 2022-10-09 00:51 | 14 | 22 | 0
51 | 2022-10-09 00:52 | 14.1 | 21.9 | 0
52 | 2022-10-09 00:53 | 14 | 21.9 | 0
53 | 2022-10-09 00:54 | 13.9 | 21.9 | 0
54 | 2022-10-09 00:55 | 14 | 22.1 | 0
55 | 2022-10-09 00:56 | 13.9 | 22.2 | 0
56 | 2022-10-09 00:57 | 13.9 | 22 | 0
57 | 2022-10-09 00:58 | 13.8 | 21.9 | 0
58 | 2022-10-09 00:59 | 13.7 | 22.1 | 0
59 | 2022-10-09 01:00 | 13.7 | 21.7 | 0
60 | 2022-10-09 01:01 | 13.7 | 22 | 0
61 | 2022-10-09 01:02 | 13.8 | 22.3 | 0
62 | 2022-10-09 01:03 | 13.6 | 21.5 | 0
63 | 2022-10-09 01:04 | 13.8 | 21.2 | 0
64 | 2022-10-09 01:05 | 13.7 | 22.1 | 0
65 | 2022-10-09 01:06 | 13.7 | 22 | 0
66 | 2022-10-09 01:07 | 13.5 | 22.5 | 0
67 | 2022-10-09 01:08 | 13.4 | 21.9 | 0
68 | 2022-10-09 01:09 | 13.6 | 21.5 | 0
69 | 2022-10-09 01:10 | 13.5 | 22.2 | 0
70 | 2022-10-09 01:11 | 13.3 | 21.8 | 0
71 | 2022-10-09 01:12 | 13.3 | 22 | 0
72 | 2022-10-09 01:13 | 13.2 | 21.9 | 0
73 | 2022-10-09 01:14 | 13.3 | 21.9 | 0
74 | 2022-10-09 01:15 | 13.2 | 23 | 0
75 | 2022-10-09 01:16 | 13.1 | 21.9 | 0
76 | 2022-10-09 01:17 | 12.9 | 21.6 | 0
77 | 2022-10-09 01:18 | 12.9 | 21.3 | 0
78 | 2022-10-09 01:19 | 13 | 21.9 | 0
79 | 2022-10-09 01:20 | 12.9 | 21.6 | 0
80 | 2022-10-09 01:21 | 12.9 | 21.5 | 0
81 | 2022-10-09 01:22 | 12.9 | 22.4 | 0
82 | 2022-10-09 01:23 | 12.9 | 22 | 0
83 | 2022-10-09 01:24 | 12.9 | 21.8 | 0
84 | 2022-10-09 01:25 | 12.8 | 22.6 | 0
85 | 2022-10-09 01:26 | 12.8 | 21.8 | 0
86 | 2022-10-09 01:27 | 12.8 | 21.4 | 0
87 | 2022-10-09 01:28 | 12.6 | 21.9 | 0
88 | 2022-10-09 01:29 | 12.6 | 21.9 | 0
89 | 2022-10-09 01:30 | 12.7 | 22.2 | 0
90 | 2022-10-09 01:31 | 12.6 | 22 | 0
91 | 2022-10-09 01:32 | 12.5 | 21.8 | 0
92 | 2022-10-09 01:33 | 12.7 | 22.4 | 0
93 | 2022-10-09 01:34 | 12.6 | 21.8 | 0
94 | 2022-10-09 01:35 | 12.8 | 21.8 | 0
95 | 2022-10-09 01:36 | 12.6 | 21.3 | 0
96 | 2022-10-09 01:37 | 12.6 | 22.6 | 0
97 | 2022-10-09 01:38 | 12.4 | 22 | 0
98 | 2022-10-09 01:39 | 12.5 | 22.1 | 0
99 | 2022-10-09 01:40 | 12.4 | 22.5 | 0
100 | 2022-10-09 01:41 | 12.4 | 21.5 | 0
101 | 2022-10-09 01:42 | 12.4 | 22.1 | 0
102 | 2022-10-09 01:43 | 12.3 | 21.7 | 0
103 | 2022-10-09 01:44 | 12.4 | 22.1 | 0
104 | 2022-10-09 01:45 | 12.3 | 22.1 | 0
105 | 2022-10-09 01:46 | 12.2 | 21.9 | 0
106 | 2022-10-09 01:47 | 12.1 | 22 | 0
107 | 2022-10-09 01:48 | 12.3 | 21.8 | 0
108 | 2022-10-09 01:49 | 12.1 | 22.2 | 0
109 | 2022-10-09 01:50 | 12.1 | 21.7 | 0
110 | 2022-10-09 01:51 | 12 | 21.9 | 0
111 | 2022-10-09 01:52 | 12 | 21.9 | 0
112 | 2022-10-09 01:53 | 12 | 21.9 | 0
113 | 2022-10-09 01:54 | 12 | 21.8 | 0
114 | 2022-10-09 01:55 | 12.1 | 22 | 0
115 | 2022-10-09 01:56 | 12.2 | 21.9 | 0
116 | 2022-10-09 01:57 | 12.2 | 22 | 0
117 | 2022-10-09 01:58 | 12.1 | 22 | 0
118 | 2022-10-09 01:59 | 12 | 22.1 | 0
119 | 2022-10-09 02:00 | 12 | 22.1 | 0
120 | 2022-10-09 02:01 | 12.1 | 22.2 | 0
121 | 2022-10-09 02:02 | 12 | 21.9 | 0
122 | 2022-10-09 02:03 | 12.1 | 22.1 | 0
123 | 2022-10-09 02:04 | 12.1 | 21.8 | 0
124 | 2022-10-09 02:05 | 11.9 | 21.6 | 0
125 | 2022-10-09 02:06 | 12.1 | 22 | 0
126 | 2022-10-09 02:07 | 12.1 | 21.4 | 0
127 | 2022-10-09 02:08 | 12 | 21.9 | 0
128 | 2022-10-09 02:09 | 12.1 | 21.8 | 0
129 | 2022-10-09 02:10 | 11.9 | 21.9 | 0
130 | 2022-10-09 02:11 | 11.9 | 21.4 | 0
131 | 2022-10-09 02:12 | 11.8 | 21.9 | 0
132 | 2022-10-09 02:13 | 12 | 21.9 | 0
133 | 2022-10-09 02:14 | 12 | 21.1 | 0
134 | 2022-10-09 02:15 | 11.8 | 22.1 | 0
135 | 2022-10-09 02:16 | 11.7 | 22.8 | 0
136 | 2022-10-09 02:17 | 11.7 | 22.8 | 0
137 | 2022-10-09 02:18 | 11.7 | 22.8 | 0
138 | 2022-10-09 02:19 | 11.6 | 21.8 | 0
139 | 2022-10-09 02:20 | 11.7 | 22.2 | 0
140 | 2022-10-09 02:21 | 11.7 | 21.8 | 0
141 | 2022-10-09 02:22 | 11.7 | 21.8 | 0
142 | 2022-10-09 02:23 | 11.6 | 21.9 | 0
143 | 2022-10-09 02:24 | 11.6 | 21.8 | 0
144 | 2022-10-09 02:25 | 11.5 | 21.9 | 0
145 | 2022-10-09 02:26 | 11.5 | 22.2 | 0
146 | 2022-10-09 02:27 | 11.5 | 21.7 | 0
147 | 2022-10-09 02:28 | 11.4 | 22.6 | 0
148 | 2022-10-09 02:29 | 11.6 | 22.1 | 0
149 | 2022-10-09 02:30 | 11.5 | 22.5 | 0
150 | 2022-10-09 02:31 | 11.5 | 22 | 0
151 | 2022-10-09 02:32 | 11.6 | 21.4 | 0
152 | 2022-10-09 02:33 | 11.5 | 22.1 | 0
153 | 2022-10-09 02:34 | 11.4 | 22 | 0
154 | 2022-10-09 02:35 | 11.6 | 21.8 | 0
155 | 2022-10-09 02:36 | 11.4 | 21.6 | 0
156 | 2022-10-09 02:37 | 11.6 | 21.8 | 0
157 | 2022-10-09 02:38 | 11.5 | 21.8 | 0
158 | 2022-10-09 02:39 | 11.3 | 22.1 | 0
159 | 2022-10-09 02:40 | 11.5 | 21.7 | 0
160 | 2022-10-09 02:41 | 11.3 | 22 | 0
161 | 2022-10-09 02:42 | 11.3 | 22.3 | 0
162 | 2022-10-09 02:43 | 11.3 | 22 | 0
163 | 2022-10-09 02:44 | 11.3 | 21.9 | 0
164 | 2022-10-09 02:45 | 11.3 | 21.8 | 0
165 | 2022-10-09 02:46 | 11.2 | 22.6 | 0
166 | 2022-10-09 02:47 | 11.3 | 22.6 | 0
167 | 2022-10-09 02:48 | 11.4 | 21.8 | 0
168 | 2022-10-09 02:49 | 11.3 | 21.3 | 0
169 | 2022-10-09 02:50 | 11.3 | 21.8 | 0
170 | 2022-10-09 02:51 | 11.6 | 22.3 | 0
171 | 2022-10-09 02:52 | 11.2 | 21.6 | 0
172 | 2022-10-09 02:53 | 11.3 | 21.8 | 0
173 | 2022-10-09 02:54 | 11.1 | 21.7 | 0
174 | 2022-10-09 02:55 | 11.1 | 21.9 | 0
175 | 2022-10-09 02:56 | 11.2 | 21.8 | 0
176 | 2022-10-09 02:57 | 11.4 | 21.4 | 0
177 | 2022-10-09 02:58 | 11.4 | 22.1 | 0
178 | 2022-10-09 02:59 | 11.2 | 21.5 | 0
179 | 2022-10-09 03:00 | 11.3 | 21.4 | 0
180 | 2022-10-09 03:01 | 11.3 | 21.7 | 0
181 | 2022-10-09 03:02 | 11.4 | 21.8 | 0
182 | 2022-10-09 03:03 | 11.3 | 22 | 0
183 | 2022-10-09 03:04 | 11.3 | 21.9 | 0
184 | 2022-10-09 03:05 | 11.3 | 21.7 | 0
185 | 2022-10-09 03:06 | 11.4 | 21.6 | 0
186 | 2022-10-09 03:07 | 11.4 | 21.8 | 0
187 | 2022-10-09 03:08 | 11.3 | 21.9 | 0
188 | 2022-10-09 03:09 | 11.4 | 21.9 | 0
189 | 2022-10-09 03:10 | 11.4 | 21.8 | 0
190 | 2022-10-09 03:11 | 11.3 | 21.7 | 0
191 | 2022-10-09 03:12 | 11.6 | 21.6 | 0
192 | 2022-10-09 03:13 | 11.4 | 21.9 | 0
193 | 2022-10-09 03:14 | 11.4 | 22 | 0
194 | 2022-10-09 03:15 | 11.4 | 21.7 | 0
195 | 2022-10-09 03:16 | 11.3 | 21.9 | 0
196 | 2022-10-09 03:17 | 11.4 | 21.9 | 0
197 | 2022-10-09 03:18 | 11.6 | 21.6 | 0
198 | 2022-10-09 03:19 | 11.3 | 22.4 | 0
199 | 2022-10-09 03:20 | 11.3 | 21.6 | 0
200 | 2022-10-09 03:21 | 11.3 | 21.8 | 0
201 | 2022-10-09 03:22 | 11.3 | 21.6 | 0
202 | 2022-10-09 03:23 | 11.3 | 21.1 | 0
203 | 2022-10-09 03:24 | 11.3 | 21.9 | 0
204 | 2022-10-09 03:25 | 11.3 | 22 | 0
205 | 2022-10-09 03:26 | 11.3 | 21.8 | 0
206 | 2022-10-09 03:27 | 11.3 | 21.8 | 0
207 | 2022-10-09 03:28 | 11.3 | 20.9 | 0
208 | 2022-10-09 03:29 | 11.4 | 21.1 | 0
209 | 2022-10-09 03:30 | 11.5 | 22 | 0
210 | 2022-10-09 03:31 | 11.4 | 22.8 | 0
211 | 2022-10-09 03:32 | 11.5 | 22.6 | 0
212 | 2022-10-09 03:33 | 11.3 | 22.6 | 0
213 | 2022-10-09 03:34 | 11.5 | 21.1 | 0
214 | 2022-10-09 03:35 | 11.6 | 21.8 | 0
215 | 2022-10-09 03:36 | 11.5 | 21.9 | 0
216 | 2022-10-09 03:37 | 11.4 | 22.2 | 0
217 | 2022-10-09 03:38 | 11.5 | 21.7 | 0
218 | 2022-10-09 03:39 | 11.4 | 21.8 | 0
219 | 2022-10-09 03:40 | 11.5 | 21.6 | 0
220 | 2022-10-09 03:41 | 11.4 | 22 | 0
221 | 2022-10-09 03:42 | 11.3 | 22.1 | 0
222 | 2022-10-09 03:43 | 11.4 | 21.6 | 0
223 | 2022-10-09 03:44 | 11.6 | 21 | 0
224 | 2022-10-09 03:45 | 11.6 | 21.1 | 0
225 | 2022-10-09 03:46 | 11.4 | 21.2 | 0
226 | 2022-10-09 03:47 | 11.6 | 22.2 | 0
227 | 2022-10-09 03:48 | 11.4 | 21.1 | 0
228 | 2022-10-09 03:49 | 11.5 | 21.9 | 0
229 | 2022-10-09 03:50 | 11.6 | 21.6 | 0
230 | 2022-10-09 03:51 | 11.4 | 22.2 | 0
231 | 2022-10-09 03:52 | 11.6 | 21.4 | 0
232 | 2022-10-09 03:53 | 11.7 | 21.2 | 0
233 | 2022-10-09 03:54 | 11.5 | 22.2 | 0
234 | 2022-10-09 03:55 | 11.5 | 21.2 | 0
235 | 2022-10-09 03:56 | 11.7 | 21.6 | 0
236 | 2022-10-09 03:57 | 11.7 | 21.1 | 0
237 | 2022-10-09 03:58 | 11.6 | 20.9 | 0
238 | 2022-10-09 03:59 | 11.7 | 21.6 | 0
239 | 2022-10-09 04:00 | 11.7 | 22.3 | 0
240 | 2022-10-09 04:01 | 11.7 | 21.6 | 0
241 | 2022-10-09 04:02 | 11.7 | 21.7 | 0
242 | 2022-10-09 04:03 | 12 | 21.9 | 0
243 | 2022-10-09 04:04 | 11.9 | 21.5 | 0
244 | 2022-10-09 04:05 | 11.8 | 22 | 0
245 | 2022-10-09 04:06 | 11.7 | 22.4 | 0
246 | 2022-10-09 04:07 | 11.7 | 21.5 | 0
247 | 2022-10-09 04:08 | 11.7 | 22 | 0
248 | 2022-10-09 04:09 | 11.7 | 21.7 | 0
249 | 2022-10-09 04:10 | 11.7 | 21.9 | 0
250 | 2022-10-09 04:11 | 11.6 | 22 | 0
251 | 2022-10-09 04:12 | 11.9 | 21.6 | 0
252 | 2022-10-09 04:13 | 11.8 | 21.8 | 0
253 | 2022-10-09 04:14 | 12 | 21.8 | 0
254 | 2022-10-09 04:15 | 11.7 | 21.6 | 0
255 | 2022-10-09 04:16 | 11.7 | 21.8 | 0
256 | 2022-10-09 04:17 | 11.9 | 21.8 | 0
257 | 2022-10-09 04:18 | 11.8 | 21.8 | 0
258 | 2022-10-09 04:19 | 12 | 21.8 | 0
259 | 2022-10-09 04:20 | 11.7 | 21.6 | 0
260 | 2022-10-09 04:21 | 11.8 | 22 | 0
261 | 2022-10-09 04:22 | 12 | 22.1 | 0
262 | 2022-10-09 04:23 | 11.9 | 21.3 | 0
263 | 2022-10-09 04:24 | 11.9 | 22 | 0
264 | 2022-10-09 04:25 | 11.9 | 21.4 | 0
265 | 2022-10-09 04:26 | 11.9 | 21.6 | 0
266 | 2022-10-09 04:27 | 11.9 | 21.5 | 0
267 | 2022-10-09 04:28 | 12 | 21.7 | 0
268 | 2022-10-09 04:29 | 12 | 21.9 | 0
269 | 2022-10-09 04:30 | 11.9 | 21.8 | 0
270 | 2022-10-09 04:31 | 12 | 21.7 | 0
271 | 2022-10-09 04:32 | 12 | 22 | 0
272 | 2022-10-09 04:33 | 12 | 22 | 0
273 | 2022-10-09 04:34 | 11.9 | 21.5 | 0
274 | 2022-10-09 04:35 | 12.2 | 22 | 0
275 | 2022-10-09 04:36 | 12.1 | 21.6 | 0
276 | 2022-10-09 04:37 | 12.2 | 21.7 | 0
277 | 2022-10-09 04:38 | 12.1 | 21.9 | 0
278 | 2022-10-09 04:39 | 12 | 21.2 | 0
279 | 2022-10-09 04:40 | 12 | 21.9 | 0
280 | 2022-10-09 04:41 | 12.2 | 21.1 | 0
281 | 2022-10-09 04:42 | 12 | 21 | 0
282 | 2022-10-09 04:43 | 12.1 | 21.8 | 0
283 | 2022-10-09 04:44 | 11.8 | 21.3 | 0
284 | 2022-10-09 04:45 | 11.9 | 21.9 | 0
285 | 2022-10-09 04:46 | 11.9 | 21.5 | 0
286 | 2022-10-09 04:47 | 12 | 21.8 | 0
287 | 2022-10-09 04:48 | 11.8 | 21.5 | 0
288 | 2022-10-09 04:49 | 11.9 | 21.8 | 0
289 | 2022-10-09 04:50 | 11.8 | 21.7 | 0
290 | 2022-10-09 04:51 | 11.9 | 21.7 | 0
291 | 2022-10-09 04:52 | 11.8 | 21.6 | 0
292 | 2022-10-09 04:53 | 11.8 | 22.4 | 0
293 | 2022-10-09 04:54 | 11.9 | 21.5 | 0
294 | 2022-10-09 04:55 | 11.6 | 21.9 | 0
295 | 2022-10-09 04:56 | 11.9 | 21.7 | 0
296 | 2022-10-09 04:57 | 11.7 | 21.8 | 0
297 | 2022-10-09 04:58 | 11.8 | 21.6 | 0
298 | 2022-10-09 04:59 | 11.7 | 21.9 | 0
299 | 2022-10-09 05:00 | 11.7 | 21.8 | 0
300 | 2022-10-09 05:01 | 11.8 | 21.9 | 0
301 | 2022-10-09 05:02 | 11.8 | 22.6 | 0
302 | 2022-10-09 05:03 | 11.7 | 22.3 | 0
303 | 2022-10-09 05:04 | 11.7 | 21.5 | 0
304 | 2022-10-09 05:05 | 11.8 | 22.4 | 0
305 | 2022-10-09 05:06 | 11.7 | 21.4 | 0
306 | 2022-10-09 05:07 | 11.7 | 22.2 | 0
307 | 2022-10-09 05:08 | 11.7 | 21.6 | 0
308 | 2022-10-09 05:09 | 11.8 | 21.6 | 0
309 | 2022-10-09 05:10 | 11.6 | 22 | 0
310 | 2022-10-09 05:11 | 11.6 | 21.9 | 0
311 | 2022-10-09 05:12 | 11.7 | 21.3 | 0
312 | 2022-10-09 05:13 | 11.7 | 21.7 | 0
313 | 2022-10-09 05:14 | 11.6 | 21.4 | 0
314 | 2022-10-09 05:15 | 11.8 | 21.8 | 0
315 | 2022-10-09 05:16 | 11.6 | 21.2 | 0
316 | 2022-10-09 05:17 | 11.6 | 21.9 | 0
317 | 2022-10-09 05:18 | 11.8 | 21.9 | 0
318 | 2022-10-09 05:19 | 11.7 | 22.1 | 0
319 | 2022-10-09 05:20 | 11.6 | 22 | 0
320 | 2022-10-09 05:21 | 11.6 | 21.5 | 0
321 | 2022-10-09 05:22 | 11.7 | 20.9 | 0
322 | 2022-10-09 05:23 | 11.6 | 21.7 | 0
323 | 2022-10-09 05:24 | 11.7 | 21.3 | 0
324 | 2022-10-09 05:25 | 11.6 | 21.9 | 0
325 | 2022-10-09 05:26 | 11.6 | 21.5 | 0
326 | 2022-10-09 05:27 | 11.5 | 21.8 | 0
327 | 2022-10-09 05:28 | 11.6 | 21.5 | 0
328 | 2022-10-09 05:29 | 11.7 | 21.5 | 0
329 | 2022-10-09 05:30 | 11.5 | 21.8 | 0
330 | 2022-10-09 05:31 | 11.7 | 21.5 | 0
331 | 2022-10-09 05:32 | 11.7 | 21.7 | 0
332 | 2022-10-09 05:33 | 11.5 | 21.8 | 0
333 | 2022-10-09 05:34 | 11.5 | 21.1 | 0
334 | 2022-10-09 05:35 | 11.7 | 20.9 | 0
335 | 2022-10-09 05:36 | 11.5 | 21.9 | 0
336 | 2022-10-09 05:37 | 11.7 | 21.1 | 0
337 | 2022-10-09 05:38 | 11.6 | 22.4 | 0
338 | 2022-10-09 05:39 | 11.6 | 21.5 | 0
339 | 2022-10-09 05:40 | 11.8 | 20.9 | 0
340 | 2022-10-09 05:41 | 11.6 | 21.1 | 0
341 | 2022-10-09 05:42 | 11.7 | 21.9 | 0
342 | 2022-10-09 05:43 | 11.5 | 22 | 0
343 | 2022-10-09 05:44 | 11.7 | 21.6 | 0
344 | 2022-10-09 05:45 | 11.7 | 21.4 | 0
345 | 2022-10-09 05:46 | 11.8 | 21.5 | 0
346 | 2022-10-09 05:47 | 11.6 | 21.7 | 0
347 | 2022-10-09 05:48 | 11.7 | 21.9 | 0
348 | 2022-10-09 05:49 | 11.8 | 21.3 | 0
349 | 2022-10-09 05:50 | 11.6 | 21.9 | 0
350 | 2022-10-09 05:51 | 11.7 | 21.5 | 0
351 | 2022-10-09 05:52 | 11.5 | 21.6 | 0
352 | 2022-10-09 05:53 | 11.6 | 21.7 | 0
353 | 2022-10-09 05:54 | 11.6 | 21.4 | 0
354 | 2022-10-09 05:55 | 11.5 | 22.2 | 0
355 | 2022-10-09 05:56 | 11.5 | 21.7 | 0
356 | 2022-10-09 05:57 | 11.6 | 21.4 | 0
357 | 2022-10-09 05:58 | 11.5 | 21.8 | 0
358 | 2022-10-09 05:59 | 11.4 | 21.6 | 0
359 | 2022-10-09 06:00 | 11.4 | 21.2 | 0
360 | 2022-10-09 06:01 | 11.6 | 22.2 | 0
361 | 2022-10-09 06:02 | 11.5 | 20.9 | 0
362 | 2022-10-09 06:03 | 11.5 | 21.1 | 0
363 | 2022-10-09 06:04 | 11.4 | 21.9 | 0
364 | 2022-10-09 06:05 | 11.5 | 21.2 | 0
365 | 2022-10-09 06:06 | 11.6 | 20.9 | 0
366 | 2022-10-09 06:07 | 11.4 | 21.3 | 0
367 | 2022-10-09 06:08 | 11.4 | 21.7 | 0
368 | 2022-10-09 06:09 | 11.4 | 21.6 | 0
369 | 2022-10-09 06:10 | 11.7 | 22.4 | 0
370 | 2022-10-09 06:11 | 11.5 | 21.9 | 0
371 | 2022-10-09 06:12 | 11.5 | 22.4 | 0
372 | 2022-10-09 06:13 | 11.5 | 21.5 | 0
373 | 2022-10-09 06:14 | 11.5 | 22 | 0
374 | 2022-10-09 06:15 | 11.6 | 21.8 | 0
375 | 2022-10-09 06:16 | 11.6 | 21.5 | 0
376 | 2022-10-09 06:17 | 11.7 | 21.5 | 0
377 | 2022-10-09 06:18 | 11.6 | 21.6 | 0
378 | 2022-10-09 06:19 | 11.6 | 21.4 | 0
379 | 2022-10-09 06:20 | 11.7 | 21.6 | 0
380 | 2022-10-09 06:21 | 11.7 | 21.6 | 0
381 | 2022-10-09 06:22 | 11.6 | 21.7 | 0
382 | 2022-10-09 06:23 | 11.8 | 21.9 | 0
383 | 2022-10-09 06:24 | 11.8 | 21.7 | 0
384 | 2022-10-09 06:25 | 11.8 | 20.8 | 0
385 | 2022-10-09 06:26 | 11.7 | 20.8 | 0
386 | 2022-10-09 06:27 | 11.6 | 21.4 | 0
387 | 2022-10-09 06:28 | 11.6 | 21.6 | 0
388 | 2022-10-09 06:29 | 11.6 | 21.4 | 0
389 | 2022-10-09 06:30 | 11.7 | 21.6 | 0
390 | 2022-10-09 06:31 | 11.5 | 21 | 0
391 | 2022-10-09 06:32 | 11.5 | 21.7 | 0
392 | 2022-10-09 06:33 | 11.5 | 21.4 | 0
393 | 2022-10-09 06:34 | 11.7 | 21.9 | 0
394 | 2022-10-09 06:35 | 11.7 | 21.4 | 0
395 | 2022-10-09 06:36 | 11.7 | 20.9 | 0
396 | 2022-10-09 06:37 | 11.7 | 21.6 | 0
397 | 2022-10-09 06:38 | 11.5 | 21.5 | 0
398 | 2022-10-09 06:39 | 11.6 | 21.2 | 0
399 | 2022-10-09 06:40 | 11.4 | 22 | 0
400 | 2022-10-09 06:41 | 11.5 | 21.1 | 0
401 | 2022-10-09 06:42 | 11.6 | 20.9 | 0
402 | 2022-10-09 06:43 | 11.5 | 21.6 | 0
403 | 2022-10-09 06:44 | 11.4 | 22.1 | 0
404 | 2022-10-09 06:45 | 11.6 | 21.4 | 0
405 | 2022-10-09 06:46 | 11.4 | 22.1 | 0
406 | 2022-10-09 06:47 | 11.6 | 21.9 | 0
407 | 2022-10-09 06:48 | 11.4 | 22.2 | 0
408 | 2022-10-09 06:49 | 11.6 | 21.3 | 0
409 | 2022-10-09 06:50 | 11.4 | 22 | 0
410 | 2022-10-09 06:51 | 11.5 | 22.2 | 0
411 | 2022-10-09 06:52 | 11.4 | 21.6 | 0
412 | 2022-10-09 06:53 | 11.3 | 22.1 | 0
413 | 2022-10-09 06:54 | 11.5 | 21.2 | 0
414 | 2022-10-09 06:55 | 11.4 | 21.6 | 0
415 | 2022-10-09 06:56 | 11.5 | 21.9 | 0
416 | 2022-10-09 06:57 | 11.6 | 21.8 | 0
417 | 2022-10-09 06:58 | 11.5 | 21.4 | 0
418 | 2022-10-09 06:59 | 11.4 | 21.5 | 0
419 | 2022-10-09 07:00 | 11.6 | 21.6 | 0
420 | 2022-10-09 07:01 | 11.4 | 21.5 | 0
421 | 2022-10-09 07:02 | 11.6 | 21.6 | 0
422 | 2022-10-09 07:03 | 11.5 | 21.3 | 0
423 | 2022-10-09 07:04 | 11.4 | 21.3 | 0
424 | 2022-10-09 07:05 | 11.6 | 21.5 | 0
425 | 2022-10-09 07:06 | 11.5 | 21.7 | 0
426 | 2022-10-09 07:07 | 11.4 | 21.1 | 0
427 | 2022-10-09 07:08 | 11.4 | 21.5 | 0
428 | 2022-10-09 07:09 | 11.6 | 21.2 | 0
429 | 2022-10-09 07:10 | 11.5 | 22 | 0
430 | 2022-10-09 07:11 | 11.5 | 21.5 | 0
431 | 2022-10-09 07:12 | 11.7 | 21.4 | 0
432 | 2022-10-09 07:13 | 11.7 | 22 | 0
433 | 2022-10-09 07:14 | 11.6 | 21.9 | 0
434 | 2022-10-09 07:15 | 11.4 | 21.9 | 0
435 | 2022-10-09 07:16 | 11.4 | 21.4 | 0
436 | 2022-10-09 07:17 | 11.6 | 21.1 | 0
437 | 2022-10-09 07:18 | 11.4 | 22 | 0
438 | 2022-10-09 07:19 | 11.4 | 21.3 | 0
439 | 2022-10-09 07:20 | 11.4 | 21.8 | 0
440 | 2022-10-09 07:21 | 11.5 | 21.4 | 0
441 | 2022-10-09 07:22 | 11.3 | 21.1 | 0
442 | 2022-10-09 07:23 | 11.5 | 20.9 | 0
443 | 2022-10-09 07:24 | 11.4 | 22.1 | 1
444 | 2022-10-09 07:25 | 11.6 | 22.2 | 1
445 | 2022-10-09 07:26 | 11.4 | 21.9 | 1
446 | 2022-10-09 07:27 | 11.5 | 21.3 | 2
447 | 2022-10-09 07:28 | 11.6 | 21.1 | 2
448 | 2022-10-09 07:29 | 11.6 | 21.1 | 3
449 | 2022-10-09 07:30 | 11.4 | 20.9 | 3
450 | 2022-10-09 07:31 | 11.5 | 22.2 | 4
451 | 2022-10-09 07:32 | 11.4 | 21.6 | 4
452 | 2022-10-09 07:33 | 11.6 | 21.6 | 5
453 | 2022-10-09 07:34 | 11.5 | 22.1 | 5
454 | 2022-10-09 07:35 | 11.7 | 20.9 | 6
455 | 2022-10-09 07:36 | 11.6 | 20.9 | 7
456 | 2022-10-09 07:37 | 11.7 | 21.4 | 7
457 | 2022-10-09 07:38 | 11.9 | 22.1 | 8
458 | 2022-10-09 07:39 | 11.9 | 21.2 | 9
459 | 2022-10-09 07:40 | 11.8 | 21.3 | 9
460 | 2022-10-09 07:41 | 11.9 | 22.2 | 10
461 | 2022-10-09 07:42 | 11.9 | 22.3 | 10
462 | 2022-10-09 07:43 | 11.9 | 21.5 | 11
463 | 2022-10-09 07:44 | 12.2 | 21.9 | 11
464 | 2022-10-09 07:45 | 12.2 | 20.8 | 12
465 | 2022-10-09 07:46 | 12.2 | 20.6 | 13
466 | 2022-10-09 07:47 | 12 | 21.1 | 13
467 | 2022-10-09 07:48 | 12.1 | 21.7 | 14
468 | 2022-10-09 07:49 | 12.2 | 20.9 | 14
469 | 2022-10-09 07:50 | 12.2 | 20.7 | 15
470 | 2022-10-09 07:51 | 12 | 21.4 | 15
471 | 2022-10-09 07:52 | 12.1 | 21.7 | 16
472 | 2022-10-09 07:53 | 12.2 | 21.4 | 16
473 | 2022-10-09 07:54 | 12.4 | 21.8 | 17
474 | 2022-10-09 07:55 | 12.5 | 21.7 | 17
475 | 2022-10-09 07:56 | 12.4 | 21 | 18
476 | 2022-10-09 07:57 | 12.3 | 22.2 | 19
477 | 2022-10-09 07:58 | 12.6 | 21 | 19
478 | 2022-10-09 07:59 | 12.4 | 21.7 | 20
479 | 2022-10-09 08:00 | 12.4 | 22 | 20
480 | 2022-10-09 08:01 | 12.6 | 21.5 | 21
481 | 2022-10-09 08:02 | 12.6 | 21.6 | 22
482 | 2022-10-09 08:03 | 12.5 | 21.5 | 22
483 | 2022-10-09 08:04 | 12.7 | 21.4 | 22
484 | 2022-10-09 08:05 | 12.6 | 21.3 | 23
485 | 2022-10-09 08:06 | 12.6 | 21.4 | 23
486 | 2022-10-09 08:07 | 12.7 | 21.6 | 23
487 | 2022-10-09 08:08 | 12.8 | 21.5 | 24
488 | 2022-10-09 08:09 | 12.7 | 21.3 | 24
489 | 2022-10-09 08:10 | 12.8 | 21.4 | 24
490 | 2022-10-09 08:11 | 12.7 | 21.4 | 25
491 | 2022-10-09 08:12 | 12.9 | 21.6 | 25
492 | 2022-10-09 08:13 | 12.8 | 21.6 | 26
493 | 2022-10-09 08:14 | 12.9 | 21.2 | 27
494 | 2022-10-09 08:15 | 12.8 | 20.6 | 28
495 | 2022-10-09 08:16 | 12.8 | 22.2 | 28
496 | 2022-10-09 08:17 | 12.9 | 22.4 | 29
497 | 2022-10-09 08:18 | 13.1 | 22.2 | 29
498 | 2022-10-09 08:19 | 13 | 21.1 | 30
499 | 2022-10-09 08:20 | 13.2 | 20.8 | 30
500 | 2022-10-09 08:21 | 13.2 | 21.3 | 31
501 | 2022-10-09 08:22 | 13 | 22.2 | 32
502 | 2022-10-09 08:23 | 13.1 | 22.4 | 32
503 | 2022-10-09 08:24 | 13.2 | 22.3 | 33
504 | 2022-10-09 08:25 | 13.2 | 21.7 | 34
505 | 2022-10-09 08:26 | 13.3 | 20.7 | 34
506 | 2022-10-09 08:27 | 13.2 | 21.5 | 35
507 | 2022-10-09 08:28 | 13.1 | 22.2 | 35
508 | 2022-10-09 08:29 | 13.4 | 21.4 | 35
509 | 2022-10-09 08:30 | 13.2 | 21.4 | 36
510 | 2022-10-09 08:31 | 13.2 | 21.5 | 36
511 | 2022-10-09 08:32 | 13.4 | 21.5 | 37
512 | 2022-10-09 08:33 | 13.4 | 21.5 | 38
513 | 2022-10-09 08:34 | 13.4 | 21.7 | 38
514 | 2022-10-09 08:35 | 13.3 | 21.8 | 39
515 | 2022-10-09 08:36 | 13.3 | 21.1 | 39
516 | 2022-10-09 08:37 | 13.5 | 21.2 | 40
517 | 2022-10-09 08:38 | 13.6 | 21.5 | 41
518 | 2022-10-09 08:39 | 13.6 | 21.2 | 42
519 | 2022-10-09 08:40 | 13.6 | 21.6 | 44
520 | 2022-10-09 08:41 | 13.6 | 21.3 | 48
521 | 2022-10-09 08:42 | 13.4 | 21.7 | 75
522 | 2022-10-09 08:43 | 13.5 | 21.5 | 132
523 | 2022-10-09 08:44 | 13.5 | 21.4 | 198
524 | 2022-10-09 08:45 | 13.6 | 21.5 | 246
525 | 2022-10-09 08:46 | 13.8 | 21.2 | 232
526 | 2022-10-09 08:47 | 13.6 | 21.1 | 204
527 | 2022-10-09 08:48 | 13.7 | 21.5 | 167
528 | 2022-10-09 08:49 | 13.8 | 21.8 | 164
529 | 2022-10-09 08:50 | 13.8 | 20.9 | 232
530 | 2022-10-09 08:51 | 13.7 | 21.6 | 257
531 | 2022-10-09 08:52 | 13.7 | 21.6 | 239
532 | 2022-10-09 08:53 | 13.9 | 21.4 | 259
533 | 2022-10-09 08:54 | 13.9 | 21.3 | 309
534 | 2022-10-09 08:55 | 14.1 | 21.5 | 320
535 | 2022-10-09 08:56 | 14.3 | 21.5 | 322
536 | 2022-10-09 08:57 | 14.4 | 22.4 | 317
537 | 2022-10-09 08:58 | 14.3 | 22.1 | 317
538 | 2022-10-09 08:59 | 14.4 | 20.7 | 324
539 | 2022-10-09 09:00 | 14.5 | 21.8 | 332
540 | 2022-10-09 09:01 | 14.3 | 21.8 | 346
541 | 2022-10-09 09:02 | 14.3 | 21.6 | 351
542 | 2022-10-09 09:03 | 14.8 | 21.2 | 355
543 | 2022-10-09 09:04 | 14.7 | 21.2 | 358
544 | 2022-10-09 09:05 | 14.6 | 21.9 | 363
545 | 2022-10-09 09:06 | 14.7 | 21.7 | 368
546 | 2022-10-09 09:07 | 14.8 | 22.1 | 372
547 | 2022-10-09 09:08 | 14.6 | 21.4 | 376
548 | 2022-10-09 09:09 | 14.8 | 20.6 | 381
549 | 2022-10-09 09:10 | 15.1 | 21.6 | 385
550 | 2022-10-09 09:11 | 15.2 | 22.4 | 389
551 | 2022-10-09 09:12 | 15 | 21.2 | 393
552 | 2022-10-09 09:13 | 15.4 | 21.4 | 398
553 | 2022-10-09 09:14 | 15.2 | 21.6 | 403
554 | 2022-10-09 09:15 | 15.4 | 21.9 | 406
555 | 2022-10-09 09:16 | 15.4 | 21.6 | 410
556 | 2022-10-09 09:17 | 15.5 | 21.1 | 411
557 | 2022-10-09 09:18 | 16 | 21.2 | 413
558 | 2022-10-09 09:19 | 16.2 | 21.4 | 409
559 | 2022-10-09 09:20 | 16.5 | 21 | 377
560 | 2022-10-09 09:21 | 16.7 | 20.6 | 401
561 | 2022-10-09 09:22 | 16.7 | 21.6 | 420
562 | 2022-10-09 09:23 | 17.2 | 21.2 | 431
563 | 2022-10-09 09:24 | 17.7 | 21.3 | 417
564 | 2022-10-09 09:25 | 17.9 | 22.2 | 432
565 | 2022-10-09 09:26 | 18.4 | 21.1 | 444
566 | 2022-10-09 09:27 | 18.6 | 21.9 | 454
567 | 2022-10-09 09:28 | 18.8 | 21.1 | 464
568 | 2022-10-09 09:29 | 19.2 | 21.6 | 468
569 | 2022-10-09 09:30 | 19.5 | 21.9 | 470
570 | 2022-10-09 09:31 | 19.5 | 21.4 | 474
571 | 2022-10-09 09:32 | 20 | 21.9 | 479
572 | 2022-10-09 09:33 | 20.3 | 21.5 | 484
573 | 2022-10-09 09:34 | 20.2 | 21 | 487
574 | 2022-10-09 09:35 | 20.5 | 22.2 | 494
575 | 2022-10-09 09:36 | 20.3 | 21.6 | 501
576 | 2022-10-09 09:37 | 20.6 | 21.9 | 495
577 | 2022-10-09 09:38 | 21 | 21.3 | 498
578 | 2022-10-09 09:39 | 21.2 | 21.7 | 509
579 | 2022-10-09 09:40 | 21.4 | 21.3 | 519
580 | 2022-10-09 09:41 | 21.3 | 21 | 523
581 | 2022-10-09 09:42 | 21.4 | 21.9 | 528
582 | 2022-10-09 09:43 | 22.1 | 21.1 | 533
583 | 2022-10-09 09:44 | 22 | 21.8 | 538
584 | 2022-10-09 09:45 | 22.5 | 21 | 544
585 | 2022-10-09 09:46 | 22.3 | 21.2 | 550
586 | 2022-10-09 09:47 | 22.4 | 21.4 | 555
587 | 2022-10-09 09:48 | 22.7 | 21.9 | 560
588 | 2022-10-09 09:49 | 22.5 | 21.7 | 564
589 | 2022-10-09 09:50 | 22.8 | 22.3 | 567
590 | 2022-10-09 09:51 | 23.1 | 22.4 | 571
591 | 2022-10-09 09:52 | 22.6 | 22.3 | 538
592 | 2022-10-09 09:53 | 22.5 | 20.9 | 579
593 | 2022-10-09 09:54 | 22.5 | 21.2 | 583
594 | 2022-10-09 09:55 | 22.7 | 22.4 | 590
595 | 2022-10-09 09:56 | 22.7 | 21.7 | 595
596 | 2022-10-09 09:57 | 22.7 | 21.8 | 600
597 | 2022-10-09 09:58 | 22.9 | 21.5 | 604
598 | 2022-10-09 09:59 | 23.3 | 21.7 | 609
599 | 2022-10-09 10:00 | 23.9 | 21.7 | 614
600 | 2022-10-09 10:01 | 23.9 | 21.5 | 620
601 | 2022-10-09 10:02 | 23.4 | 21.5 | 628
602 | 2022-10-09 10:03 | 23.4 | 21.5 | 608
603 | 2022-10-09 10:04 | 23.4 | 21.8 | 615
604 | 2022-10-09 10:05 | 23.2 | 21.3 | 624
605 | 2022-10-09 10:06 | 23.2 | 21.6 | 636
606 | 2022-10-09 10:07 | 23.1 | 21.2 | 595
607 | 2022-10-09 10:08 | 23.1 | 21.6 | 559
608 | 2022-10-09 10:09 | 23.5 | 20.9 | 563
609 | 2022-10-09 10:10 | 23.1 | 20.8 | 527
610 | 2022-10-09 10:11 | 23.2 | 21.6 | 574
611 | 2022-10-09 10:12 | 22.9 | 21.5 | 539
612 | 2022-10-09 10:13 | 22.8 | 21.9 | 549
613 | 2022-10-09 10:14 | 22.8 | 21.4 | 531
614 | 2022-10-09 10:15 | 22.8 | 21.3 | 543
615 | 2022-10-09 10:16 | 22.7 | 20.7 | 514
616 | 2022-10-09 10:17 | 22.3 | 21.6 | 515
617 | 2022-10-09 10:18 | 22.2 | 21.2 | 503
618 | 2022-10-09 10:19 | 22.2 | 21.9 | 528
619 | 2022-10-09 10:20 | 22.2 | 20.8 | 525
620 | 2022-10-09 10:21 | 22.4 | 21.3 | 542
621 | 2022-10-09 10:22 | 22.4 | 22.1 | 550
622 | 2022-10-09 10:23 | 22.6 | 21.8 | 668
623 | 2022-10-09 10:24 | 22.9 | 21.5 | 743
624 | 2022-10-09 10:25 | 23.1 | 20.8 | 739
625 | 2022-10-09 10:26 | 23.3 | 21.9 | 758
626 | 2022-10-09 10:27 | 23.3 | 21.8 | 758
627 | 2022-10-09 10:28 | 23.9 | 22 | 760
628 | 2022-10-09 10:29 | 23.2 | 22.3 | 763
629 | 2022-10-09 10:30 | 23.5 | 21.6 | 766
630 | 2022-10-09 10:31 | 23.4 | 21.5 | 769
631 | 2022-10-09 10:32 | 23.6 | 20.9 | 775
632 | 2022-10-09 10:33 | 23.6 | 21.7 | 777
633 | 2022-10-09 10:34 | 23.7 | 21.6 | 779
634 | 2022-10-09 10:35 | 23.8 | 21.8 | 785
635 | 2022-10-09 10:36 | 23.4 | 21.9 | 735
636 | 2022-10-09 10:37 | 23.5 | 21.5 | 722
637 | 2022-10-09 10:38 | 23.9 | 21.4 | 704
638 | 2022-10-09 10:39 | 24 | 21.4 | 648
639 | 2022-10-09 10:40 | 24.3 | 21.3 | 653
640 | 2022-10-09 10:41 | 24 | 21.5 | 753
641 | 2022-10-09 10:42 | 24.2 | 21.7 | 703
642 | 2022-10-09 10:43 | 24.1 | 21.3 | 708
643 | 2022-10-09 10:44 | 24 | 21.5 | 660
644 | 2022-10-09 10:45 | 23.7 | 21.5 | 677
645 | 2022-10-09 10:46 | 24 | 21.3 | 667
646 | 2022-10-09 10:47 | 24.4 | 21.5 | 612
647 | 2022-10-09 10:48 | 24 | 21.8 | 572
648 | 2022-10-09 10:49 | 23.9 | 21.1 | 512
649 | 2022-10-09 10:50 | 23.8 | 21.1 | 484
650 | 2022-10-09 10:51 | 24.2 | 21.2 | 544
651 | 2022-10-09 10:52 | 23.8 | 21.4 | 528
652 | 2022-10-09 10:53 | 23.5 | 21 | 648
653 | 2022-10-09 10:54 | 23.6 | 20.9 | 685
654 | 2022-10-09 10:55 | 23.2 | 21.4 | 669
655 | 2022-10-09 10:56 | 23.1 | 21.4 | 740
656 | 2022-10-09 10:57 | 22.9 | 21.6 | 776
657 | 2022-10-09 10:58 | 23.2 | 21.5 | 817
658 | 2022-10-09 10:59 | 23.4 | 21.2 | 823
659 | 2022-10-09 11:00 | 23.5 | 21.1 | 836
660 | 2022-10-09 11:01 | 23.8 | 21.5 | 846
661 | 2022-10-09 11:02 | 24.3 | 21.5 | 851
662 | 2022-10-09 11:03 | 24.1 | 21.7 | 855
663 | 2022-10-09 11:04 | 24.2 | 21.6 | 852
664 | 2022-10-09 11:05 | 24.3 | 21.6 | 855
665 | 2022-10-09 11:06 | 24.6 | 21.7 | 849
666 | 2022-10-09 11:07 | 24.3 | 21.6 | 856
667 | 2022-10-09 11:08 | 24.6 | 21.5 | 854
668 | 2022-10-09 11:09 | 25.3 | 21.6 | 866
669 | 2022-10-09 11:10 | 24.1 | 21.6 | 866
670 | 2022-10-09 11:11 | 24 | 21.3 | 873
671 | 2022-10-09 11:12 | 24.3 | 22.4 | 876
672 | 2022-10-09 11:13 | 24.4 | 21.6 | 877
673 | 2022-10-09 11:14 | 24.4 | 21.9 | 880
674 | 2022-10-09 11:15 | 24.9 | 20.9 | 883
675 | 2022-10-09 11:16 | 25.1 | 21.4 | 887
676 | 2022-10-09 11:17 | 25.4 | 21.8 | 879
677 | 2022-10-09 11:18 | 25 | 21.9 | 871
678 | 2022-10-09 11:19 | 25 | 21.3 | 863
679 | 2022-10-09 11:20 | 25.3 | 21.4 | 866
680 | 2022-10-09 11:21 | 25.5 | 21.8 | 863
681 | 2022-10-09 11:22 | 24.8 | 22.4 | 829
682 | 2022-10-09 11:23 | 24.4 | 22.1 | 831
683 | 2022-10-09 11:24 | 23.4 | 22 | 829
684 | 2022-10-09 11:25 | 23.7 | 21.5 | 818
685 | 2022-10-09 11:26 | 24.4 | 21.3 | 840
686 | 2022-10-09 11:27 | 24.7 | 21.9 | 628
687 | 2022-10-09 11:28 | 24.5 | 21.4 | 592
688 | 2022-10-09 11:29 | 24.5 | 21.9 | 644
689 | 2022-10-09 11:30 | 24.6 | 21.4 | 732
690 | 2022-10-09 11:31 | 24.4 | 21.4 | 770
691 | 2022-10-09 11:32 | 24.7 | 21.4 | 773
692 | 2022-10-09 11:33 | 24.8 | 22.1 | 833
693 | 2022-10-09 11:34 | 24.9 | 21.6 | 849
694 | 2022-10-09 11:35 | 24.8 | 21.7 | 773
695 | 2022-10-09 11:36 | 24.5 | 21.8 | 784
696 | 2022-10-09 11:37 | 24.1 | 21.6 | 732
697 | 2022-10-09 11:38 | 24.2 | 21.4 | 775
698 | 2022-10-09 11:39 | 24.4 | 21.6 | 805
699 | 2022-10-09 11:40 | 24.3 | 21.7 | 819
700 | 2022-10-09 11:41 | 25.1 | 21.5 | 829
701 | 2022-10-09 11:42 | 24.7 | 21.8 | 831
702 | 2022-10-09 11:43 | 24.9 | 21.7 | 820
703 | 2022-10-09 11:44 | 24.9 | 21.6 | 822
704 | 2022-10-09 11:45 | 24.8 | 21.7 | 814
705 | 2022-10-09 11:46 | 24.8 | 22.2 | 781
706 | 2022-10-09 11:47 | 25.2 | 22.6 | 800
707 | 2022-10-09 11:48 | 25.3 | 21.4 | 787
708 | 2022-10-09 11:49 | 24.4 | 21.8 | 742
709 | 2022-10-09 11:50 | 24.4 | 21.6 | 753
710 | 2022-10-09 11:51 | 24 | 21.6 | 775
711 | 2022-10-09 11:52 | 24.1 | 21.7 | 806
712 | 2022-10-09 11:53 | 24.1 | 22.1 | 827
713 | 2022-10-09 11:54 | 24.2 | 22 | 857
714 | 2022-10-09 11:55 | 24.4 | 21.2 | 871
715 | 2022-10-09 11:56 | 25.6 | 22.4 | 881
716 | 2022-10-09 11:57 | 25.2 | 21.5 | 895
717 | 2022-10-09 11:58 | 24.6 | 21.8 | 910
718 | 2022-10-09 11:59 | 24.6 | 21.7 | 890
719 | 2022-10-09 12:00 | 24.7 | 21.6 | 899
720 | 2022-10-09 12:01 | 24.1 | 21.2 | 900
721 | 2022-10-09 12:02 | 24.9 | 21.9 | 910
722 | 2022-10-09 12:03 | 24.7 | 21.8 | 919
723 | 2022-10-09 12:04 | 25.7 | 21.5 | 913
724 | 2022-10-09 12:05 | 25.5 | 21.4 | 918
725 | 2022-10-09 12:06 | 25.7 | 21.8 | 929
726 | 2022-10-09 12:07 | 25.8 | 21.5 | 939
727 | 2022-10-09 12:08 | 26.1 | 21.4 | 945
728 | 2022-10-09 12:09 | 25.9 | 22.4 | 954
729 | 2022-10-09 12:10 | 25.8 | 21.7 | 958
730 | 2022-10-09 12:11 | 25.8 | 21.4 | 966
731 | 2022-10-09 12:12 | 25.5 | 20.9 | 963
732 | 2022-10-09 12:13 | 25.5 | 21.6 | 969
733 | 2022-10-09 12:14 | 25.7 | 21.4 | 973
734 | 2022-10-09 12:15 | 26 | 21.8 | 970
735 | 2022-10-09 12:16 | 25.7 | 21.4 | 972
736 | 2022-10-09 12:17 | 26 | 22 | 980
737 | 2022-10-09 12:18 | 25.4 | 22 | 996
738 | 2022-10-09 12:19 | 25 | 21.8 | 972
739 | 2022-10-09 12:20 | 25.2 | 22.5 | 955
740 | 2022-10-09 12:21 | 25.5 | 21.5 | 903
741 | 2022-10-09 12:22 | 25.8 | 22.5 | 939
742 | 2022-10-09 12:23 | 25.6 | 22.2 | 947
743 | 2022-10-09 12:24 | 25.3 | 21.9 | 910
744 | 2022-10-09 12:25 | 25.5 | 21.6 | 819
745 | 2022-10-09 12:26 | 25 | 21.7 | 856
746 | 2022-10-09 12:27 | 25.2 | 21.7 | 918
747 | 2022-10-09 12:28 | 25.3 | 21.6 | 910
748 | 2022-10-09 12:29 | 25.1 | 22 | 895
749 | 2022-10-09 12:30 | 25.3 | 21.7 | 803
750 | 2022-10-09 12:31 | 25 | 21.6 | 801
751 | 2022-10-09 12:32 | 25.3 | 21.9 | 845
752 | 2022-10-09 12:33 | 25.3 | 22 | 934
753 | 2022-10-09 12:34 | 25.2 | 21.3 | 971
754 | 2022-10-09 12:35 | 25.8 | 21.2 | 995
755 | 2022-10-09 12:36 | 25.9 | 22.1 | 994
756 | 2022-10-09 12:37 | 25.6 | 21.6 | 980
757 | 2022-10-09 12:38 | 25.4 | 21.8 | 988
758 | 2022-10-09 12:39 | 25 | 21.6 | 972
759 | 2022-10-09 12:40 | 25 | 21.8 | 936
760 | 2022-10-09 12:41 | 25.4 | 21.3 | 963
761 | 2022-10-09 12:42 | 26 | 21.9 | 962
762 | 2022-10-09 12:43 | 26.2 | 21.2 | 843
763 | 2022-10-09 12:44 | 25.9 | 21.1 | 879
764 | 2022-10-09 12:45 | 26 | 21.3 | 942
765 | 2022-10-09 12:46 | 26.3 | 21.3 | 932
766 | 2022-10-09 12:47 | 26.8 | 22.4 | 935
767 | 2022-10-09 12:48 | 26.6 | 21.9 | 955
768 | 2022-10-09 12:49 | 26 | 22 | 961
769 | 2022-10-09 12:50 | 26.4 | 22.5 | 973
770 | 2022-10-09 12:51 | 25.8 | 21.9 | 978
771 | 2022-10-09 12:52 | 25.9 | 21.3 | 966
772 | 2022-10-09 12:53 | 25.8 | 22.1 | 967
773 | 2022-10-09 12:54 | 25 | 21.7 | 966
774 | 2022-10-09 12:55 | 25.2 | 22.1 | 966
775 | 2022-10-09 12:56 | 25.5 | 22.3 | 965
776 | 2022-10-09 12:57 | 25.5 | 22 | 958
777 | 2022-10-09 12:58 | 25.4 | 22.2 | 964
778 | 2022-10-09 12:59 | 25.7 | 22.1 | 963
779 | 2022-10-09 13:00 | 25.4 | 21.8 | 964
780 | 2022-10-09 13:01 | 25.8 | 21 | 967
781 | 2022-10-09 13:02 | 25.6 | 22.2 | 973
782 | 2022-10-09 13:03 | 25.2 | 22.2 | 976
783 | 2022-10-09 13:04 | 25.2 | 22 | 975
784 | 2022-10-09 13:05 | 25.5 | 21.1 | 979
785 | 2022-10-09 13:06 | 25.1 | 21.5 | 974
786 | 2022-10-09 13:07 | 25 | 22.5 | 967
787 | 2022-10-09 13:08 | 25.2 | 21.7 | 967
788 | 2022-10-09 13:09 | 25.8 | 22.4 | 978
789 | 2022-10-09 13:10 | 25.7 | 21.8 | 977
790 | 2022-10-09 13:11 | 26 | 21.7 | 972
791 | 2022-10-09 13:12 | 25.7 | 22.1 | 966
792 | 2022-10-09 13:13 | 26.4 | 21.7 | 964
793 | 2022-10-09 13:14 | 26.2 | 21.8 | 967
794 | 2022-10-09 13:15 | 26.2 | 22.1 | 980
795 | 2022-10-09 13:16 | 26.5 | 21.3 | 979
796 | 2022-10-09 13:17 | 26.9 | 21.8 | 990
797 | 2022-10-09 13:18 | 26.6 | 21.9 | 993
798 | 2022-10-09 13:19 | 27 | 22 | 993
799 | 2022-10-09 13:20 | 26.6 | 22 | 994
800 | 2022-10-09 13:21 | 26.9 | 21.9 | 1000
801 | 2022-10-09 13:22 | 27 | 22.3 | 996
802 | 2022-10-09 13:23 | 27 | 21.8 | 992
803 | 2022-10-09 13:24 | 26.9 | 22.1 | 992
804 | 2022-10-09 13:25 | 26.9 | 21.8 | 987
805 | 2022-10-09 13:26 | 27 | 21.9 | 987
806 | 2022-10-09 13:27 | 27.4 | 22 | 984
807 | 2022-10-09 13:28 | 27.2 | 21.8 | 984
808 | 2022-10-09 13:29 | 26.8 | 21.8 | 980
809 | 2022-10-09 13:30 | 27.1 | 21.9 | 978
810 | 2022-10-09 13:31 | 27.1 | 21.3 | 980
811 | 2022-10-09 13:32 | 26.4 | 22.1 | 972
812 | 2022-10-09 13:33 | 26 | 21.6 | 959
813 | 2022-10-09 13:34 | 26.4 | 22.3 | 948
814 | 2022-10-09 13:35 | 26.4 | 22.6 | 969
815 | 2022-10-09 13:36 | 26 | 22.7 | 979
816 | 2022-10-09 13:37 | 26.6 | 22.1 | 981
817 | 2022-10-09 13:38 | 26.6 | 22.3 | 971
818 | 2022-10-09 13:39 | 26.3 | 21.9 | 964
819 | 2022-10-09 13:40 | 26.1 | 21.9 | 959
820 | 2022-10-09 13:41 | 25.6 | 21.9 | 958
821 | 2022-10-09 13:42 | 26.3 | 22.1 | 952
822 | 2022-10-09 13:43 | 26.5 | 21.3 | 948
823 | 2022-10-09 13:44 | 26.3 | 21.8 | 951
824 | 2022-10-09 13:45 | 27.1 | 22.1 | 957
825 | 2022-10-09 13:46 | 27.5 | 21.6 | 962
826 | 2022-10-09 13:47 | 27.2 | 21.1 | 964
827 | 2022-10-09 13:48 | 27.4 | 21.2 | 969
828 | 2022-10-09 13:49 | 27.6 | 22.3 | 969
829 | 2022-10-09 13:50 | 27.4 | 21.9 | 966
830 | 2022-10-09 13:51 | 27.6 | 22.1 | 962
831 | 2022-10-09 13:52 | 27.5 | 21.8 | 964
832 | 2022-10-09 13:53 | 26.9 | 21.9 | 964
833 | 2022-10-09 13:54 | 26.7 | 21.8 | 962
834 | 2022-10-09 13:55 | 26.8 | 21.9 | 957
835 | 2022-10-09 13:56 | 26.8 | 22.3 | 960
836 | 2022-10-09 13:57 | 26.9 | 21.9 | 957
837 | 2022-10-09 13:58 | 26.6 | 21.3 | 950
838 | 2022-10-09 13:59 | 26.7 | 21.7 | 951
839 | 2022-10-09 14:00 | 26.7 | 22.2 | 953
840 | 2022-10-09 14:01 | 26.8 | 21.9 | 954
841 | 2022-10-09 14:02 | 27 | 21.7 | 963
842 | 2022-10-09 14:03 | 27.4 | 21.9 | 961
843 | 2022-10-09 14:04 | 26.9 | 21.9 | 955
844 | 2022-10-09 14:05 | 26.3 | 22.5 | 957
845 | 2022-10-09 14:06 | 26.4 | 21.4 | 956
846 | 2022-10-09 14:07 | 26.8 | 21.1 | 954
847 | 2022-10-09 14:08 | 27.1 | 21.1 | 951
848 | 2022-10-09 14:09 | 27.3 | 22.2 | 948
849 | 2022-10-09 14:10 | 27.2 | 22.6 | 939
850 | 2022-10-09 14:11 | 27.3 | 21.9 | 938
851 | 2022-10-09 14:12 | 27.2 | 21.7 | 933
852 | 2022-10-09 14:13 | 27.5 | 21.2 | 931
853 | 2022-10-09 14:14 | 27.3 | 22.1 | 937
854 | 2022-10-09 14:15 | 26.7 | 22.8 | 930
855 | 2022-10-09 14:16 | 27.3 | 22.7 | 928
856 | 2022-10-09 14:17 | 27.3 | 21.9 | 931
857 | 2022-10-09 14:18 | 27 | 21.9 | 929
858 | 2022-10-09 14:19 | 27.2 | 22.1 | 927
859 | 2022-10-09 14:20 | 28 | 21.9 | 926
860 | 2022-10-09 14:21 | 28.2 | 21.7 | 920
861 | 2022-10-09 14:22 | 28 | 22.3 | 920
862 | 2022-10-09 14:23 | 27.1 | 22 | 921
863 | 2022-10-09 14:24 | 26.8 | 21.9 | 917
864 | 2022-10-09 14:25 | 27.3 | 22.8 | 922
865 | 2022-10-09 14:26 | 26.9 | 21.9 | 924
866 | 2022-10-09 14:27 | 27 | 22.1 | 924
867 | 2022-10-09 14:28 | 27.3 | 21.8 | 922
868 | 2022-10-09 14:29 | 27.5 | 22.4 | 921
869 | 2022-10-09 14:30 | 27.1 | 22.7 | 920
870 | 2022-10-09 14:31 | 27.1 | 21.7 | 911
871 | 2022-10-09 14:32 | 27.3 | 21.9 | 914
872 | 2022-10-09 14:33 | 26.5 | 21.9 | 914
873 | 2022-10-09 14:34 | 26.6 | 22.2 | 915
874 | 2022-10-09 14:35 | 26.7 | 21.9 | 913
875 | 2022-10-09 14:36 | 26.6 | 22.7 | 911
876 | 2022-10-09 14:37 | 26.4 | 22.3 | 908
877 | 2022-10-09 14:38 | 25.9 | 21.9 | 904
878 | 2022-10-09 14:39 | 26.3 | 21.9 | 899
879 | 2022-10-09 14:40 | 26.5 | 21.7 | 894
880 | 2022-10-09 14:41 | 26.4 | 22.8 | 886
881 | 2022-10-09 14:42 | 26.7 | 22.9 | 888
882 | 2022-10-09 14:43 | 26.6 | 22.6 | 885
883 | 2022-10-09 14:44 | 26.9 | 21.7 | 896
884 | 2022-10-09 14:45 | 27.5 | 21.9 | 891
885 | 2022-10-09 14:46 | 27.4 | 22.1 | 888
886 | 2022-10-09 14:47 | 26.9 | 22.1 | 882
887 | 2022-10-09 14:48 | 27.2 | 21.9 | 876
888 | 2022-10-09 14:49 | 26.4 | 22 | 871
889 | 2022-10-09 14:50 | 26.3 | 22.1 | 867
890 | 2022-10-09 14:51 | 26 | 21.5 | 861
891 | 2022-10-09 14:52 | 26 | 21.1 | 875
892 | 2022-10-09 14:53 | 26.4 | 21.9 | 870
893 | 2022-10-09 14:54 | 26.2 | 21.8 | 863
894 | 2022-10-09 14:55 | 26.2 | 21.9 | 857
895 | 2022-10-09 14:56 | 26.3 | 22 | 848
896 | 2022-10-09 14:57 | 26.4 | 22.1 | 848
897 | 2022-10-09 14:58 | 26.6 | 21.9 | 853
898 | 2022-10-09 14:59 | 26.5 | 22 | 851
899 | 2022-10-09 15:00 | 25.4 | 22.5 | 853
900 | 2022-10-09 15:01 | 25.1 | 21.5 | 850
901 | 2022-10-09 15:02 | 25.7 | 22.1 | 852
902 | 2022-10-09 15:03 | 26.3 | 21.9 | 850
903 | 2022-10-09 15:04 | 26.8 | 22.5 | 847
904 | 2022-10-09 15:05 | 27.1 | 22.2 | 844
905 | 2022-10-09 15:06 | 26.8 | 21.7 | 840
906 | 2022-10-09 15:07 | 26.6 | 22.1 | 831
907 | 2022-10-09 15:08 | 26.1 | 22.2 | 826
908 | 2022-10-09 15:09 | 26.4 | 22 | 823
909 | 2022-10-09 15:10 | 26.6 | 21.4 | 820
910 | 2022-10-09 15:11 | 27.2 | 22.6 | 818
911 | 2022-10-09 15:12 | 27.5 | 22.1 | 823
912 | 2022-10-09 15:13 | 27.6 | 22.3 | 825
913 | 2022-10-09 15:14 | 27 | 21.9 | 826
914 | 2022-10-09 15:15 | 27.3 | 21.9 | 830
915 | 2022-10-09 15:16 | 27.1 | 22.5 | 822
916 | 2022-10-09 15:17 | 26.8 | 22.1 | 810
917 | 2022-10-09 15:18 | 26.9 | 22.1 | 804
918 | 2022-10-09 15:19 | 27 | 22 | 804
919 | 2022-10-09 15:20 | 27 | 21.9 | 804
920 | 2022-10-09 15:21 | 26.8 | 22.4 | 800
921 | 2022-10-09 15:22 | 26.5 | 22.2 | 798
922 | 2022-10-09 15:23 | 26.6 | 22.4 | 788
923 | 2022-10-09 15:24 | 26.6 | 21.9 | 780
924 | 2022-10-09 15:25 | 26.7 | 21.9 | 777
925 | 2022-10-09 15:26 | 26.7 | 22 | 780
926 | 2022-10-09 15:27 | 25.6 | 22.3 | 777
927 | 2022-10-09 15:28 | 25.5 | 22.3 | 779
928 | 2022-10-09 15:29 | 25.8 | 22.2 | 772
929 | 2022-10-09 15:30 | 26.1 | 22.3 | 770
930 | 2022-10-09 15:31 | 26 | 21.8 | 772
931 | 2022-10-09 15:32 | 26.3 | 21.8 | 771
932 | 2022-10-09 15:33 | 26.1 | 21.5 | 768
933 | 2022-10-09 15:34 | 25.8 | 21.3 | 764
934 | 2022-10-09 15:35 | 25.9 | 22.1 | 753
935 | 2022-10-09 15:36 | 26.2 | 22.5 | 750
936 | 2022-10-09 15:37 | 25.7 | 22.7 | 746
937 | 2022-10-09 15:38 | 25.7 | 21.7 | 742
938 | 2022-10-09 15:39 | 26 | 22.6 | 737
939 | 2022-10-09 15:40 | 26.5 | 22.6 | 735
940 | 2022-10-09 15:41 | 27 | 21.4 | 729
941 | 2022-10-09 15:42 | 27 | 21.7 | 727
942 | 2022-10-09 15:43 | 27.2 | 22.1 | 726
943 | 2022-10-09 15:44 | 27 | 21.3 | 724
944 | 2022-10-09 15:45 | 26.2 | 21.9 | 723
945 | 2022-10-09 15:46 | 26.4 | 21.3 | 718
946 | 2022-10-09 15:47 | 26.6 | 21.9 | 712
947 | 2022-10-09 15:48 | 26.6 | 22.1 | 710
948 | 2022-10-09 15:49 | 26.3 | 21.8 | 707
949 | 2022-10-09 15:50 | 25.8 | 22.1 | 706
950 | 2022-10-09 15:51 | 25.7 | 22.2 | 702
951 | 2022-10-09 15:52 | 25.3 | 22 | 699
952 | 2022-10-09 15:53 | 25.6 | 21.9 | 694
953 | 2022-10-09 15:54 | 25.8 | 21.7 | 689
954 | 2022-10-09 15:55 | 26.1 | 21.7 | 686
955 | 2022-10-09 15:56 | 26.4 | 22.2 | 683
956 | 2022-10-09 15:57 | 26.7 | 21.9 | 680
957 | 2022-10-09 15:58 | 26.3 | 21.7 | 677
958 | 2022-10-09 15:59 | 26.4 | 22.3 | 672
959 | 2022-10-09 16:00 | 26.2 | 22 | 666
960 | 2022-10-09 16:01 | 25.8 | 22.1 | 665
961 | 2022-10-09 16:02 | 25.7 | 21.9 | 664
962 | 2022-10-09 16:03 | 26.1 | 21.8 | 660
963 | 2022-10-09 16:04 | 26.1 | 21.8 | 656
964 | 2022-10-09 16:05 | 26.2 | 22.3 | 654
965 | 2022-10-09 16:06 | 26.4 | 22.4 | 649
966 | 2022-10-09 16:07 | 26.6 | 21.9 | 646
967 | 2022-10-09 16:08 | 25.9 | 22 | 641
968 | 2022-10-09 16:09 | 26 | 22.2 | 638
969 | 2022-10-09 16:10 | 25.8 | 21.9 | 636
970 | 2022-10-09 16:11 | 26.2 | 22 | 634
971 | 2022-10-09 16:12 | 25.9 | 22.1 | 631
972 | 2022-10-09 16:13 | 25.9 | 22.1 | 627
973 | 2022-10-09 16:14 | 25.9 | 22.3 | 621
974 | 2022-10-09 16:15 | 25.9 | 22.1 | 621
975 | 2022-10-09 16:16 | 25.7 | 22 | 616
976 | 2022-10-09 16:17 | 25.6 | 21.8 | 610
977 | 2022-10-09 16:18 | 25.4 | 21.3 | 606
978 | 2022-10-09 16:19 | 25.6 | 21.9 | 603
979 | 2022-10-09 16:20 | 25.7 | 22.1 | 600
980 | 2022-10-09 16:21 | 26.2 | 21.7 | 597
981 | 2022-10-09 16:22 | 25.7 | 22.5 | 592
982 | 2022-10-09 16:23 | 25.2 | 22.2 | 589
983 | 2022-10-09 16:24 | 25.8 | 21.8 | 586
984 | 2022-10-09 16:25 | 26 | 21.6 | 583
985 | 2022-10-09 16:26 | 25.9 | 22.2 | 578
986 | 2022-10-09 16:27 | 26.1 | 22.6 | 574
987 | 2022-10-09 16:28 | 25.9 | 22.5 | 571
988 | 2022-10-09 16:29 | 25.8 | 22 | 569
989 | 2022-10-09 16:30 | 25.9 | 22.2 | 564
990 | 2022-10-09 16:31 | 26.1 | 22.2 | 559
991 | 2022-10-09 16:32 | 26.3 | 22.8 | 556
992 | 2022-10-09 16:33 | 26.2 | 23.1 | 551
993 | 2022-10-09 16:34 | 25.9 | 22 | 548
994 | 2022-10-09 16:35 | 25.8 | 22.2 | 545
995 | 2022-10-09 16:36 | 24.8 | 22.3 | 540
996 | 2022-10-09 16:37 | 24.6 | 22.4 | 535
997 | 2022-10-09 16:38 | 25.2 | 22.1 | 531
998 | 2022-10-09 16:39 | 25.4 | 21.9 | 527
999 | 2022-10-09 16:40 | 25.7 | 22 | 523
1000 | 2022-10-09 16:41 | 25.9 | 22.4 | 518
1001 | 2022-10-09 16:42 | 25.5 | 22 | 514
1002 | 2022-10-09 16:43 | 24.9 | 22.1 | 509
1003 | 2022-10-09 16:44 | 24.9 | 22.5 | 506
1004 | 2022-10-09 16:45 | 25 | 22.3 | 500
1005 | 2022-10-09 16:46 | 25.5 | 21.6 | 495
1006 | 2022-10-09 16:47 | 25.8 | 22 | 491
1007 | 2022-10-09 16:48 | 25.9 | 21.8 | 487
1008 | 2022-10-09 16:49 | 25.9 | 21.9 | 483
1009 | 2022-10-09 16:50 | 26.2 | 22.1 | 480
1010 | 2022-10-09 16:51 | 26.2 | 21.9 | 476
1011 | 2022-10-09 16:52 | 26.1 | 22.2 | 472
1012 | 2022-10-09 16:53 | 25.5 | 22.4 | 469
1013 | 2022-10-09 16:54 | 25.4 | 22.8 | 463
1014 | 2022-10-09 16:55 | 25.3 | 22.3 | 460
1015 | 2022-10-09 16:56 | 25.4 | 22.6 | 455
1016 | 2022-10-09 16:57 | 25.5 | 23 | 452
1017 | 2022-10-09 16:58 | 25.3 | 22.2 | 447
1018 | 2022-10-09 16:59 | 25.2 | 23 | 445
1019 | 2022-10-09 17:00 | 24.8 | 22.9 | 443
1020 | 2022-10-09 17:01 | 24.8 | 22.5 | 440
1021 | 2022-10-09 17:02 | 24.9 | 22.2 | 434
1022 | 2022-10-09 17:03 | 24.7 | 21.6 | 429
1023 | 2022-10-09 17:04 | 24.9 | 21.4 | 423
1024 | 2022-10-09 17:05 | 25 | 22.5 | 417
1025 | 2022-10-09 17:06 | 25.1 | 21.6 | 412
1026 | 2022-10-09 17:07 | 25.3 | 22.8 | 408
1027 | 2022-10-09 17:08 | 25.1 | 22 | 404
1028 | 2022-10-09 17:09 | 25 | 22.8 | 399
1029 | 2022-10-09 17:10 | 25 | 23 | 393
1030 | 2022-10-09 17:11 | 25 | 22.4 | 390
1031 | 2022-10-09 17:12 | 25.3 | 22 | 385
1032 | 2022-10-09 17:13 | 25.2 | 22.1 | 382
1033 | 2022-10-09 17:14 | 24.8 | 22.1 | 378
1034 | 2022-10-09 17:15 | 25 | 22.5 | 374
1035 | 2022-10-09 17:16 | 24.6 | 22.6 | 369
1036 | 2022-10-09 17:17 | 24.8 | 23.1 | 364
1037 | 2022-10-09 17:18 | 24.4 | 22.4 | 357
1038 | 2022-10-09 17:19 | 24.3 | 22.2 | 353
1039 | 2022-10-09 17:20 | 24.3 | 22.1 | 350
1040 | 2022-10-09 17:21 | 24.3 | 21.6 | 345
1041 | 2022-10-09 17:22 | 23.9 | 22.5 | 342
1042 | 2022-10-09 17:23 | 24.2 | 21.8 | 337
1043 | 2022-10-09 17:24 | 24.4 | 22.8 | 334
1044 | 2022-10-09 17:25 | 24.8 | 22.3 | 328
1045 | 2022-10-09 17:26 | 24.7 | 22.1 | 322
1046 | 2022-10-09 17:27 | 25.2 | 22.3 | 319
1047 | 2022-10-09 17:28 | 24.6 | 22 | 315
1048 | 2022-10-09 17:29 | 24.5 | 22.4 | 308
1049 | 2022-10-09 17:30 | 24.5 | 22.1 | 305
1050 | 2022-10-09 17:31 | 24.5 | 22.2 | 300
1051 | 2022-10-09 17:32 | 24.2 | 22 | 296
1052 | 2022-10-09 17:33 | 24.1 | 22.3 | 291
1053 | 2022-10-09 17:34 | 23.8 | 22.1 | 288
1054 | 2022-10-09 17:35 | 23.6 | 22 | 285
1055 | 2022-10-09 17:36 | 23.7 | 22.1 | 280
1056 | 2022-10-09 17:37 | 23.9 | 22.1 | 276
1057 | 2022-10-09 17:38 | 23.8 | 22.4 | 272
1058 | 2022-10-09 17:39 | 23.9 | 22.3 | 269
1059 | 2022-10-09 17:40 | 24.2 | 22.2 | 265
1060 | 2022-10-09 17:41 | 24.1 | 22 | 260
1061 | 2022-10-09 17:42 | 24 | 22.3 | 256
1062 | 2022-10-09 17:43 | 23.8 | 22.2 | 252
1063 | 2022-10-09 17:44 | 23.7 | 22.1 | 248
1064 | 2022-10-09 17:45 | 23.8 | 21.9 | 245
1065 | 2022-10-09 17:46 | 23.6 | 22 | 241
1066 | 2022-10-09 17:47 | 23.7 | 21.2 | 237
1067 | 2022-10-09 17:48 | 23.7 | 21.5 | 234
1068 | 2022-10-09 17:49 | 23.9 | 22.9 | 229
1069 | 2022-10-09 17:50 | 23.6 | 21.6 | 226
1070 | 2022-10-09 17:51 | 23.6 | 21.9 | 221
1071 | 2022-10-09 17:52 | 23.9 | 21.7 | 217
1072 | 2022-10-09 17:53 | 23.4 | 22.4 | 212
1073 | 2022-10-09 17:54 | 23.6 | 21.5 | 208
1074 | 2022-10-09 17:55 | 23.6 | 21.8 | 204
1075 | 2022-10-09 17:56 | 23.7 | 22.9 | 199
1076 | 2022-10-09 17:57 | 23.9 | 22.2 | 195
1077 | 2022-10-09 17:58 | 23.7 | 22.1 | 191
1078 | 2022-10-09 17:59 | 23.6 | 21.8 | 186
1079 | 2022-10-09 18:00 | 23.5 | 21.5 | 182
1080 | 2022-10-09 18:01 | 23.6 | 22.3 | 178
1081 | 2022-10-09 18:02 | 23.4 | 22.2 | 174
1082 | 2022-10-09 18:03 | 23.2 | 22.1 | 170
1083 | 2022-10-09 18:04 | 23.1 | 22 | 167
1084 | 2022-10-09 18:05 | 23 | 22.1 | 162
1085 | 2022-10-09 18:06 | 22.9 | 22.1 | 158
1086 | 2022-10-09 18:07 | 23.1 | 22.6 | 154
1087 | 2022-10-09 18:08 | 23 | 21.9 | 149
1088 | 2022-10-09 18:09 | 23.2 | 22.5 | 146
1089 | 2022-10-09 18:10 | 23.3 | 23 | 141
1090 | 2022-10-09 18:11 | 23.3 | 22.3 | 138
1091 | 2022-10-09 18:12 | 23 | 22.4 | 134
1092 | 2022-10-09 18:13 | 23 | 23 | 130
1093 | 2022-10-09 18:14 | 23 | 22.2 | 126
1094 | 2022-10-09 18:15 | 22.8 | 23 | 123
1095 | 2022-10-09 18:16 | 22.6 | 21.9 | 118
1096 | 2022-10-09 18:17 | 22.7 | 22.1 | 115
1097 | 2022-10-09 18:18 | 22.6 | 21.5 | 110
1098 | 2022-10-09 18:19 | 22.7 | 21.6 | 106
1099 | 2022-10-09 18:20 | 22.6 | 22.9 | 102
1100 | 2022-10-09 18:21 | 22.5 | 22.8 | 98
1101 | 2022-10-09 18:22 | 22.3 | 21.6 | 94
1102 | 2022-10-09 18:23 | 22.3 | 21.4 | 90
1103 | 2022-10-09 18:24 | 22.2 | 21.7 | 85
1104 | 2022-10-09 18:25 | 22.1 | 22.4 | 82
1105 | 2022-10-09 18:26 | 22.1 | 22.2 | 78
1106 | 2022-10-09 18:27 | 22 | 22 | 74
1107 | 2022-10-09 18:28 | 21.9 | 21.7 | 70
1108 | 2022-10-09 18:29 | 21.8 | 22.1 | 65
1109 | 2022-10-09 18:30 | 21.6 | 22.3 | 52
1110 | 2022-10-09 18:31 | 21.6 | 22 | 40
1111 | 2022-10-09 18:32 | 21.4 | 22.3 | 30
1112 | 2022-10-09 18:33 | 21.3 | 22.1 | 19
1113 | 2022-10-09 18:34 | 21.4 | 22.4 | 23
1114 | 2022-10-09 18:35 | 21.5 | 22.4 | 26
1115 | 2022-10-09 18:36 | 21.3 | 21.8 | 24
1116 | 2022-10-09 18:37 | 21.5 | 22.6 | 22
1117 | 2022-10-09 18:38 | 21.3 | 22 | 16
1118 | 2022-10-09 18:39 | 21.2 | 22.2 | 14
1119 | 2022-10-09 18:40 | 21.4 | 22.4 | 11
1120 | 2022-10-09 18:41 | 21.1 | 22.2 | 8
1121 | 2022-10-09 18:42 | 21 | 22.3 | 7
1122 | 2022-10-09 18:43 | 20.9 | 22.1 | 7
1123 | 2022-10-09 18:44 | 20.8 | 22.1 | 6
1124 | 2022-10-09 18:45 | 20.9 | 22.1 | 5
1125 | 2022-10-09 18:46 | 20.8 | 22.3 | 4
1126 | 2022-10-09 18:47 | 20.5 | 21.9 | 4
1127 | 2022-10-09 18:48 | 20.5 | 22.3 | 3
1128 | 2022-10-09 18:49 | 20.4 | 22.1 | 3
1129 | 2022-10-09 18:50 | 20.5 | 22.2 | 2
1130 | 2022-10-09 18:51 | 20.3 | 22 | 1
1131 | 2022-10-09 18:52 | 20.4 | 22 | 1
1132 | 2022-10-09 18:53 | 20.3 | 22.2 | 0
1133 | 2022-10-09 18:54 | 20.3 | 22.2 | 0
1134 | 2022-10-09 18:55 | 20.3 | 21.9 | 0
1135 | 2022-10-09 18:56 | 20.2 | 22.1 | 0
1136 | 2022-10-09 18:57 | 20.2 | 22.1 | 0
1137 | 2022-10-09 18:58 | 20.1 | 21.8 | 0
1138 | 2022-10-09 18:59 | 19.8 | 21.5 | 0
1139 | 2022-10-09 19:00 | 19.8 | 22.1 | 0
1140 | 2022-10-09 19:01 | 19.8 | 22.1 | 0
1141 | 2022-10-09 19:02 | 19.8 | 22.1 | 0
1142 | 2022-10-09 19:03 | 19.8 | 22.1 | 0
1143 | 2022-10-09 19:04 | 19.6 | 22.2 | 0
1144 | 2022-10-09 19:05 | 19.6 | 22.1 | 0
1145 | 2022-10-09 19:06 | 19.5 | 22.1 | 0
1146 | 2022-10-09 19:07 | 19.4 | 22.2 | 0
1147 | 2022-10-09 19:08 | 19.2 | 22.2 | 0
1148 | 2022-10-09 19:09 | 19.3 | 22.3 | 0
1149 | 2022-10-09 19:10 | 19 | 22.3 | 0
1150 | 2022-10-09 19:11 | 19.2 | 22.5 | 0
1151 | 2022-10-09 19:12 | 19.4 | 22.4 | 0
1152 | 2022-10-09 19:13 | 19.3 | 21.9 | 0
1153 | 2022-10-09 19:14 | 19.5 | 21.9 | 0
1154 | 2022-10-09 19:15 | 19.2 | 22.1 | 0
1155 | 2022-10-09 19:16 | 19.3 | 22 | 0
1156 | 2022-10-09 19:17 | 19.1 | 21.9 | 0
1157 | 2022-10-09 19:18 | 19.2 | 21.8 | 0
1158 | 2022-10-09 19:19 | 19.2 | 22.1 | 0
1159 | 2022-10-09 19:20 | 19.2 | 22.8 | 0
1160 | 2022-10-09 19:21 | 19.3 | 22.7 | 0
1161 | 2022-10-09 19:22 | 19.2 | 22.6 | 0
1162 | 2022-10-09 19:23 | 19.2 | 22.1 | 0
1163 | 2022-10-09 19:24 | 19.1 | 22.3 | 0
1164 | 2022-10-09 19:25 | 19.2 | 22.2 | 0
1165 | 2022-10-09 19:26 | 19.3 | 22 | 0
1166 | 2022-10-09 19:27 | 19.2 | 22.1 | 0
1167 | 2022-10-09 19:28 | 19.2 | 22.2 | 0
1168 | 2022-10-09 19:29 | 19.3 | 22.1 | 0
1169 | 2022-10-09 19:30 | 19.3 | 22.3 | 0
1170 | 2022-10-09 19:31 | 19.2 | 22 | 0
1171 | 2022-10-09 19:32 | 19 | 22.2 | 0
1172 | 2022-10-09 19:33 | 18.8 | 22 | 0
1173 | 2022-10-09 19:34 | 18.9 | 21.9 | 0
1174 | 2022-10-09 19:35 | 18.8 | 22.3 | 0
1175 | 2022-10-09 19:36 | 19.2 | 21.6 | 0
1176 | 2022-10-09 19:37 | 19.2 | 22.3 | 0
1177 | 2022-10-09 19:38 | 19.2 | 22 | 0
1178 | 2022-10-09 19:39 | 19.1 | 21.9 | 0
1179 | 2022-10-09 19:40 | 19 | 22.2 | 0
1180 | 2022-10-09 19:41 | 19 | 22.1 | 0
1181 | 2022-10-09 19:42 | 19.1 | 21.8 | 0
1182 | 2022-10-09 19:43 | 19 | 22 | 0
1183 | 2022-10-09 19:44 | 19 | 21.9 | 0
1184 | 2022-10-09 19:45 | 18.9 | 21.9 | 0
1185 | 2022-10-09 19:46 | 18.8 | 21.9 | 0
1186 | 2022-10-09 19:47 | 18.7 | 22.1 | 0
1187 | 2022-10-09 19:48 | 18.6 | 22.2 | 0
1188 | 2022-10-09 19:49 | 18.7 | 22.2 | 0
1189 | 2022-10-09 19:50 | 18.9 | 21.9 | 0
1190 | 2022-10-09 19:51 | 18.7 | 22.3 | 0
1191 | 2022-10-09 19:52 | 18.6 | 22.1 | 0
1192 | 2022-10-09 19:53 | 18.7 | 21.9 | 0
1193 | 2022-10-09 19:54 | 18.7 | 22 | 0
1194 | 2022-10-09 19:55 | 18.5 | 22.3 | 0
1195 | 2022-10-09 19:56 | 18.6 | 21.9 | 0
1196 | 2022-10-09 19:57 | 18.8 | 21.8 | 0
1197 | 2022-10-09 19:58 | 18.6 | 22.1 | 0
1198 | 2022-10-09 19:59 | 18.5 | 22.1 | 0
1199 | 2022-10-09 20:00 | 18.5 | 22 | 0
1200 | 2022-10-09 20:01 | 18.4 | 22 | 0
1201 | 2022-10-09 20:02 | 18.5 | 22.1 | 0
1202 | 2022-10-09 20:03 | 18.6 | 22.1 | 0
1203 | 2022-10-09 20:04 | 18.4 | 22.2 | 0
1204 | 2022-10-09 20:05 | 18.6 | 22.1 | 0
1205 | 2022-10-09 20:06 | 18.7 | 22.2 | 0
1206 | 2022-10-09 20:07 | 18.9 | 21.7 | 0
1207 | 2022-10-09 20:08 | 18.7 | 22.2 | 0
1208 | 2022-10-09 20:09 | 18.7 | 22.2 | 0
1209 | 2022-10-09 20:10 | 18.9 | 22.1 | 0
1210 | 2022-10-09 20:11 | 18.6 | 21.3 | 0
1211 | 2022-10-09 20:12 | 18.4 | 21.3 | 0
1212 | 2022-10-09 20:13 | 18.3 | 21.4 | 0
1213 | 2022-10-09 20:14 | 18 | 21.6 | 0
1214 | 2022-10-09 20:15 | 18 | 21.7 | 0
1215 | 2022-10-09 20:16 | 18.2 | 22.8 | 0
1216 | 2022-10-09 20:17 | 18.4 | 22.4 | 0
1217 | 2022-10-09 20:18 | 18.2 | 22 | 0
1218 | 2022-10-09 20:19 | 18.7 | 22.8 | 0
1219 | 2022-10-09 20:20 | 19 | 22.3 | 0
1220 | 2022-10-09 20:21 | 18.7 | 21.6 | 0
1221 | 2022-10-09 20:22 | 18.9 | 22.1 | 0
1222 | 2022-10-09 20:23 | 18.3 | 22.7 | 0
1223 | 2022-10-09 20:24 | 18.3 | 21.4 | 0
1224 | 2022-10-09 20:25 | 18.2 | 22.4 | 0
1225 | 2022-10-09 20:26 | 18.3 | 22.7 | 0
1226 | 2022-10-09 20:27 | 18.5 | 21.7 | 0
1227 | 2022-10-09 20:28 | 18.5 | 21.9 | 0
1228 | 2022-10-09 20:29 | 18.5 | 22.6 | 0
1229 | 2022-10-09 20:30 | 18.5 | 22.1 | 0
1230 | 2022-10-09 20:31 | 18.8 | 21.6 | 0
1231 | 2022-10-09 20:32 | 18.7 | 21.6 | 0
1232 | 2022-10-09 20:33 | 18.5 | 21.8 | 0
1233 | 2022-10-09 20:34 | 18.4 | 21.9 | 0
1234 | 2022-10-09 20:35 | 18.2 | 22 | 0
1235 | 2022-10-09 20:36 | 18.2 | 21.4 | 0
1236 | 2022-10-09 20:37 | 18.3 | 22.2 | 0
1237 | 2022-10-09 20:38 | 18.5 | 21.8 | 0
1238 | 2022-10-09 20:39 | 18.4 | 21.8 | 0
1239 | 2022-10-09 20:40 | 18.3 | 21.9 | 0
1240 | 2022-10-09 20:41 | 18.3 | 21.5 | 0
1241 | 2022-10-09 20:42 | 18.2 | 21.5 | 0
1242 | 2022-10-09 20:43 | 18.1 | 22.1 | 0
1243 | 2022-10-09 20:44 | 18.1 | 22.4 | 0
1244 | 2022-10-09 20:45 | 18.1 | 22.1 | 0
1245 | 2022-10-09 20:46 | 18 | 22.4 | 0
1246 | 2022-10-09 20:47 | 17.8 | 21.9 | 0
1247 | 2022-10-09 20:48 | 17.8 | 21.9 | 0
1248 | 2022-10-09 20:49 | 18.1 | 22.1 | 0
1249 | 2022-10-09 20:50 | 18.1 | 22.3 | 0
1250 | 2022-10-09 20:51 | 17.9 | 22.2 | 0
1251 | 2022-10-09 20:52 | 17.8 | 21.9 | 0
1252 | 2022-10-09 20:53 | 17.5 | 22.1 | 0
1253 | 2022-10-09 20:54 | 17.4 | 22 | 0
1254 | 2022-10-09 20:55 | 17.7 | 22.1 | 0
1255 | 2022-10-09 20:56 | 17.7 | 22 | 0
1256 | 2022-10-09 20:57 | 17.7 | 22.4 | 0
1257 | 2022-10-09 20:58 | 18.1 | 22.2 | 0
1258 | 2022-10-09 20:59 | 18.1 | 22 | 0
1259 | 2022-10-09 21:00 | 17.9 | 22.4 | 0
1260 | 2022-10-09 21:01 | 17.7 | 22.4 | 0
1261 | 2022-10-09 21:02 | 17.6 | 21.9 | 0
1262 | 2022-10-09 21:03 | 17.4 | 22.3 | 0
1263 | 2022-10-09 21:04 | 17.2 | 22.2 | 0
1264 | 2022-10-09 21:05 | 17.1 | 22.1 | 0
1265 | 2022-10-09 21:06 | 17.4 | 22.2 | 0
1266 | 2022-10-09 21:07 | 17.2 | 22.3 | 0
1267 | 2022-10-09 21:08 | 17.2 | 22.4 | 0
1268 | 2022-10-09 21:09 | 17.4 | 22.9 | 0
1269 | 2022-10-09 21:10 | 17.5 | 22.3 | 0
1270 | 2022-10-09 21:11 | 17.5 | 22.5 | 0
1271 | 2022-10-09 21:12 | 17.2 | 21.9 | 0
1272 | 2022-10-09 21:13 | 17.2 | 22.5 | 0
1273 | 2022-10-09 21:14 | 17 | 22 | 0
1274 | 2022-10-09 21:15 | 16.9 | 22.7 | 0
1275 | 2022-10-09 21:16 | 16.6 | 22.3 | 0
1276 | 2022-10-09 21:17 | 16.6 | 21.9 | 0
1277 | 2022-10-09 21:18 | 16.5 | 22.7 | 0
1278 | 2022-10-09 21:19 | 16.4 | 21.6 | 0
1279 | 2022-10-09 21:20 | 16.5 | 22.4 | 0
1280 | 2022-10-09 21:21 | 16.6 | 21.7 | 0
1281 | 2022-10-09 21:22 | 16.3 | 21.5 | 0
1282 | 2022-10-09 21:23 | 16.4 | 22 | 0
1283 | 2022-10-09 21:24 | 16.3 | 22 | 0
1284 | 2022-10-09 21:25 | 16.5 | 21.9 | 0
1285 | 2022-10-09 21:26 | 16.4 | 22.3 | 0
1286 | 2022-10-09 21:27 | 16.5 | 22 | 0
1287 | 2022-10-09 21:28 | 16.3 | 22.1 | 0
1288 | 2022-10-09 21:29 | 16.3 | 22.2 | 0
1289 | 2022-10-09 21:30 | 16.1 | 22.4 | 0
1290 | 2022-10-09 21:31 | 16 | 22 | 0
1291 | 2022-10-09 21:32 | 16.1 | 22.4 | 0
1292 | 2022-10-09 21:33 | 15.8 | 22 | 0
1293 | 2022-10-09 21:34 | 15.8 | 22.2 | 0
1294 | 2022-10-09 21:35 | 15.7 | 21.9 | 0
1295 | 2022-10-09 21:36 | 15.8 | 22.2 | 0
1296 | 2022-10-09 21:37 | 15.8 | 22.1 | 0
1297 | 2022-10-09 21:38 | 15.9 | 21.5 | 0
1298 | 2022-10-09 21:39 | 15.7 | 21.5 | 0
1299 | 2022-10-09 21:40 | 15.8 | 22.1 | 0
1300 | 2022-10-09 21:41 | 15.8 | 22.4 | 0
1301 | 2022-10-09 21:42 | 15.7 | 22 | 0
1302 | 2022-10-09 21:43 | 15.5 | 22.3 | 0
1303 | 2022-10-09 21:44 | 15.6 | 21.9 | 0
1304 | 2022-10-09 21:45 | 15.5 | 22.1 | 0
1305 | 2022-10-09 21:46 | 15.6 | 22.2 | 0
1306 | 2022-10-09 21:47 | 15.5 | 23 | 0
1307 | 2022-10-09 21:48 | 15.4 | 22.3 | 0
1308 | 2022-10-09 21:49 | 15.4 | 21.7 | 0
1309 | 2022-10-09 21:50 | 15.3 | 22.4 | 0
1310 | 2022-10-09 21:51 | 15.3 | 22.2 | 0
1311 | 2022-10-09 21:52 | 15.2 | 22.1 | 0
1312 | 2022-10-09 21:53 | 15.2 | 22 | 0
1313 | 2022-10-09 21:54 | 15.1 | 21.9 | 0
1314 | 2022-10-09 21:55 | 15 | 21.9 | 0
1315 | 2022-10-09 21:56 | 15.1 | 22.1 | 0
1316 | 2022-10-09 21:57 | 15.2 | 22.2 | 0
1317 | 2022-10-09 21:58 | 15 | 22.2 | 0
1318 | 2022-10-09 21:59 | 15 | 21.8 | 0
1319 | 2022-10-09 22:00 | 14.9 | 21.8 | 0
1320 | 2022-10-09 22:01 | 14.9 | 21.9 | 0
1321 | 2022-10-09 22:02 | 14.9 | 22.2 | 0
1322 | 2022-10-09 22:03 | 14.8 | 22.1 | 0
1323 | 2022-10-09 22:04 | 14.8 | 22 | 0
1324 | 2022-10-09 22:05 | 14.9 | 21.9 | 0
1325 | 2022-10-09 22:06 | 15 | 22 | 0
1326 | 2022-10-09 22:07 | 15 | 22.2 | 0
1327 | 2022-10-09 22:08 | 14.9 | 22.1 | 0
1328 | 2022-10-09 22:09 | 14.8 | 21.4 | 0
1329 | 2022-10-09 22:10 | 14.8 | 21.9 | 0
1330 | 2022-10-09 22:11 | 14.7 | 22.1 | 0
1331 | 2022-10-09 22:12 | 14.7 | 22.3 | 0
1332 | 2022-10-09 22:13 | 14.8 | 21.8 | 0
1333 | 2022-10-09 22:14 | 14.6 | 22.3 | 0
1334 | 2022-10-09 22:15 | 14.7 | 22.2 | 0
1335 | 2022-10-09 22:16 | 14.6 | 21.4 | 0
1336 | 2022-10-09 22:17 | 14.7 | 22.3 | 0
1337 | 2022-10-09 22:18 | 14.8 | 22.1 | 0
1338 | 2022-10-09 22:19 | 14.6 | 22.6 | 0
1339 | 2022-10-09 22:20 | 14.6 | 22.7 | 0
1340 | 2022-10-09 22:21 | 14.6 | 23 | 0
1341 | 2022-10-09 22:22 | 14.5 | 21.8 | 0
1342 | 2022-10-09 22:23 | 14.6 | 22 | 0
1343 | 2022-10-09 22:24 | 14.6 | 22.1 | 0
1344 | 2022-10-09 22:25 | 14.5 | 22 | 0
1345 | 2022-10-09 22:26 | 14.6 | 22 | 0
1346 | 2022-10-09 22:27 | 14.6 | 21.7 | 0
1347 | 2022-10-09 22:28 | 14.5 | 22.2 | 0
1348 | 2022-10-09 22:29 | 14.5 | 22.2 | 0
1349 | 2022-10-09 22:30 | 14.6 | 21.8 | 0
1350 | 2022-10-09 22:31 | 14.5 | 21.8 | 0
1351 | 2022-10-09 22:32 | 14.6 | 21.9 | 0
1352 | 2022-10-09 22:33 | 14.5 | 21.9 | 0
1353 | 2022-10-09 22:34 | 14.7 | 22.1 | 0
1354 | 2022-10-09 22:35 | 14.3 | 22.3 | 0
1355 | 2022-10-09 22:36 | 14.5 | 22.1 | 0
1356 | 2022-10-09 22:37 | 14.4 | 22.1 | 0
1357 | 2022-10-09 22:38 | 14.3 | 22.1 | 0
1358 | 2022-10-09 22:39 | 14.5 | 22 | 0
1359 | 2022-10-09 22:40 | 14.4 | 22.1 | 0
1360 | 2022-10-09 22:41 | 14.3 | 22 | 0
1361 | 2022-10-09 22:42 | 14.3 | 21.9 | 0
1362 | 2022-10-09 22:43 | 14.4 | 21.9 | 0
1363 | 2022-10-09 22:44 | 14.2 | 22.1 | 0
1364 | 2022-10-09 22:45 | 14.1 | 22 | 0
1365 | 2022-10-09 22:46 | 14.2 | 21.9 | 0
1366 | 2022-10-09 22:47 | 14.2 | 21.9 | 0
1367 | 2022-10-09 22:48 | 14.1 | 22 | 0
1368 | 2022-10-09 22:49 | 14.3 | 22.1 | 0
1369 | 2022-10-09 22:50 | 14.2 | 21.9 | 0
1370 | 2022-10-09 22:51 | 14.2 | 22.1 | 0
1371 | 2022-10-09 22:52 | 14.1 | 22 | 0
1372 | 2022-10-09 22:53 | 14.2 | 22.1 | 0
1373 | 2022-10-09 22:54 | 14.1 | 22 | 0
1374 | 2022-10-09 22:55 | 14 | 22 | 0
1375 | 2022-10-09 22:56 | 14 | 21.9 | 0
1376 | 2022-10-09 22:57 | 14 | 22 | 0
1377 | 2022-10-09 22:58 | 14 | 22.1 | 0
1378 | 2022-10-09 22:59 | 14.1 | 22.1 | 0
1379 | 2022-10-09 23:00 | 14.1 | 22 | 0
1380 | 2022-10-09 23:01 | 14.2 | 21.8 | 0
1381 | 2022-10-09 23:02 | 14.1 | 21.6 | 0
1382 | 2022-10-09 23:03 | 14.1 | 22.4 | 0
1383 | 2022-10-09 23:04 | 14.2 | 21.8 | 0
1384 | 2022-10-09 23:05 | 14 | 21.9 | 0
1385 | 2022-10-09 23:06 | 14 | 22.1 | 0
1386 | 2022-10-09 23:07 | 13.9 | 22.4 | 0
1387 | 2022-10-09 23:08 | 14.1 | 22.5 | 0
1388 | 2022-10-09 23:09 | 14.2 | 22 | 0
1389 | 2022-10-09 23:10 | 14 | 21.8 | 0
1390 | 2022-10-09 23:11 | 14 | 22.1 | 0
1391 | 2022-10-09 23:12 | 14 | 22.3 | 0
1392 | 2022-10-09 23:13 | 14 | 21.9 | 0
1393 | 2022-10-09 23:14 | 14.1 | 22.3 | 0
1394 | 2022-10-09 23:15 | 14 | 22 | 0
1395 | 2022-10-09 23:16 | 14 | 22 | 0
1396 | 2022-10-09 23:17 | 13.9 | 22 | 0
1397 | 2022-10-09 23:18 | 13.9 | 22.1 | 0
1398 | 2022-10-09 23:19 | 13.9 | 21.8 | 0
1399 | 2022-10-09 23:20 | 13.9 | 21.9 | 0
1400 | 2022-10-09 23:21 | 14 | 21.8 | 0
1401 | 2022-10-09 23:22 | 14 | 22 | 0
1402 | 2022-10-09 23:23 | 14 | 22.2 | 0
1403 | 2022-10-09 23:24 | 13.9 | 21.9 | 0
1404 | 2022-10-09 23:25 | 14 | 22 | 0
1405 | 2022-10-09 23:26 | 14 | 21.8 | 0
1406 | 2022-10-09 23:27 | 14 | 22 | 0
1407 | 2022-10-09 23:28 | 13.9 | 21.9 | 0
1408 | 2022-10-09 23:29 | 13.9 | 22 | 0
1409 | 2022-10-09 23:30 | 13.9 | 21.8 | 0
1410 | 2022-10-09 23:31 | 14.1 | 22.6 | 0
1411 | 2022-10-09 23:32 | 14.1 | 21.4 | 0
1412 | 2022-10-09 23:33 | 14.3 | 21.9 | 0
1413 | 2022-10-09 23:34 | 14.2 | 22 | 0
1414 | 2022-10-09 23:35 | 14.2 | 22.4 | 0
1415 | 2022-10-09 23:36 | 14.1 | 22.8 | 0
1416 | 2022-10-09 23:37 | 14.1 | 21.7 | 0
1417 | 2022-10-09 23:38 | 14 | 22.1 | 0
1418 | 2022-10-09 23:39 | 13.9 | 21.8 | 0
1419 | 2022-10-09 23:40 | 13.9 | 22 | 0
1420 | 2022-10-09 23:41 | 13.9 | 22.2 | 0
1421 | 2022-10-09 23:42 | 13.9 | 21.4 | 0
1422 | 2022-10-09 23:43 | 13.7 | 22.3 | 0
1423 | 2022-10-09 23:44 | 13.8 | 21.9 | 0
1424 | 2022-10-09 23:45 | 14 | 21.7 | 0
1425 | 2022-10-09 23:46 | 13.9 | 21.5 | 0
1426 | 2022-10-09 23:47 | 13.8 | 21.4 | 0
1427 | 2022-10-09 23:48 | 14 | 21.8 | 0
1428 | 2022-10-09 23:49 | 13.8 | 22.2 | 0
1429 | 2022-10-09 23:50 | 14 | 22.1 | 0
1430 | 2022-10-09 23:51 | 13.7 | 22.2 | 0
1431 | 2022-10-09 23:52 | 13.9 | 21.8 | 0
1432 | 2022-10-09 23:53 | 13.8 | 22.1 | 0
1433 | 2022-10-09 23:54 | 13.9 | 21.9 | 0
1434 | 2022-10-09 23:55 | 13.8 | 22.1 | 0
1435 | 2022-10-09 23:56 | 13.9 | 22 | 0
1436 | 2022-10-09 23:57 | 13.9 | 22 | 0
1437 | 2022-10-09 23:58 | 14 | 21.8 | 0
1438 | 2022-10-09 23:59 | 13.8 | 22.4 | 0

## 21-12-2022_WITH HEAT
| Date&time_x | OUTDOOR_TEMP | INDOOR_TEMP | SH_INLET | SH_RETURN | FLOW_FAN_COILS_INDOOR | PYRANOMETER
0 | 2022-12-21 | 7.3 | 18.9 | 16.3 | 12.3 | 0 | 0
1 | 2022-12-21 00:01 | 7.3 | 18.9 | 16.2 | 12.3 | 0 | 0
2 | 2022-12-21 00:02 | 7.3 | 18.9 | 16.2 | 12.3 | 0 | 0
3 | 2022-12-21 00:03 | 7.4 | 18.9 | 16.2 | 12.2 | 0 | 0
4 | 2022-12-21 00:04 | 7.3 | 18.9 | 16.2 | 12.2 | 0 | 0
5 | 2022-12-21 00:05 | 7.3 | 18.9 | 16.1 | 12.2 | 0 | 0
6 | 2022-12-21 00:06 | 7.3 | 19 | 16.1 | 12.2 | 0 | 0
7 | 2022-12-21 00:07 | 7.5 | 19 | 16.1 | 12.2 | 0 | 0
8 | 2022-12-21 00:08 | 7.5 | 18.9 | 16.1 | 12.1 | 0 | 0
9 | 2022-12-21 00:09 | 7.3 | 18.9 | 16.1 | 12.1 | 0 | 0
10 | 2022-12-21 00:10 | 7.5 | 18.9 | 16 | 12.1 | 0 | 0
11 | 2022-12-21 00:11 | 7.3 | 18.9 | 16 | 12.1 | 0 | 0
12 | 2022-12-21 00:12 | 7.3 | 18.9 | 16 | 12 | 0 | 0
13 | 2022-12-21 00:13 | 7.3 | 18.9 | 15.9 | 12 | 0 | 0
14 | 2022-12-21 00:14 | 7.5 | 18.9 | 15.9 | 12 | 0 | 0
15 | 2022-12-21 00:15 | 7.4 | 18.9 | 15.9 | 12 | 0 | 0
16 | 2022-12-21 00:16 | 7.4 | 18.9 | 15.9 | 11.9 | 0 | 0
17 | 2022-12-21 00:17 | 7.5 | 18.8 | 15.8 | 11.9 | 0 | 0
18 | 2022-12-21 00:18 | 7.4 | 18.9 | 15.8 | 11.9 | 0 | 0
19 | 2022-12-21 00:19 | 7.5 | 18.9 | 15.8 | 11.9 | 0 | 0
20 | 2022-12-21 00:20 | 7.4 | 18.8 | 15.8 | 11.9 | 0 | 0
21 | 2022-12-21 00:21 | 7.4 | 18.9 | 15.7 | 11.8 | 0 | 0
22 | 2022-12-21 00:22 | 7.4 | 18.9 | 15.7 | 11.8 | 0 | 0
23 | 2022-12-21 00:23 | 7.4 | 18.9 | 15.7 | 11.8 | 0 | 0
24 | 2022-12-21 00:24 | 7.4 | 18.8 | 15.7 | 11.8 | 0 | 0
25 | 2022-12-21 00:25 | 7.3 | 18.9 | 15.7 | 11.7 | 0 | 0
26 | 2022-12-21 00:26 | 7.4 | 18.8 | 15.7 | 11.7 | 0 | 0
27 | 2022-12-21 00:27 | 7.4 | 18.8 | 15.7 | 11.7 | 0 | 0
28 | 2022-12-21 00:28 | 7.4 | 18.8 | 15.7 | 11.7 | 0 | 0
29 | 2022-12-21 00:29 | 7.5 | 18.9 | 15.7 | 11.7 | 0 | 0
30 | 2022-12-21 00:30 | 7.5 | 18.8 | 15.6 | 11.6 | 0 | 0
31 | 2022-12-21 00:31 | 7.5 | 18.8 | 15.6 | 11.6 | 0 | 0
32 | 2022-12-21 00:32 | 7.6 | 18.8 | 15.6 | 11.6 | 0 | 0
33 | 2022-12-21 00:33 | 7.3 | 18.8 | 15.5 | 11.6 | 0 | 0
34 | 2022-12-21 00:34 | 7.4 | 18.8 | 15.5 | 11.6 | 0 | 0
35 | 2022-12-21 00:35 | 7.5 | 18.7 | 15.5 | 11.5 | 0 | 0
36 | 2022-12-21 00:36 | 7.4 | 18.8 | 15.4 | 11.5 | 0 | 0
37 | 2022-12-21 00:37 | 7.3 | 18.8 | 15.4 | 11.5 | 0 | 0
38 | 2022-12-21 00:38 | 7.4 | 18.8 | 15.4 | 11.5 | 0 | 0
39 | 2022-12-21 00:39 | 7.3 | 18.8 | 15.4 | 11.5 | 0 | 0
40 | 2022-12-21 00:40 | 7.3 | 18.8 | 15.3 | 11.5 | 0 | 0
41 | 2022-12-21 00:41 | 7.4 | 18.8 | 15.3 | 11.5 | 0 | 0
42 | 2022-12-21 00:42 | 7.3 | 18.7 | 15.3 | 11.5 | 0 | 0
43 | 2022-12-21 00:43 | 7.3 | 18.7 | 15.3 | 11.4 | 0 | 0
44 | 2022-12-21 00:44 | 7.3 | 18.7 | 15.3 | 11.4 | 0 | 0
45 | 2022-12-21 00:45 | 7.5 | 18.8 | 15.2 | 11.4 | 0 | 0
46 | 2022-12-21 00:46 | 7.2 | 18.7 | 15.2 | 11.4 | 0 | 0
47 | 2022-12-21 00:47 | 7.3 | 18.8 | 15.2 | 11.4 | 0 | 0
48 | 2022-12-21 00:48 | 7.3 | 18.7 | 15.2 | 11.4 | 0 | 0
49 | 2022-12-21 00:49 | 7.3 | 18.7 | 15.2 | 11.4 | 0 | 0
50 | 2022-12-21 00:50 | 7.4 | 18.8 | 15.2 | 11.4 | 0 | 0
51 | 2022-12-21 00:51 | 7.5 | 18.7 | 15.1 | 11.3 | 0 | 0
52 | 2022-12-21 00:52 | 7.3 | 18.7 | 15.1 | 11.3 | 0 | 0
53 | 2022-12-21 00:53 | 7.4 | 18.7 | 15.1 | 11.3 | 0 | 0
54 | 2022-12-21 00:54 | 7.4 | 18.7 | 15.1 | 11.3 | 0 | 0
55 | 2022-12-21 00:55 | 7.5 | 18.7 | 15.1 | 11.3 | 0 | 0
56 | 2022-12-21 00:56 | 7.5 | 18.7 | 15.1 | 11.3 | 0 | 0
57 | 2022-12-21 00:57 | 7.5 | 18.7 | 15.1 | 11.3 | 0 | 0
58 | 2022-12-21 00:58 | 7.5 | 18.8 | 15.1 | 11.3 | 0 | 0
59 | 2022-12-21 00:59 | 7.3 | 18.7 | 15.1 | 11.2 | 0 | 0
60 | 2022-12-21 01:00 | 7.5 | 18.7 | 15 | 11.2 | 0 | 0
61 | 2022-12-21 01:01 | 7.5 | 18.7 | 15 | 11.2 | 0 | 0
62 | 2022-12-21 01:02 | 7.4 | 18.7 | 15 | 11.2 | 0 | 0
63 | 2022-12-21 01:03 | 7.4 | 18.6 | 15 | 11.2 | 0 | 0
64 | 2022-12-21 01:04 | 7.4 | 18.6 | 15 | 11.9 | 0 | 0
65 | 2022-12-21 01:05 | 7.5 | 18.7 | 14.9 | 12 | 0 | 0
66 | 2022-12-21 01:06 | 7.4 | 18.6 | 15 | 11.9 | 0 | 0
67 | 2022-12-21 01:07 | 7.5 | 18.7 | 38 | 17.4 | 0.365 | 0
68 | 2022-12-21 01:08 | 7.5 | 18.6 | 39.8 | 32.3 | 0.408 | 0
69 | 2022-12-21 01:09 | 7.5 | 18.6 | 39.2 | 36.4 | 0.922 | 0
70 | 2022-12-21 01:10 | 7.5 | 18.7 | 37.7 | 37.2 | 0.948 | 0
71 | 2022-12-21 01:11 | 7.5 | 18.6 | 37.3 | 36.6 | 0.943 | 0
72 | 2022-12-21 01:12 | 7.5 | 18.6 | 37.3 | 36.5 | 0.934 | 0
73 | 2022-12-21 01:13 | 7.4 | 18.6 | 37.8 | 36.6 | 0.952 | 0
74 | 2022-12-21 01:14 | 7.4 | 18.6 | 38.1 | 37.1 | 0.968 | 0
75 | 2022-12-21 01:15 | 7.5 | 18.7 | 38.1 | 37.3 | 0.975 | 0
76 | 2022-12-21 01:16 | 7.4 | 18.7 | 37.9 | 37.2 | 0.98 | 0
77 | 2022-12-21 01:17 | 7.6 | 18.7 | 37.8 | 37.1 | 0.976 | 0
78 | 2022-12-21 01:18 | 7.6 | 18.7 | 37.8 | 37 | 0.979 | 0
79 | 2022-12-21 01:19 | 7.7 | 18.7 | 37.9 | 37.1 | 0.98 | 0
80 | 2022-12-21 01:20 | 7.5 | 18.8 | 37.8 | 37.1 | 0.978 | 0
81 | 2022-12-21 01:21 | 7.5 | 18.7 | 37.8 | 37.1 | 0.976 | 0
82 | 2022-12-21 01:22 | 7.7 | 18.7 | 37.8 | 37.1 | 0.98 | 0
83 | 2022-12-21 01:23 | 7.5 | 18.8 | 37.8 | 37.1 | 0.98 | 0
84 | 2022-12-21 01:24 | 7.7 | 18.7 | 37.8 | 37.1 | 0.976 | 0
85 | 2022-12-21 01:25 | 7.5 | 18.8 | 37.8 | 37.1 | 0.975 | 0
86 | 2022-12-21 01:26 | 7.5 | 18.7 | 37.8 | 37.1 | 0.98 | 0
87 | 2022-12-21 01:27 | 7.6 | 18.8 | 37.8 | 37 | 0.976 | 0
88 | 2022-12-21 01:28 | 7.6 | 18.8 | 37.7 | 37 | 0.974 | 0
89 | 2022-12-21 01:29 | 7.5 | 18.7 | 37.7 | 37 | 0.977 | 0
90 | 2022-12-21 01:30 | 7.5 | 18.7 | 37.7 | 37 | 0.975 | 0
91 | 2022-12-21 01:31 | 7.6 | 18.7 | 37.7 | 37 | 0.977 | 0
92 | 2022-12-21 01:32 | 7.7 | 18.7 | 37.7 | 36.9 | 0.975 | 0
93 | 2022-12-21 01:33 | 7.8 | 18.7 | 37.6 | 36.9 | 0.979 | 0
94 | 2022-12-21 01:34 | 7.7 | 18.7 | 37.6 | 36.9 | 0.974 | 0
95 | 2022-12-21 01:35 | 7.8 | 18.7 | 37.6 | 36.9 | 0.972 | 0
96 | 2022-12-21 01:36 | 7.6 | 18.8 | 37.6 | 36.9 | 0.976 | 0
97 | 2022-12-21 01:37 | 7.7 | 18.7 | 37.6 | 36.8 | 0.974 | 0
98 | 2022-12-21 01:38 | 7.7 | 18.7 | 37.6 | 36.8 | 0.979 | 0
99 | 2022-12-21 01:39 | 7.7 | 18.8 | 37.5 | 36.8 | 0.975 | 0
100 | 2022-12-21 01:40 | 7.6 | 18.7 | 37.5 | 36.8 | 0.975 | 0
101 | 2022-12-21 01:41 | 7.8 | 18.7 | 37.5 | 36.7 | 0.974 | 0
102 | 2022-12-21 01:42 | 7.6 | 18.7 | 37.5 | 36.8 | 0.973 | 0
103 | 2022-12-21 01:43 | 7.6 | 18.7 | 37.4 | 36.7 | 0.972 | 0
104 | 2022-12-21 01:44 | 7.7 | 18.7 | 37.4 | 36.7 | 0.979 | 0
105 | 2022-12-21 01:45 | 7.6 | 18.7 | 37.4 | 36.7 | 0.978 | 0
106 | 2022-12-21 01:46 | 7.6 | 18.7 | 37.4 | 36.7 | 0.975 | 0
107 | 2022-12-21 01:47 | 7.8 | 18.7 | 37.4 | 36.6 | 0.978 | 0
108 | 2022-12-21 01:48 | 7.6 | 18.7 | 37.4 | 36.6 | 0.975 | 0
109 | 2022-12-21 01:49 | 7.6 | 18.7 | 37.3 | 36.6 | 0.973 | 0
110 | 2022-12-21 01:50 | 7.7 | 18.8 | 37.3 | 36.6 | 0.971 | 0
111 | 2022-12-21 01:51 | 7.7 | 18.8 | 37.2 | 36.6 | 0.974 | 0
112 | 2022-12-21 01:52 | 7.7 | 18.8 | 37.2 | 36.5 | 0.974 | 0
113 | 2022-12-21 01:53 | 7.7 | 18.7 | 37.2 | 36.5 | 0.974 | 0
114 | 2022-12-21 01:54 | 7.9 | 18.7 | 37.1 | 36.5 | 0.97 | 0
115 | 2022-12-21 01:55 | 7.7 | 18.7 | 37.2 | 36.4 | 0.974 | 0
116 | 2022-12-21 01:56 | 7.8 | 18.7 | 37.4 | 36.5 | 0.973 | 0
117 | 2022-12-21 01:57 | 7.8 | 18.7 | 37.8 | 36.7 | 0.976 | 0
118 | 2022-12-21 01:58 | 7.8 | 18.7 | 37.6 | 37.1 | 0.974 | 0
119 | 2022-12-21 01:59 | 7.8 | 18.7 | 37.5 | 36.8 | 0.974 | 0
120 | 2022-12-21 02:00 | 7.8 | 18.7 | 37.5 | 36.8 | 0.976 | 0
121 | 2022-12-21 02:01 | 7.8 | 18.7 | 37.5 | 36.8 | 0.97 | 0
122 | 2022-12-21 02:02 | 7.7 | 18.7 | 37.4 | 36.8 | 0.973 | 0
123 | 2022-12-21 02:03 | 7.8 | 18.7 | 37.3 | 36.6 | 0.975 | 0
124 | 2022-12-21 02:04 | 7.6 | 18.6 | 37.5 | 36.6 | 0.975 | 0
125 | 2022-12-21 02:05 | 7.6 | 18.7 | 37.9 | 36.9 | 0.977 | 0
126 | 2022-12-21 02:06 | 7.6 | 18.7 | 38.3 | 37.3 | 0.975 | 0
127 | 2022-12-21 02:07 | 7.7 | 18.6 | 38.9 | 37.9 | 0.973 | 0
128 | 2022-12-21 02:08 | 7.7 | 18.6 | 38.4 | 37.8 | 0.977 | 0
129 | 2022-12-21 02:09 | 7.6 | 18.6 | 38.2 | 37.6 | 0.975 | 0
130 | 2022-12-21 02:10 | 7.6 | 18.7 | 38.4 | 37.6 | 0.974 | 0
131 | 2022-12-21 02:11 | 7.6 | 18.7 | 38.4 | 37.6 | 0.977 | 0
132 | 2022-12-21 02:12 | 7.7 | 18.7 | 38.5 | 37.6 | 0.974 | 0
133 | 2022-12-21 02:13 | 7.7 | 18.7 | 38.4 | 37.7 | 0.974 | 0
134 | 2022-12-21 02:14 | 7.6 | 18.7 | 38.4 | 37.7 | 0.973 | 0
135 | 2022-12-21 02:15 | 7.6 | 18.7 | 38.4 | 37.6 | 0.975 | 0
136 | 2022-12-21 02:16 | 7.7 | 18.7 | 38.4 | 37.6 | 0.974 | 0
137 | 2022-12-21 02:17 | 7.6 | 18.7 | 38.3 | 37.6 | 0.971 | 0
138 | 2022-12-21 02:18 | 7.7 | 18.7 | 38.3 | 37.6 | 0.972 | 0
139 | 2022-12-21 02:19 | 7.6 | 18.6 | 38.3 | 37.6 | 0.977 | 0
140 | 2022-12-21 02:20 | 7.8 | 18.6 | 38.2 | 37.5 | 0.974 | 0
141 | 2022-12-21 02:21 | 7.7 | 18.7 | 38.2 | 37.5 | 0.975 | 0
142 | 2022-12-21 02:22 | 7.8 | 18.7 | 38.2 | 37.5 | 0.973 | 0
143 | 2022-12-21 02:23 | 7.6 | 18.6 | 38.2 | 37.5 | 0.976 | 0
144 | 2022-12-21 02:24 | 7.7 | 18.6 | 38.1 | 37.4 | 0.977 | 0
145 | 2022-12-21 02:25 | 7.8 | 18.6 | 38.1 | 37.4 | 0.979 | 0
146 | 2022-12-21 02:26 | 7.7 | 18.6 | 38.1 | 37.3 | 0.97 | 0
147 | 2022-12-21 02:27 | 7.6 | 18.6 | 38 | 37.3 | 0.974 | 0
148 | 2022-12-21 02:28 | 7.8 | 18.6 | 38 | 37.3 | 0.976 | 0
149 | 2022-12-21 02:29 | 7.8 | 18.6 | 37.9 | 37.2 | 0.977 | 0
150 | 2022-12-21 02:30 | 7.8 | 18.6 | 37.9 | 37.2 | 0.975 | 0
151 | 2022-12-21 02:31 | 7.6 | 18.7 | 37.9 | 37.2 | 0.966 | 0
152 | 2022-12-21 02:32 | 7.6 | 18.6 | 37.8 | 37.1 | 0.976 | 0
153 | 2022-12-21 02:33 | 7.7 | 18.5 | 37.7 | 37 | 0.971 | 0
154 | 2022-12-21 02:34 | 7.9 | 18.5 | 37.9 | 37 | 0.973 | 0
155 | 2022-12-21 02:35 | 7.9 | 18.6 | 38.3 | 37.2 | 0.974 | 0
156 | 2022-12-21 02:36 | 7.8 | 18.7 | 38.8 | 37.7 | 0.978 | 0
157 | 2022-12-21 02:37 | 7.6 | 18.6 | 39.3 | 38.3 | 0.976 | 0
158 | 2022-12-21 02:38 | 7.7 | 18.6 | 38.7 | 38.2 | 0.975 | 0
159 | 2022-12-21 02:39 | 7.8 | 18.6 | 38.6 | 38 | 0.978 | 0
160 | 2022-12-21 02:40 | 7.8 | 18.6 | 38.7 | 37.9 | 0.976 | 0
161 | 2022-12-21 02:41 | 7.8 | 18.6 | 38.5 | 37.9 | 0.977 | 0
162 | 2022-12-21 02:42 | 7.8 | 18.6 | 38.6 | 37.8 | 0.978 | 0
163 | 2022-12-21 02:43 | 7.6 | 18.6 | 38.6 | 37.9 | 0.975 | 0
164 | 2022-12-21 02:44 | 7.7 | 18.6 | 38.5 | 37.8 | 0.974 | 0
165 | 2022-12-21 02:45 | 7.8 | 18.6 | 38.6 | 37.8 | 0.975 | 0
166 | 2022-12-21 02:46 | 7.7 | 18.7 | 38.6 | 37.9 | 0.974 | 0
167 | 2022-12-21 02:47 | 7.8 | 18.6 | 38.5 | 37.8 | 0.977 | 0
168 | 2022-12-21 02:48 | 7.8 | 18.6 | 38.4 | 37.8 | 0.978 | 0
169 | 2022-12-21 02:49 | 7.8 | 18.6 | 38.4 | 37.6 | 0.974 | 0
170 | 2022-12-21 02:50 | 7.9 | 18.6 | 38.4 | 37.6 | 0.974 | 0
171 | 2022-12-21 02:51 | 7.9 | 18.6 | 38.3 | 37.6 | 0.976 | 0
172 | 2022-12-21 02:52 | 7.8 | 18.6 | 38.3 | 37.5 | 0.977 | 0
173 | 2022-12-21 02:53 | 7.8 | 18.6 | 38.3 | 37.5 | 0.973 | 0
174 | 2022-12-21 02:54 | 7.7 | 18.6 | 38.3 | 37.5 | 0.976 | 0
175 | 2022-12-21 02:55 | 7.8 | 18.6 | 38.2 | 37.5 | 0.975 | 0
176 | 2022-12-21 02:56 | 7.8 | 18.6 | 38.1 | 37.4 | 0.974 | 0
177 | 2022-12-21 02:57 | 7.8 | 18.6 | 38 | 37.4 | 0.975 | 0
178 | 2022-12-21 02:58 | 7.9 | 18.6 | 38 | 37.3 | 0.974 | 0
179 | 2022-12-21 02:59 | 7.9 | 18.6 | 38.1 | 37.3 | 0.976 | 0
180 | 2022-12-21 03:00 | 7.9 | 18.6 | 38 | 37.3 | 0.971 | 0
181 | 2022-12-21 03:01 | 7.8 | 18.5 | 38 | 37.3 | 0.974 | 0
182 | 2022-12-21 03:02 | 7.8 | 18.5 | 37.9 | 37.2 | 0.973 | 0
183 | 2022-12-21 03:03 | 7.9 | 18.5 | 37.8 | 37.1 | 0.975 | 0
184 | 2022-12-21 03:04 | 7.8 | 18.6 | 38 | 37.2 | 0.976 | 0
185 | 2022-12-21 03:05 | 7.8 | 18.5 | 38.4 | 37.4 | 0.969 | 0
186 | 2022-12-21 03:06 | 7.9 | 18.5 | 38.9 | 37.9 | 0.976 | 0
187 | 2022-12-21 03:07 | 7.9 | 18.6 | 39.5 | 38.3 | 0.976 | 0
188 | 2022-12-21 03:08 | 8 | 18.6 | 38.9 | 38.7 | 0.978 | 0
189 | 2022-12-21 03:09 | 7.8 | 18.6 | 38.9 | 38.1 | 0.977 | 0
190 | 2022-12-21 03:10 | 7.8 | 18.5 | 39 | 38.1 | 0.976 | 0
191 | 2022-12-21 03:11 | 7.9 | 18.6 | 38.9 | 38.2 | 0.978 | 0
192 | 2022-12-21 03:12 | 7.8 | 18.5 | 38.9 | 38.2 | 0.977 | 0
193 | 2022-12-21 03:13 | 7.7 | 18.6 | 38.9 | 38.2 | 0.975 | 0
194 | 2022-12-21 03:14 | 7.8 | 18.6 | 38.6 | 38.1 | 0.974 | 0
195 | 2022-12-21 03:15 | 7.8 | 18.5 | 38.7 | 37.8 | 0.976 | 0
196 | 2022-12-21 03:16 | 7.8 | 18.5 | 38.7 | 37.9 | 0.978 | 0
197 | 2022-12-21 03:17 | 7.8 | 18.5 | 38.7 | 38 | 0.977 | 0
198 | 2022-12-21 03:18 | 8 | 18.6 | 38.7 | 38 | 0.974 | 0
199 | 2022-12-21 03:19 | 7.8 | 18.5 | 38.7 | 38 | 0.979 | 0
200 | 2022-12-21 03:20 | 7.8 | 18.5 | 38.6 | 37.9 | 0.977 | 0
201 | 2022-12-21 03:21 | 7.9 | 18.5 | 38.6 | 37.9 | 0.974 | 0
202 | 2022-12-21 03:22 | 8 | 18.5 | 38.5 | 37.8 | 0.975 | 0
203 | 2022-12-21 03:23 | 8 | 18.6 | 38.6 | 37.8 | 0.978 | 0
204 | 2022-12-21 03:24 | 8 | 18.6 | 38.4 | 37.8 | 0.979 | 0
205 | 2022-12-21 03:25 | 7.8 | 18.5 | 38.4 | 37.7 | 0.977 | 0
206 | 2022-12-21 03:26 | 7.8 | 18.5 | 38.3 | 37.6 | 0.971 | 0
207 | 2022-12-21 03:27 | 7.8 | 18.5 | 38.3 | 37.6 | 0.977 | 0
208 | 2022-12-21 03:28 | 7.9 | 18.5 | 38.3 | 37.6 | 0.976 | 0
209 | 2022-12-21 03:29 | 8 | 18.5 | 38.3 | 37.6 | 0.973 | 0
210 | 2022-12-21 03:30 | 7.8 | 18.5 | 38.3 | 37.5 | 0.977 | 0
211 | 2022-12-21 03:31 | 7.8 | 18.5 | 38.1 | 37.5 | 0.974 | 0
212 | 2022-12-21 03:32 | 7.8 | 18.5 | 38.1 | 37.4 | 0.979 | 0
213 | 2022-12-21 03:33 | 7.9 | 18.5 | 38.1 | 37.4 | 0.974 | 0
214 | 2022-12-21 03:34 | 7.9 | 18.4 | 38.1 | 37.4 | 0.977 | 0
215 | 2022-12-21 03:35 | 7.9 | 18.4 | 38.1 | 37.3 | 0.978 | 0
216 | 2022-12-21 03:36 | 7.9 | 18.5 | 38 | 37.3 | 0.977 | 0
217 | 2022-12-21 03:37 | 7.8 | 18.5 | 38 | 37.3 | 0.978 | 0
218 | 2022-12-21 03:38 | 7.8 | 18.6 | 37.9 | 37.2 | 0.981 | 0
219 | 2022-12-21 03:39 | 7.7 | 18.6 | 37.8 | 37.1 | 0.976 | 0
220 | 2022-12-21 03:40 | 7.7 | 18.5 | 37.7 | 37.1 | 0.973 | 0
221 | 2022-12-21 03:41 | 7.9 | 18.4 | 37.7 | 37 | 0.98 | 0
222 | 2022-12-21 03:42 | 7.8 | 18.5 | 37.6 | 36.9 | 0.977 | 0
223 | 2022-12-21 03:43 | 7.7 | 18.5 | 37.6 | 36.9 | 0.974 | 0
224 | 2022-12-21 03:44 | 7.6 | 18.5 | 37.6 | 36.9 | 0.975 | 0
225 | 2022-12-21 03:45 | 7.7 | 18.5 | 37.5 | 36.9 | 0.978 | 0
226 | 2022-12-21 03:46 | 7.6 | 18.5 | 37.5 | 36.8 | 0.973 | 0
227 | 2022-12-21 03:47 | 7.6 | 18.5 | 37.4 | 36.8 | 0.973 | 0
228 | 2022-12-21 03:48 | 7.6 | 18.5 | 37.3 | 36.6 | 0.975 | 0
229 | 2022-12-21 03:49 | 7.6 | 18.4 | 37.4 | 36.6 | 0.975 | 0
230 | 2022-12-21 03:50 | 7.6 | 18.5 | 37.4 | 36.7 | 0.97 | 0
231 | 2022-12-21 03:51 | 7.7 | 18.5 | 37.3 | 36.7 | 0.974 | 0
232 | 2022-12-21 03:52 | 7.7 | 18.4 | 37.3 | 36.6 | 0.974 | 0
233 | 2022-12-21 03:53 | 7.6 | 18.4 | 37.2 | 36.6 | 0.978 | 0
234 | 2022-12-21 03:54 | 7.6 | 18.5 | 37.2 | 36.5 | 0.974 | 0
235 | 2022-12-21 03:55 | 7.5 | 18.5 | 37.2 | 36.5 | 0.977 | 0
236 | 2022-12-21 03:56 | 7.6 | 18.4 | 37.1 | 36.5 | 0.972 | 0
237 | 2022-12-21 03:57 | 7.5 | 18.5 | 37.1 | 36.3 | 0.972 | 0
238 | 2022-12-21 03:58 | 7.6 | 18.5 | 37.2 | 36.4 | 0.977 | 0
239 | 2022-12-21 03:59 | 7.4 | 18.5 | 37.8 | 36.6 | 0.977 | 0
240 | 2022-12-21 04:00 | 7.4 | 18.4 | 37.8 | 37.2 | 0.975 | 0
241 | 2022-12-21 04:01 | 7.6 | 18.5 | 37.5 | 37 | 0.974 | 0
242 | 2022-12-21 04:02 | 7.6 | 18.4 | 37.5 | 36.8 | 0.976 | 0
243 | 2022-12-21 04:03 | 7.4 | 18.4 | 37.4 | 36.7 | 0.975 | 0
244 | 2022-12-21 04:04 | 7.4 | 18.4 | 37.7 | 36.8 | 0.975 | 0
245 | 2022-12-21 04:05 | 7.6 | 18.5 | 38.2 | 37.1 | 0.974 | 0
246 | 2022-12-21 04:06 | 7.5 | 18.4 | 38.6 | 37.6 | 0.976 | 0
247 | 2022-12-21 04:07 | 7.5 | 18.4 | 39.2 | 37.9 | 0.98 | 0
248 | 2022-12-21 04:08 | 7.4 | 18.4 | 38.8 | 38.4 | 0.977 | 0
249 | 2022-12-21 04:09 | 7.4 | 18.4 | 38.7 | 38 | 0.977 | 0
250 | 2022-12-21 04:10 | 7.4 | 18.4 | 38.9 | 38.1 | 0.977 | 0
251 | 2022-12-21 04:11 | 7.4 | 18.4 | 38.8 | 38.1 | 0.979 | 0
252 | 2022-12-21 04:12 | 7.6 | 18.4 | 38.7 | 38 | 0.977 | 0
253 | 2022-12-21 04:13 | 7.5 | 18.4 | 38.7 | 38 | 0.978 | 0
254 | 2022-12-21 04:14 | 7.7 | 18.4 | 38.8 | 38 | 0.976 | 0
255 | 2022-12-21 04:15 | 7.6 | 18.4 | 38.7 | 38 | 0.975 | 0
256 | 2022-12-21 04:16 | 7.6 | 18.4 | 38.7 | 38 | 0.98 | 0
257 | 2022-12-21 04:17 | 7.7 | 18.4 | 38.7 | 37.9 | 0.977 | 0
258 | 2022-12-21 04:18 | 7.7 | 18.4 | 38.6 | 37.9 | 0.977 | 0
259 | 2022-12-21 04:19 | 7.5 | 18.4 | 38.6 | 37.9 | 0.978 | 0
260 | 2022-12-21 04:20 | 7.5 | 18.4 | 38.6 | 37.9 | 0.978 | 0
261 | 2022-12-21 04:21 | 7.6 | 18.4 | 38.5 | 37.8 | 0.98 | 0
262 | 2022-12-21 04:22 | 7.5 | 18.4 | 38.5 | 37.8 | 0.979 | 0
263 | 2022-12-21 04:23 | 7.5 | 18.4 | 38.5 | 37.7 | 0.976 | 0
264 | 2022-12-21 04:24 | 7.6 | 18.4 | 38.4 | 37.7 | 0.978 | 0
265 | 2022-12-21 04:25 | 7.8 | 18.5 | 38.4 | 37.7 | 0.978 | 0
266 | 2022-12-21 04:26 | 7.7 | 18.4 | 38.3 | 37.6 | 0.98 | 0
267 | 2022-12-21 04:27 | 7.7 | 18.4 | 38.2 | 37.5 | 0.974 | 0
268 | 2022-12-21 04:28 | 7.6 | 18.4 | 38.2 | 37.5 | 0.974 | 0
269 | 2022-12-21 04:29 | 7.6 | 18.4 | 38.2 | 37.5 | 0.98 | 0
270 | 2022-12-21 04:30 | 7.8 | 18.4 | 38.2 | 37.4 | 0.977 | 0
271 | 2022-12-21 04:31 | 7.8 | 18.5 | 38.1 | 37.4 | 0.974 | 0
272 | 2022-12-21 04:32 | 7.8 | 18.4 | 38 | 37.4 | 0.978 | 0
273 | 2022-12-21 04:33 | 7.6 | 18.3 | 38 | 37.3 | 0.977 | 0
274 | 2022-12-21 04:34 | 7.8 | 18.5 | 38.1 | 37.3 | 0.974 | 0
275 | 2022-12-21 04:35 | 7.6 | 18.3 | 38.4 | 37.5 | 0.972 | 0
276 | 2022-12-21 04:36 | 7.5 | 18.3 | 39 | 37.9 | 0.979 | 0
277 | 2022-12-21 04:37 | 7.8 | 18.3 | 39.5 | 38.4 | 0.979 | 0
278 | 2022-12-21 04:38 | 7.6 | 18.3 | 39.8 | 38.8 | 0.979 | 0
279 | 2022-12-21 04:39 | 7.8 | 18.4 | 40.3 | 39.1 | 0.984 | 0
280 | 2022-12-21 04:40 | 7.7 | 18.3 | 40.7 | 39.6 | 0.978 | 0
281 | 2022-12-21 04:41 | 7.8 | 18.4 | 41.1 | 39.9 | 0.979 | 0
282 | 2022-12-21 04:42 | 7.5 | 18.3 | 41.5 | 40.4 | 0.98 | 0
283 | 2022-12-21 04:43 | 7.7 | 18.4 | 41.9 | 40.7 | 0.977 | 0
284 | 2022-12-21 04:44 | 7.7 | 18.4 | 42.3 | 41.1 | 0.981 | 0
285 | 2022-12-21 04:45 | 7.7 | 18.4 | 42.7 | 41.6 | 0.979 | 0
286 | 2022-12-21 04:46 | 7.5 | 18.3 | 43.2 | 42 | 0.981 | 0
287 | 2022-12-21 04:47 | 7.6 | 18.4 | 43.6 | 42.4 | 0.982 | 0
288 | 2022-12-21 04:48 | 7.7 | 18.3 | 44 | 42.7 | 0.986 | 0
289 | 2022-12-21 04:49 | 7.5 | 18.3 | 44.4 | 43.2 | 0.986 | 0
290 | 2022-12-21 04:50 | 7.5 | 18.3 | 44.9 | 43.6 | 0.981 | 0
291 | 2022-12-21 04:51 | 7.5 | 18.4 | 45.3 | 44.1 | 0.986 | 0
292 | 2022-12-21 04:52 | 7.5 | 18.4 | 45.9 | 44.4 | 0.987 | 0
293 | 2022-12-21 04:53 | 7.6 | 18.3 | 45.9 | 45.1 | 0.983 | 0
294 | 2022-12-21 04:54 | 7.6 | 18.4 | 45.6 | 44.8 | 0.988 | 0
295 | 2022-12-21 04:55 | 7.5 | 18.3 | 45.8 | 44.8 | 0.986 | 0
296 | 2022-12-21 04:56 | 7.5 | 18.3 | 45.7 | 44.7 | 0.982 | 0
297 | 2022-12-21 04:57 | 7.6 | 18.4 | 45.7 | 44.7 | 0.985 | 0
298 | 2022-12-21 04:58 | 7.6 | 18.3 | 45.6 | 44.6 | 0.987 | 0
299 | 2022-12-21 04:59 | 7.4 | 18.4 | 45.5 | 44.6 | 0.985 | 0
300 | 2022-12-21 05:00 | 7.5 | 18.3 | 45.4 | 44.5 | 0.983 | 0
301 | 2022-12-21 05:01 | 7.4 | 18.3 | 45.4 | 44.4 | 0.989 | 0
302 | 2022-12-21 05:02 | 7.6 | 18.4 | 45.3 | 44.4 | 0.988 | 0
303 | 2022-12-21 05:03 | 7.7 | 18.4 | 45.3 | 44.3 | 0.985 | 0
304 | 2022-12-21 05:04 | 7.4 | 18.4 | 45.6 | 44.4 | 0.979 | 0
305 | 2022-12-21 05:05 | 7.4 | 18.3 | 46 | 44.8 | 0.982 | 0
306 | 2022-12-21 05:06 | 7.6 | 18.3 | 46.5 | 45.2 | 0.984 | 0
307 | 2022-12-21 05:07 | 7.3 | 18.3 | 46.8 | 45.6 | 0.988 | 0
308 | 2022-12-21 05:08 | 7.5 | 18.3 | 47.1 | 45.8 | 0.99 | 0
309 | 2022-12-21 05:09 | 7.6 | 18.3 | 47.8 | 46.2 | 0.985 | 0
310 | 2022-12-21 05:10 | 7.3 | 18.4 | 47.6 | 46.8 | 0.987 | 0
311 | 2022-12-21 05:11 | 7.6 | 18.3 | 47.5 | 46.3 | 0.987 | 0
312 | 2022-12-21 05:12 | 7.3 | 18.4 | 47.4 | 46.5 | 0.985 | 0
313 | 2022-12-21 05:13 | 7.3 | 18.4 | 47.3 | 46.2 | 0.988 | 0
314 | 2022-12-21 05:14 | 7.4 | 18.3 | 47.3 | 46.3 | 0.985 | 0
315 | 2022-12-21 05:15 | 7.3 | 18.4 | 47.3 | 46.3 | 0.986 | 0
316 | 2022-12-21 05:17 | 7.4 | 18.3 | 47.3 | 46.3 | 0.986 | 0
317 | 2022-12-21 05:17 | 7.1 | 18.4 | 47.2 | 46.2 | 0.985 | 0
318 | 2022-12-21 05:19 | 7.4 | 18.3 | 47.2 | 46.2 | 0.984 | 0
319 | 2022-12-21 05:20 | 7.2 | 18.4 | 47.1 | 46.1 | 0.984 | 0
320 | 2022-12-21 05:20 | 7.3 | 18.4 | 47 | 46.1 | 0.988 | 0
321 | 2022-12-21 05:22 | 7.1 | 18.3 | 47 | 46 | 0.987 | 0
322 | 2022-12-21 05:23 | 7.1 | 18.4 | 46.9 | 45.9 | 0.989 | 0
323 | 2022-12-21 05:24 | 7.1 | 18.4 | 46.8 | 45.8 | 0.988 | 0
324 | 2022-12-21 05:24 | 7.2 | 18.4 | 46.7 | 45.8 | 0.984 | 0
325 | 2022-12-21 05:26 | 7.4 | 18.3 | 46.7 | 45.7 | 0.987 | 0
326 | 2022-12-21 05:26 | 7.5 | 18.3 | 46.6 | 45.6 | 0.985 | 0
327 | 2022-12-21 05:27 | 7.3 | 18.3 | 46.5 | 45.6 | 0.986 | 0
328 | 2022-12-21 05:28 | 7.5 | 18.3 | 46.5 | 45.5 | 0.987 | 0
329 | 2022-12-21 05:29 | 7.2 | 18.4 | 46.3 | 45.4 | 0.984 | 0
330 | 2022-12-21 05:30 | 7.3 | 18.4 | 46.3 | 45.3 | 0.986 | 0
331 | 2022-12-21 05:31 | 7.4 | 18.3 | 46.2 | 45.2 | 0.986 | 0
332 | 2022-12-21 05:33 | 7.1 | 18.4 | 46.1 | 45.1 | 0.983 | 0
333 | 2022-12-21 05:34 | 7.3 | 18.3 | 46.3 | 45.1 | 0.986 | 0
334 | 2022-12-21 05:34 | 7.4 | 18.3 | 46.6 | 45.4 | 0.983 | 0
335 | 2022-12-21 05:35 | 7.1 | 18.3 | 47 | 45.6 | 0.985 | 0
336 | 2022-12-21 05:36 | 7.1 | 18.3 | 47.4 | 46.1 | 0.986 | 0
337 | 2022-12-21 05:38 | 7.4 | 18.4 | 47.9 | 46.5 | 0.988 | 0
338 | 2022-12-21 05:38 | 7.3 | 18.3 | 47.5 | 46.8 | 0.994 | 0
339 | 2022-12-21 05:40 | 7.2 | 18.3 | 47.3 | 46.3 | 0.987 | 0
340 | 2022-12-21 05:40 | 7.3 | 18.3 | 47.4 | 46.4 | 0.987 | 0
341 | 2022-12-21 05:42 | 7.3 | 18.3 | 47.3 | 46.3 | 0.987 | 0
342 | 2022-12-21 05:42 | 7.3 | 18.3 | 47.2 | 46.3 | 0.984 | 0
343 | 2022-12-21 05:44 | 7.2 | 18.3 | 47.1 | 46.2 | 1.156 | 0
344 | 2022-12-21 05:44 | 7.2 | 18.3 | 47 | 35.4 | 1.582 | 0
345 | 2022-12-21 05:46 | 7.3 | 18.2 | 47 | 43.8 | 1.598 | 0
346 | 2022-12-21 05:46 | 7.3 | 18.3 | 46.6 | 45 | 1.591 | 0
347 | 2022-12-21 05:48 | 7.3 | 18.3 | 45.5 | 44.3 | 1.585 | 0
348 | 2022-12-21 05:49 | 7.2 | 18.3 | 45.9 | 43.9 | 1.593 | 0
349 | 2022-12-21 05:50 | 7.1 | 18.3 | 46 | 44.2 | 1.594 | 0
350 | 2022-12-21 05:50 | 7.2 | 18.3 | 45.9 | 44.2 | 1.593 | 0
351 | 2022-12-21 05:51 | 7.1 | 18.3 | 45.9 | 44.1 | 1.588 | 0
352 | 2022-12-21 05:52 | 7.1 | 18.2 | 45.8 | 44.1 | 1.593 | 0
353 | 2022-12-21 05:54 | 7 | 18.2 | 45.7 | 44 | 1.589 | 0
354 | 2022-12-21 05:54 | 7.1 | 18.3 | 45.5 | 43.9 | 1.592 | 0
355 | 2022-12-21 05:55 | 7.1 | 18.3 | 45.4 | 43.8 | 1.594 | 0
356 | 2022-12-21 05:56 | 7.1 | 18.3 | 45.3 | 43.6 | 1.592 | 0
357 | 2022-12-21 05:58 | 7 | 18.2 | 45.2 | 43.6 | 1.588 | 0
358 | 2022-12-21 05:58 | 7.1 | 18.3 | 45 | 43.4 | 1.594 | 0
359 | 2022-12-21 06:00 | 7.1 | 18.2 | 44.9 | 44 | 1.592 | 0
360 | 2022-12-21 06:00 | 6.9 | 18.2 | 44.9 | 44.1 | 1.59 | 0
361 | 2022-12-21 06:02 | 7.1 | 18.2 | 44.8 | 44 | 1.574 | 0
362 | 2022-12-21 06:02 | 7.2 | 18.2 | 44.8 | 44 | 0.985 | 0
363 | 2022-12-21 06:04 | 6.9 | 18.2 | 44.8 | 43.8 | 0.984 | 0
364 | 2022-12-21 06:05 | 7 | 18.2 | 44.8 | 43.8 | 0.983 | 0
365 | 2022-12-21 06:06 | 7 | 18.2 | 45 | 43.9 | 0.98 | 0
366 | 2022-12-21 06:06 | 6.9 | 18.2 | 45.5 | 44.1 | 0.986 | 0
367 | 2022-12-21 06:08 | 6.9 | 18.2 | 46 | 44.7 | 0.985 | 0
368 | 2022-12-21 06:09 | 7.1 | 18.2 | 46.3 | 45.1 | 0.987 | 0
369 | 2022-12-21 06:10 | 6.9 | 18.3 | 46.8 | 45.5 | 0.986 | 0
370 | 2022-12-21 06:10 | 6.9 | 18.2 | 46.2 | 45.5 | 0.986 | 0
371 | 2022-12-21 06:11 | 6.9 | 18.2 | 46.2 | 45.2 | 0.983 | 0
372 | 2022-12-21 06:12 | 7 | 18.2 | 46 | 45.2 | 0.984 | 0
373 | 2022-12-21 06:14 | 7.1 | 18.2 | 46 | 45 | 0.982 | 0
374 | 2022-12-21 06:14 | 7 | 18.2 | 45.9 | 45.1 | 0.988 | 0
375 | 2022-12-21 06:16 | 7 | 18.2 | 45.9 | 44.9 | 0.982 | 0
376 | 2022-12-21 06:16 | 7 | 18.3 | 45.7 | 44.9 | 1.038 | 0
377 | 2022-12-21 06:18 | 7 | 18.2 | 45.7 | 43.2 | 1.569 | 0
378 | 2022-12-21 06:18 | 6.9 | 18.2 | 45.7 | 43.1 | 1.642 | 0
379 | 2022-12-21 06:20 | 6.9 | 18.2 | 45.6 | 43.8 | 1.643 | 0
380 | 2022-12-21 06:20 | 7 | 18.2 | 45.1 | 43.5 | 1.649 | 0
381 | 2022-12-21 06:22 | 7.1 | 18.3 | 45.3 | 43.3 | 1.642 | 0
382 | 2022-12-21 06:22 | 6.9 | 18.3 | 45.3 | 43.4 | 1.647 | 0
383 | 2022-12-21 06:24 | 6.9 | 18.2 | 45.1 | 43.4 | 1.646 | 0
384 | 2022-12-21 06:25 | 6.9 | 18.3 | 45 | 43.2 | 1.646 | 0
385 | 2022-12-21 06:26 | 7 | 18.3 | 44.9 | 43.1 | 1.648 | 0
386 | 2022-12-21 06:26 | 7 | 18.3 | 44.6 | 43 | 1.648 | 0
387 | 2022-12-21 06:27 | 6.9 | 18.3 | 44.6 | 42.8 | 1.649 | 0
388 | 2022-12-21 06:29 | 6.9 | 18.3 | 44.5 | 42.7 | 1.648 | 0
389 | 2022-12-21 06:30 | 7 | 18.4 | 44.4 | 42.7 | 1.645 | 0
390 | 2022-12-21 06:31 | 6.7 | 18.5 | 44.2 | 42.5 | 1.648 | 0
391 | 2022-12-21 06:32 | 6.7 | 18.4 | 44.1 | 42.4 | 1.639 | 0
392 | 2022-12-21 06:33 | 6.7 | 18.4 | 44 | 42.4 | 1.643 | 0
393 | 2022-12-21 06:34 | 6.6 | 18.4 | 43.8 | 42.2 | 1.647 | 0
394 | 2022-12-21 06:34 | 6.8 | 18.4 | 43.7 | 42.1 | 1.644 | 0
395 | 2022-12-21 06:36 | 6.8 | 18.4 | 43.5 | 41.9 | 1.643 | 0
396 | 2022-12-21 06:36 | 6.7 | 18.5 | 43.4 | 41.8 | 1.648 | 0
397 | 2022-12-21 06:37 | 6.7 | 18.4 | 43.3 | 41.7 | 1.644 | 0
398 | 2022-12-21 06:38 | 6.7 | 18.5 | 43.2 | 41.5 | 1.642 | 0
399 | 2022-12-21 06:40 | 6.8 | 18.5 | 43 | 42.4 | 1.647 | 0
400 | 2022-12-21 06:40 | 6.8 | 18.4 | 43 | 42.2 | 1.649 | 0
401 | 2022-12-21 06:41 | 6.6 | 18.5 | 43 | 42.2 | 1.642 | 0
402 | 2022-12-21 06:42 | 6.5 | 18.4 | 43 | 42.2 | 1.625 | 0
403 | 2022-12-21 06:43 | 6.5 | 18.4 | 42.9 | 42.2 | 1.508 | 0
404 | 2022-12-21 06:44 | 6.6 | 18.4 | 42.9 | 42.1 | 1.184 | 0
405 | 2022-12-21 06:46 | 6.7 | 18.4 | 42.7 | 41.9 | 0.984 | 0
406 | 2022-12-21 06:47 | 6.5 | 18.4 | 42.6 | 41.8 | 0.983 | 0
407 | 2022-12-21 06:48 | 6.7 | 18.3 | 42.6 | 41.7 | 0.983 | 0
408 | 2022-12-21 06:49 | 6.7 | 18.3 | 42.5 | 41.7 | 0.979 | 0
409 | 2022-12-21 06:50 | 6.7 | 18.3 | 42.4 | 41.6 | 0.979 | 0
410 | 2022-12-21 06:50 | 6.8 | 18.3 | 42.4 | 41.6 | 0.978 | 0
411 | 2022-12-21 06:52 | 6.7 | 18.3 | 42.3 | 41.5 | 0.983 | 0
412 | 2022-12-21 06:53 | 6.6 | 18.3 | 42.2 | 41.4 | 0.977 | 0
413 | 2022-12-21 06:54 | 6.7 | 18.3 | 42.1 | 41.4 | 0.983 | 0
414 | 2022-12-21 06:54 | 6.8 | 18.3 | 42 | 41.1 | 0.983 | 0
415 | 2022-12-21 06:56 | 6.8 | 18.3 | 42 | 41.2 | 0.981 | 0
416 | 2022-12-21 06:56 | 6.7 | 18.3 | 42 | 41.1 | 0.98 | 0
417 | 2022-12-21 06:57 | 6.6 | 18.3 | 41.9 | 41.1 | 0.978 | 0
418 | 2022-12-21 06:58 | 6.6 | 18.2 | 41.8 | 41 | 0.979 | 0
419 | 2022-12-21 06:59 | 6.8 | 18.3 | 41.8 | 40.9 | 0.978 | 0
420 | 2022-12-21 07:00 | 6.7 | 18.3 | 41.7 | 40.9 | 0.98 | 0
421 | 2022-12-21 07:01 | 6.7 | 18.3 | 41.6 | 40.9 | 0.975 | 0
422 | 2022-12-21 07:03 | 6.6 | 18.2 | 41.5 | 40.7 | 0.979 | 0
423 | 2022-12-21 07:04 | 6.5 | 18.2 | 41.3 | 40.5 | 0.978 | 0
424 | 2022-12-21 07:04 | 6.5 | 18.2 | 41.5 | 40.5 | 0.981 | 0
425 | 2022-12-21 07:05 | 6.7 | 18.2 | 42 | 40.8 | 0.979 | 0
426 | 2022-12-21 07:06 | 6.7 | 18.3 | 42.4 | 41.3 | 0.982 | 0
427 | 2022-12-21 07:08 | 6.5 | 18.2 | 42.8 | 41.7 | 0.981 | 0
428 | 2022-12-21 07:08 | 6.7 | 18.3 | 43 | 42 | 0.98 | 0
429 | 2022-12-21 07:10 | 6.4 | 18.2 | 43.5 | 42.3 | 0.982 | 0
430 | 2022-12-21 07:10 | 6.4 | 18.3 | 43.8 | 42.7 | 0.982 | 0
431 | 2022-12-21 07:12 | 6.4 | 18.3 | 44.3 | 43 | 0.982 | 0
432 | 2022-12-21 07:12 | 6.7 | 18.3 | 44.8 | 43.5 | 0.983 | 0
433 | 2022-12-21 07:14 | 6.5 | 18.2 | 45.2 | 43.9 | 0.985 | 0
434 | 2022-12-21 07:14 | 6.4 | 18.2 | 45.7 | 44.3 | 0.982 | 0
435 | 2022-12-21 07:16 | 6.2 | 18.2 | 45.9 | 44.9 | 0.981 | 0
436 | 2022-12-21 07:16 | 6.2 | 18.2 | 45.4 | 44.6 | 0.985 | 0
437 | 2022-12-21 07:18 | 6.5 | 18.2 | 45.7 | 44.4 | 0.984 | 0
438 | 2022-12-21 07:19 | 6.6 | 18.2 | 45.4 | 44.6 | 0.983 | 0
439 | 2022-12-21 07:20 | 6.5 | 18.2 | 45.3 | 44.4 | 0.982 | 0
440 | 2022-12-21 07:20 | 6.6 | 18.2 | 45.2 | 44.3 | 0.984 | 0
441 | 2022-12-21 07:21 | 6.3 | 18.2 | 45 | 44.2 | 1.5 | 0
442 | 2022-12-21 07:22 | 6.3 | 18.2 | 45 | 36.5 | 1.578 | 0
443 | 2022-12-21 07:24 | 6.4 | 18.2 | 45 | 43 | 1.591 | 0
444 | 2022-12-21 07:24 | 6.4 | 18.2 | 44.6 | 43.2 | 1.591 | 0
445 | 2022-12-21 07:25 | 6.4 | 18.2 | 44.4 | 42.7 | 1.584 | 0
446 | 2022-12-21 07:26 | 6.5 | 18.2 | 44.6 | 42.8 | 1.589 | 0
447 | 2022-12-21 07:28 | 6.3 | 18.1 | 44.6 | 42.9 | 1.588 | 0
448 | 2022-12-21 07:28 | 6.5 | 18.3 | 44.6 | 42.9 | 1.586 | 0
449 | 2022-12-21 07:30 | 6.5 | 18.1 | 44.5 | 42.8 | 1.582 | 0
450 | 2022-12-21 07:30 | 6.4 | 18.1 | 44.4 | 42.8 | 1.585 | 0
451 | 2022-12-21 07:32 | 6.5 | 18.1 | 44.3 | 42.7 | 1.58 | 0
452 | 2022-12-21 07:32 | 6.4 | 18.1 | 44.1 | 42.6 | 1.588 | 0
453 | 2022-12-21 07:34 | 6.3 | 18.1 | 44.1 | 42.5 | 1.582 | 1
454 | 2022-12-21 07:35 | 6.5 | 18.1 | 44.2 | 42.4 | 1.584 | 1
455 | 2022-12-21 07:36 | 6.5 | 18.1 | 44.5 | 42.6 | 1.583 | 2
456 | 2022-12-21 07:36 | 6.6 | 18.1 | 45.1 | 42.9 | 1.586 | 2
457 | 2022-12-21 07:38 | 6.7 | 18.1 | 45.2 | 43.4 | 1.586 | 2
458 | 2022-12-21 07:39 | 6.6 | 18.1 | 45.3 | 44.3 | 1.588 | 3
459 | 2022-12-21 07:40 | 6.6 | 18.1 | 45.2 | 44.4 | 1.588 | 3
460 | 2022-12-21 07:40 | 6.6 | 18.1 | 45.3 | 44.4 | 1.565 | 4
461 | 2022-12-21 07:41 | 6.5 | 18.1 | 45.4 | 44.4 | 0.985 | 4
462 | 2022-12-21 07:42 | 6.6 | 18.1 | 45.3 | 44.4 | 0.982 | 4
463 | 2022-12-21 07:44 | 6.7 | 18.1 | 45.2 | 44.3 | 0.981 | 5
464 | 2022-12-21 07:44 | 6.6 | 18.1 | 45.2 | 44.2 | 0.982 | 5
465 | 2022-12-21 07:46 | 6.7 | 18.2 | 45 | 44.2 | 0.983 | 6
466 | 2022-12-21 07:46 | 6.6 | 18.1 | 44.9 | 44 | 0.983 | 6
467 | 2022-12-21 07:48 | 6.5 | 18.2 | 44.9 | 44 | 0.982 | 7
468 | 2022-12-21 07:48 | 6.7 | 18.2 | 44.8 | 43.9 | 0.982 | 7
469 | 2022-12-21 07:50 | 6.5 | 18.1 | 44.8 | 43.9 | 0.983 | 8
470 | 2022-12-21 07:50 | 6.5 | 18.1 | 44.8 | 43.8 | 0.986 | 8
471 | 2022-12-21 07:52 | 6.5 | 18.1 | 44.7 | 43.8 | 0.979 | 8
472 | 2022-12-21 07:53 | 6.5 | 18.1 | 44.7 | 43.7 | 0.982 | 9
473 | 2022-12-21 07:54 | 6.3 | 18.1 | 44.5 | 43.6 | 0.982 | 9
474 | 2022-12-21 07:55 | 6.4 | 18.1 | 44.5 | 43.5 | 0.982 | 10
475 | 2022-12-21 07:56 | 6.3 | 18.1 | 44.5 | 43.6 | 0.984 | 10
476 | 2022-12-21 07:57 | 6.5 | 18.2 | 44.4 | 43.5 | 0.981 | 11
477 | 2022-12-21 07:58 | 6.6 | 18.1 | 44.3 | 43.4 | 0.982 | 12
478 | 2022-12-21 07:59 | 6.3 | 18.1 | 44.2 | 43.3 | 0.986 | 12
479 | 2022-12-21 08:00 | 6.6 | 18.2 | 44.2 | 43.3 | 0.978 | 13
480 | 2022-12-21 08:01 | 6.3 | 18.1 | 44.1 | 43.2 | 0.982 | 14
481 | 2022-12-21 08:02 | 6.4 | 18.1 | 44.1 | 42.6 | 1.59 | 15
482 | 2022-12-21 08:03 | 6.5 | 18 | 44 | 40.5 | 1.869 | 15
483 | 2022-12-21 08:04 | 6.4 | 18 | 43.8 | 37.7 | 2.001 | 16
484 | 2022-12-21 08:05 | 6.4 | 18 | 43.5 | 40 | 2.007 | 17
485 | 2022-12-21 08:06 | 6.7 | 18.3 | 43.4 | 40.2 | 2.005 | 17
486 | 2022-12-21 08:07 | 6.5 | 18.6 | 43.7 | 40.1 | 2.014 | 18
487 | 2022-12-21 08:08 | 6.5 | 19 | 44 | 40.4 | 2.012 | 19
488 | 2022-12-21 08:09 | 6.3 | 19.4 | 44.2 | 40.6 | 2.013 | 19
489 | 2022-12-21 08:10 | 6.4 | 19.8 | 44 | 40.8 | 2.01 | 20
490 | 2022-12-21 08:11 | 6.6 | 19.9 | 43.6 | 40.7 | 2.012 | 21
491 | 2022-12-21 08:12 | 6.6 | 20.1 | 43.5 | 40.3 | 2.009 | 21
492 | 2022-12-21 08:13 | 6.5 | 20.2 | 43.2 | 40.2 | 2.011 | 21
493 | 2022-12-21 08:14 | 6.4 | 20.2 | 43 | 40 | 2.011 | 21
494 | 2022-12-21 08:15 | 6.4 | 20.4 | 42.7 | 39.8 | 2.008 | 22
495 | 2022-12-21 08:16 | 6.3 | 20.5 | 42.5 | 39.6 | 2.007 | 23
496 | 2022-12-21 08:17 | 6.6 | 20.5 | 42.2 | 39.3 | 2.015 | 23
497 | 2022-12-21 08:18 | 6.6 | 20.5 | 42 | 39.1 | 2.009 | 24
498 | 2022-12-21 08:19 | 6.7 | 20.5 | 41.8 | 39 | 2.006 | 24
499 | 2022-12-21 08:20 | 6.7 | 20.6 | 41.6 | 38.7 | 2.004 | 25
500 | 2022-12-21 08:21 | 6.4 | 20.5 | 41.3 | 38.6 | 2.008 | 25
501 | 2022-12-21 08:22 | 6.4 | 20.5 | 41.1 | 38.4 | 2.008 | 26
502 | 2022-12-21 08:23 | 6.6 | 20.6 | 40.9 | 38.2 | 2.005 | 26
503 | 2022-12-21 08:24 | 6.4 | 20.6 | 40.6 | 38 | 2.006 | 26
504 | 2022-12-21 08:25 | 6.6 | 20.6 | 40.4 | 37.7 | 1.997 | 27
505 | 2022-12-21 08:26 | 6.7 | 20.6 | 40.2 | 37.5 | 2.006 | 28
506 | 2022-12-21 08:27 | 6.7 | 20.7 | 40 | 37.3 | 2.002 | 29
507 | 2022-12-21 08:28 | 6.6 | 20.6 | 39.8 | 37.2 | 2.007 | 29
508 | 2022-12-21 08:29 | 6.5 | 20.6 | 39.5 | 37 | 2.009 | 30
509 | 2022-12-21 08:30 | 6.5 | 20.7 | 39.3 | 36.8 | 2.006 | 32
510 | 2022-12-21 08:31 | 6.6 | 20.7 | 39 | 36.5 | 2.002 | 34
511 | 2022-12-21 08:32 | 6.6 | 20.8 | 38.8 | 36.4 | 2.005 | 34
512 | 2022-12-21 08:33 | 6.6 | 20.8 | 38.6 | 36.1 | 1.999 | 36
513 | 2022-12-21 08:34 | 6.6 | 20.7 | 38.5 | 36 | 1.994 | 38
514 | 2022-12-21 08:35 | 6.6 | 20.6 | 38.6 | 35.9 | 2 | 42
515 | 2022-12-21 08:36 | 6.7 | 20.7 | 39.1 | 36 | 1.999 | 44
516 | 2022-12-21 08:37 | 6.8 | 20.7 | 39.3 | 36.5 | 1.999 | 47
517 | 2022-12-21 08:38 | 6.7 | 20.7 | 39.5 | 36.6 | 2.011 | 47
518 | 2022-12-21 08:39 | 6.6 | 20.7 | 39.8 | 36.8 | 2 | 47
519 | 2022-12-21 08:40 | 6.7 | 20.7 | 40.1 | 37.1 | 1.998 | 48
520 | 2022-12-21 08:41 | 6.5 | 20.8 | 40.4 | 37.3 | 2.002 | 52
521 | 2022-12-21 08:42 | 6.5 | 20.7 | 40.6 | 37.6 | 2.007 | 49
522 | 2022-12-21 08:43 | 6.6 | 20.7 | 40.8 | 37.7 | 2.005 | 50
523 | 2022-12-21 08:44 | 6.5 | 20.7 | 41.1 | 38 | 2.009 | 55
524 | 2022-12-21 08:45 | 6.7 | 20.9 | 41.3 | 38.2 | 2.01 | 61
525 | 2022-12-21 08:46 | 6.6 | 20.9 | 41.5 | 38.4 | 2.002 | 61
526 | 2022-12-21 08:47 | 6.4 | 20.9 | 41.8 | 38.6 | 1.998 | 60
527 | 2022-12-21 08:48 | 6.6 | 21 | 42 | 38.8 | 2.003 | 57
528 | 2022-12-21 08:49 | 6.7 | 21.1 | 42.2 | 39 | 2.01 | 54
529 | 2022-12-21 08:50 | 6.7 | 21 | 42.3 | 39.2 | 2.006 | 63
530 | 2022-12-21 08:51 | 6.9 | 21 | 42.1 | 39.3 | 2.009 | 68
531 | 2022-12-21 08:52 | 6.9 | 21.1 | 42 | 39.1 | 2.006 | 62
532 | 2022-12-21 08:53 | 6.9 | 21.1 | 42 | 39 | 2.005 | 61
533 | 2022-12-21 08:54 | 6.8 | 21 | 42.4 | 39 | 2.003 | 62
534 | 2022-12-21 08:55 | 7 | 21.1 | 42.6 | 39.4 | 2.001 | 60
535 | 2022-12-21 08:56 | 6.9 | 21 | 42.8 | 39.5 | 2.009 | 59
536 | 2022-12-21 08:57 | 6.9 | 21.1 | 42.9 | 39.7 | 2.008 | 56
537 | 2022-12-21 08:58 | 6.7 | 21.1 | 43.1 | 39.8 | 2.012 | 59
538 | 2022-12-21 08:59 | 6.8 | 21.2 | 43.3 | 40 | 2.009 | 60
539 | 2022-12-21 09:00 | 6.9 | 21.2 | 43.5 | 40.2 | 2.008 | 55
540 | 2022-12-21 09:01 | 7.1 | 21.2 | 43.4 | 40.3 | 2.009 | 55
541 | 2022-12-21 09:02 | 7 | 21.3 | 43.1 | 40.2 | 2.008 | 62
542 | 2022-12-21 09:03 | 7.2 | 21.3 | 42.9 | 39.9 | 2.003 | 74
543 | 2022-12-21 09:04 | 7 | 21.4 | 42.7 | 39.8 | 2.008 | 81
544 | 2022-12-21 09:05 | 7 | 21.4 | 42.9 | 39.7 | 2.001 | 75
545 | 2022-12-21 09:06 | 7.2 | 21.4 | 43.2 | 39.9 | 2.009 | 63
546 | 2022-12-21 09:07 | 7.3 | 21.4 | 43.4 | 40.1 | 2.009 | 54
547 | 2022-12-21 09:08 | 7.2 | 21.4 | 43.7 | 40.3 | 2.017 | 52
548 | 2022-12-21 09:09 | 7 | 21.5 | 43.9 | 40.5 | 2.007 | 53
549 | 2022-12-21 09:10 | 7.3 | 21.5 | 44 | 40.7 | 2.012 | 53
550 | 2022-12-21 09:11 | 7.3 | 21.4 | 44.1 | 40.9 | 2.008 | 52
551 | 2022-12-21 09:12 | 7.1 | 21.6 | 43.7 | 40.8 | 2.012 | 55
552 | 2022-12-21 09:13 | 7.4 | 21.6 | 43.5 | 40.5 | 2.005 | 56
553 | 2022-12-21 09:14 | 7.4 | 21.6 | 43.2 | 40.3 | 2.005 | 62
554 | 2022-12-21 09:15 | 7.3 | 21.7 | 43 | 40.1 | 2.008 | 69
555 | 2022-12-21 09:16 | 7.4 | 21.5 | 42.7 | 39.9 | 2.005 | 69
556 | 2022-12-21 09:17 | 7.4 | 21.5 | 42.6 | 39.6 | 2.008 | 73
557 | 2022-12-21 09:18 | 7.4 | 21.5 | 42.4 | 39.5 | 1.998 | 78
558 | 2022-12-21 09:19 | 7.4 | 21.5 | 42.1 | 39.3 | 2.009 | 79
559 | 2022-12-21 09:20 | 7.5 | 21.5 | 41.9 | 39.1 | 2.005 | 85
560 | 2022-12-21 09:21 | 7.5 | 21.5 | 41.7 | 38.9 | 2.004 | 98
561 | 2022-12-21 09:22 | 7.6 | 21.4 | 41.4 | 38.8 | 2.005 | 100
562 | 2022-12-21 09:23 | 7.7 | 21.4 | 41.2 | 38.5 | 2.006 | 103
563 | 2022-12-21 09:24 | 7.5 | 21.4 | 41 | 38.3 | 2.005 | 112
564 | 2022-12-21 09:25 | 7.5 | 21.5 | 40.8 | 38.2 | 1.999 | 113
565 | 2022-12-21 09:26 | 7.7 | 21.5 | 40.6 | 38 | 2.001 | 110
566 | 2022-12-21 09:27 | 7.7 | 21.4 | 40.4 | 37.8 | 1.995 | 100
567 | 2022-12-21 09:28 | 7.8 | 21.4 | 40.2 | 37.6 | 2.002 | 118
568 | 2022-12-21 09:29 | 7.8 | 21.5 | 39.9 | 37.4 | 2.004 | 230
569 | 2022-12-21 09:30 | 7.8 | 21.4 | 39.7 | 37.2 | 1.999 | 437
570 | 2022-12-21 09:31 | 8.1 | 21.4 | 39.5 | 37 | 1.996 | 573
571 | 2022-12-21 09:32 | 8.2 | 21.5 | 39.3 | 36.8 | 1.996 | 580
572 | 2022-12-21 09:33 | 8.5 | 21.4 | 39.2 | 36.6 | 1.993 | 593
573 | 2022-12-21 09:34 | 8.5 | 21.5 | 39 | 36.5 | 1.996 | 610
574 | 2022-12-21 09:35 | 8.9 | 21.3 | 39 | 36.4 | 2.001 | 617
575 | 2022-12-21 09:36 | 8.9 | 21.4 | 39.3 | 36.5 | 1.995 | 614
576 | 2022-12-21 09:37 | 9.4 | 21.4 | 39.6 | 36.6 | 2.001 | 613
577 | 2022-12-21 09:38 | 9.5 | 21.4 | 40 | 37 | 1.999 | 614
578 | 2022-12-21 09:39 | 9.5 | 21.4 | 40.2 | 37.3 | 1.999 | 631
579 | 2022-12-21 09:40 | 9.9 | 21.4 | 40.5 | 37.4 | 1.999 | 625
580 | 2022-12-21 09:41 | 10.1 | 21.4 | 40.7 | 37.8 | 1.998 | 633
581 | 2022-12-21 09:42 | 9.9 | 21.5 | 40.8 | 38 | 2.003 | 659
582 | 2022-12-21 09:43 | 9.7 | 21.4 | 40.7 | 38 | 2.003 | 664
583 | 2022-12-21 09:44 | 9.8 | 21.4 | 40.4 | 37.9 | 2.003 | 630
584 | 2022-12-21 09:45 | 9.5 | 21.5 | 40.3 | 37.6 | 2.004 | 634
585 | 2022-12-21 09:46 | 9.4 | 21.6 | 40 | 37.5 | 2 | 624
586 | 2022-12-21 09:47 | 9.4 | 21.5 | 39.7 | 37.3 | 2.003 | 645
587 | 2022-12-21 09:48 | 9.6 | 21.5 | 39.7 | 37.1 | 1.997 | 181
588 | 2022-12-21 09:49 | 9.4 | 21.5 | 39.4 | 37 | 2.002 | 181
589 | 2022-12-21 09:50 | 9.5 | 21.6 | 39.2 | 36.8 | 2 | 576
590 | 2022-12-21 09:51 | 9.5 | 21.6 | 39 | 36.6 | 1.999 | 201
591 | 2022-12-21 09:52 | 9.6 | 21.6 | 38.9 | 36.5 | 1.997 | 194
592 | 2022-12-21 09:53 | 9.7 | 21.6 | 38.7 | 36.3 | 1.999 | 677
593 | 2022-12-21 09:54 | 9.9 | 21.6 | 38.5 | 36.2 | 1.996 | 383
594 | 2022-12-21 09:55 | 10 | 21.6 | 38.3 | 36 | 1.993 | 387
595 | 2022-12-21 09:56 | 10.2 | 21.6 | 38.1 | 35.8 | 1.999 | 697
596 | 2022-12-21 09:57 | 10.4 | 21.7 | 38 | 35.7 | 2.002 | 327
597 | 2022-12-21 09:58 | 10 | 21.7 | 37.7 | 35.5 | 1.99 | 203
598 | 2022-12-21 09:59 | 9.6 | 21.7 | 37.5 | 35.3 | 1.992 | 213
599 | 2022-12-21 10:00 | 9.6 | 21.7 | 37.4 | 35.2 | 2.005 | 692
600 | 2022-12-21 10:01 | 10.1 | 21.7 | 37.2 | 35 | 1.995 | 688
601 | 2022-12-21 10:02 | 10.1 | 21.7 | 37 | 34.9 | 1.992 | 710
602 | 2022-12-21 10:03 | 10.2 | 21.6 | 36.9 | 34.7 | 1.997 | 717
603 | 2022-12-21 10:04 | 10.4 | 21.6 | 36.7 | 34.6 | 1.997 | 720
604 | 2022-12-21 10:05 | 10.7 | 21.6 | 36.8 | 34.5 | 1.996 | 705
605 | 2022-12-21 10:06 | 10.6 | 21.7 | 37.2 | 34.6 | 1.993 | 687
606 | 2022-12-21 10:07 | 10.7 | 21.7 | 37.6 | 34.9 | 1.992 | 699
607 | 2022-12-21 10:08 | 11 | 21.6 | 37.8 | 35.2 | 1.998 | 778
608 | 2022-12-21 10:09 | 11.3 | 21.6 | 38.1 | 35.4 | 1.998 | 775
609 | 2022-12-21 10:10 | 11.5 | 21.6 | 38.5 | 35.7 | 1.994 | 755
610 | 2022-12-21 10:11 | 10.9 | 21.7 | 38.6 | 36 | 2.003 | 724
611 | 2022-12-21 10:12 | 10.8 | 21.7 | 38.5 | 36.1 | 1.999 | 713
612 | 2022-12-21 10:13 | 11 | 21.7 | 38.4 | 36 | 1.998 | 708
613 | 2022-12-21 10:14 | 10.9 | 21.7 | 38.2 | 35.9 | 2.002 | 705
614 | 2022-12-21 10:15 | 10.8 | 21.8 | 38.1 | 35.8 | 1.997 | 709
615 | 2022-12-21 10:16 | 11 | 21.8 | 37.9 | 35.7 | 1.995 | 720
616 | 2022-12-21 10:17 | 10.8 | 21.7 | 37.7 | 36.2 | 1.998 | 746
617 | 2022-12-21 10:18 | 11 | 21.4 | 37.6 | 36.1 | 1.992 | 756
618 | 2022-12-21 10:19 | 11.2 | 21.1 | 37.5 | 36 | 1.994 | 767
619 | 2022-12-21 10:20 | 11.3 | 20.9 | 37.4 | 35.9 | 1.947 | 755
620 | 2022-12-21 10:21 | 10.9 | 20.8 | 37.4 | 35.7 | 1.833 | 615
621 | 2022-12-21 10:22 | 10.4 | 20.7 | 37.1 | 35.7 | 1.839 | 706
622 | 2022-12-21 10:23 | 10.4 | 20.6 | 37 | 35.4 | 1.834 | 237
623 | 2022-12-21 10:24 | 10.7 | 20.5 | 36.9 | 35.4 | 1.828 | 170
624 | 2022-12-21 10:25 | 10.3 | 20.5 | 36.9 | 35.3 | 1.835 | 764
625 | 2022-12-21 10:26 | 10.4 | 20.5 | 37.3 | 35.3 | 1.835 | 360
626 | 2022-12-21 10:27 | 10.5 | 20.5 | 37.3 | 35.7 | 1.829 | 319
627 | 2022-12-21 10:28 | 10.2 | 20.5 | 37.2 | 35.6 | 1.836 | 708
628 | 2022-12-21 10:29 | 10.5 | 20.4 | 37.1 | 35.6 | 1.826 | 771
629 | 2022-12-21 10:30 | 10.3 | 20.4 | 37 | 35.5 | 1.832 | 795
630 | 2022-12-21 10:31 | 10.2 | 20.5 | 36.9 | 35.3 | 1.992 | 270
631 | 2022-12-21 10:32 | 10.4 | 20.7 | 36.8 | 34.6 | 1.994 | 798
632 | 2022-12-21 10:33 | 10.4 | 20.7 | 36.6 | 34.5 | 1.993 | 209
633 | 2022-12-21 10:34 | 10.1 | 20.9 | 36.4 | 34.4 | 1.997 | 815
634 | 2022-12-21 10:35 | 9.9 | 21.1 | 36.8 | 34.3 | 1.993 | 851
635 | 2022-12-21 10:36 | 10 | 21.1 | 37.1 | 34.6 | 1.997 | 873
636 | 2022-12-21 10:37 | 10.4 | 21.3 | 37.4 | 34.9 | 1.995 | 882
637 | 2022-12-21 10:38 | 10.4 | 21.6 | 37.8 | 35.1 | 1.993 | 858
638 | 2022-12-21 10:39 | 10.4 | 21.6 | 38.1 | 35.4 | 1.992 | 919
639 | 2022-12-21 10:40 | 10.6 | 21.6 | 38.4 | 35.7 | 1.999 | 927
640 | 2022-12-21 10:41 | 10.9 | 21.7 | 38.7 | 36 | 1.997 | 886
641 | 2022-12-21 10:42 | 11.1 | 21.8 | 38.8 | 36.2 | 2 | 899
642 | 2022-12-21 10:43 | 11.2 | 21.8 | 38.5 | 36.3 | 2.005 | 783
643 | 2022-12-21 10:44 | 10.8 | 21.9 | 38.5 | 36.1 | 1.995 | 251
644 | 2022-12-21 10:45 | 10.6 | 21.8 | 38.3 | 36 | 2.001 | 283
645 | 2022-12-21 10:46 | 10.4 | 21.9 | 38.1 | 35.9 | 2.003 | 811
646 | 2022-12-21 10:47 | 10.6 | 21.9 | 38 | 35.7 | 1.999 | 876
647 | 2022-12-21 10:48 | 11 | 22 | 37.7 | 35.6 | 1.995 | 857
648 | 2022-12-21 10:49 | 11.1 | 21.9 | 37.7 | 35.4 | 1.995 | 593
649 | 2022-12-21 10:50 | 10.5 | 22 | 37.4 | 35.3 | 1.992 | 833
650 | 2022-12-21 10:51 | 10.4 | 21.9 | 37.2 | 35.1 | 1.998 | 231
651 | 2022-12-21 10:52 | 10.9 | 21.9 | 37.1 | 34.9 | 1.997 | 822
652 | 2022-12-21 10:53 | 11.1 | 21.9 | 36.9 | 35 | 2.001 | 774
653 | 2022-12-21 10:54 | 10.8 | 21.8 | 36.8 | 35.4 | 1.991 | 781
654 | 2022-12-21 10:55 | 11 | 21.5 | 36.7 | 35.3 | 1.993 | 822
655 | 2022-12-21 10:56 | 11.3 | 21.3 | 37 | 35.3 | 1.984 | 737
656 | 2022-12-21 10:57 | 11.3 | 21.1 | 37.1 | 35.5 | 1.832 | 808
657 | 2022-12-21 10:58 | 11.1 | 21 | 37 | 35.5 | 1.833 | 832
658 | 2022-12-21 10:59 | 10.3 | 20.9 | 37 | 35.4 | 1.83 | 754
659 | 2022-12-21 11:00 | 10.5 | 20.9 | 36.8 | 35.3 | 1.827 | 840
660 | 2022-12-21 11:01 | 11.1 | 20.9 | 36.8 | 35.2 | 1.837 | 726
661 | 2022-12-21 11:02 | 11.6 | 20.8 | 36.7 | 35.2 | 1.829 | 837
662 | 2022-12-21 11:03 | 11.3 | 20.7 | 36.7 | 35.1 | 1.833 | 846
663 | 2022-12-21 11:04 | 11.4 | 20.7 | 36.7 | 35.1 | 1.826 | 853
664 | 2022-12-21 11:05 | 11.5 | 20.7 | 37.2 | 35.2 | 1.829 | 801
665 | 2022-12-21 11:06 | 11 | 20.8 | 37.6 | 35.7 | 1.826 | 869
666 | 2022-12-21 11:07 | 10.8 | 20.7 | 37.9 | 36 | 1.835 | 876
667 | 2022-12-21 11:08 | 11.4 | 20.7 | 38.3 | 36.3 | 1.834 | 867
668 | 2022-12-21 11:09 | 11.5 | 20.6 | 38.7 | 36.6 | 1.833 | 416
669 | 2022-12-21 11:10 | 11.3 | 20.6 | 39 | 37 | 1.831 | 418
670 | 2022-12-21 11:11 | 11 | 20.6 | 39.3 | 37.3 | 1.83 | 868
671 | 2022-12-21 11:12 | 10.9 | 20.5 | 39.7 | 37.5 | 1.837 | 692
672 | 2022-12-21 11:13 | 10.7 | 20.6 | 40.1 | 38 | 1.829 | 799
673 | 2022-12-21 11:14 | 10.9 | 20.5 | 40.4 | 38.3 | 1.831 | 869
674 | 2022-12-21 11:15 | 10.8 | 20.6 | 40.8 | 38.6 | 1.837 | 792
675 | 2022-12-21 11:16 | 11.4 | 20.6 | 41 | 38.9 | 1.839 | 262
676 | 2022-12-21 11:17 | 10.8 | 20.6 | 40.9 | 39.1 | 1.835 | 861
677 | 2022-12-21 11:18 | 10.9 | 20.8 | 40.8 | 38.8 | 1.995 | 889
678 | 2022-12-21 11:19 | 11.1 | 20.9 | 40.6 | 37.5 | 2.005 | 254
679 | 2022-12-21 11:20 | 11.3 | 21.1 | 40.4 | 37.9 | 1.997 | 893
680 | 2022-12-21 11:21 | 10.8 | 21.4 | 40 | 37.7 | 1.999 | 855
681 | 2022-12-21 11:22 | 10.8 | 21.6 | 39.9 | 37.4 | 1.999 | 864
682 | 2022-12-21 11:23 | 11.4 | 21.9 | 39.8 | 37.3 | 1.999 | 871
683 | 2022-12-21 11:24 | 11.4 | 22 | 39.6 | 37.2 | 1.997 | 863
684 | 2022-12-21 11:25 | 11.7 | 22.1 | 39.3 | 37 | 1.994 | 865
685 | 2022-12-21 11:26 | 10.9 | 22.2 | 39.2 | 36.8 | 2.003 | 865
686 | 2022-12-21 11:27 | 10.6 | 22.3 | 38.9 | 36.7 | 2 | 854
687 | 2022-12-21 11:28 | 10.9 | 22.3 | 38.8 | 36.7 | 1.994 | 856
688 | 2022-12-21 11:29 | 11.1 | 22.1 | 38.6 | 37.1 | 1.997 | 853
689 | 2022-12-21 11:30 | 11 | 21.8 | 38.5 | 37 | 1.991 | 850
690 | 2022-12-21 11:31 | 11.2 | 21.6 | 38.4 | 36.9 | 1.973 | 852
691 | 2022-12-21 11:32 | 11.5 | 21.4 | 38.3 | 36.7 | 1.83 | 782
692 | 2022-12-21 11:33 | 10.9 | 21.3 | 38.2 | 36.6 | 1.838 | 861
693 | 2022-12-21 11:34 | 11 | 21.3 | 38.1 | 36.5 | 1.835 | 848
694 | 2022-12-21 11:35 | 11.3 | 21.2 | 38.3 | 36.5 | 1.833 | 857
695 | 2022-12-21 11:36 | 11.3 | 21.1 | 38.6 | 36.7 | 1.834 | 856
696 | 2022-12-21 11:37 | 11.7 | 21 | 38.9 | 36.9 | 1.837 | 850
697 | 2022-12-21 11:38 | 11.7 | 21 | 39.3 | 37.3 | 1.829 | 847
698 | 2022-12-21 11:39 | 11.5 | 20.9 | 39.8 | 37.6 | 1.834 | 849
699 | 2022-12-21 11:40 | 11.2 | 21 | 40 | 38 | 1.835 | 846
700 | 2022-12-21 11:41 | 10.9 | 20.9 | 40.4 | 38.2 | 1.84 | 845
701 | 2022-12-21 11:42 | 11.2 | 20.8 | 40.7 | 38.6 | 1.84 | 845
702 | 2022-12-21 11:43 | 11.9 | 20.8 | 41 | 38.9 | 1.837 | 846
703 | 2022-12-21 11:44 | 12 | 20.8 | 40.9 | 39.1 | 1.84 | 847
704 | 2022-12-21 11:45 | 11.9 | 20.8 | 40.9 | 39 | 1.836 | 851
705 | 2022-12-21 11:46 | 11.7 | 20.7 | 40.8 | 38.9 | 1.84 | 849
706 | 2022-12-21 11:47 | 11.8 | 20.7 | 40.7 | 38.9 | 1.836 | 851
707 | 2022-12-21 11:48 | 11.7 | 20.7 | 40.6 | 38.8 | 1.835 | 854
708 | 2022-12-21 11:49 | 11.8 | 20.6 | 40.4 | 38.6 | 1.838 | 855
709 | 2022-12-21 11:50 | 11.8 | 20.6 | 40.3 | 38.5 | 1.83 | 855
710 | 2022-12-21 11:51 | 12.2 | 20.6 | 40.2 | 38.4 | 1.833 | 851
711 | 2022-12-21 11:52 | 12.5 | 20.6 | 40.1 | 38.3 | 1.832 | 853
712 | 2022-12-21 11:53 | 11.6 | 20.6 | 40 | 38.2 | 1.834 | 858
713 | 2022-12-21 11:54 | 11.5 | 20.6 | 39.8 | 38.1 | 1.834 | 859
714 | 2022-12-21 11:55 | 11.8 | 20.6 | 39.7 | 38 | 1.832 | 854
715 | 2022-12-21 11:56 | 11.8 | 20.6 | 39.5 | 37.9 | 1.829 | 769
716 | 2022-12-21 11:57 | 11.5 | 20.6 | 39.4 | 37.7 | 1.84 | 796
717 | 2022-12-21 11:58 | 11.6 | 20.6 | 39 | 37.6 | 1.836 | 855
718 | 2022-12-21 11:59 | 11.9 | 20.6 | 39.1 | 37.2 | 1.837 | 860
719 | 2022-12-21 12:00 | 11.4 | 20.6 | 39 | 37.3 | 1.829 | 864
720 | 2022-12-21 12:01 | 11.9 | 20.6 | 38.8 | 37.2 | 1.83 | 859
721 | 2022-12-21 12:02 | 11.4 | 20.6 | 38.7 | 37.1 | 1.834 | 854
722 | 2022-12-21 12:03 | 11.2 | 20.5 | 38.6 | 37 | 1.828 | 856
723 | 2022-12-21 12:04 | 11.2 | 20.5 | 38.5 | 37.3 | 1.831 | 851
724 | 2022-12-21 12:05 | 11.3 | 20.5 | 38.8 | 37.3 | 1.838 | 858
725 | 2022-12-21 12:06 | 11.6 | 20.6 | 39 | 37.6 | 1.832 | 865
726 | 2022-12-21 12:07 | 12.1 | 20.6 | 39.5 | 37.9 | 1.654 | 859
727 | 2022-12-21 12:08 | 12.4 | 20.8 | 39.7 | 38.2 | 1.746 | 860
728 | 2022-12-21 12:09 | 11.7 | 20.8 | 39.7 | 36.1 | 1.883 | 856
729 | 2022-12-21 12:10 | 11.3 | 20.9 | 39.4 | 37.3 | 1.888 | 836
730 | 2022-12-21 12:11 | 11.1 | 21.1 | 39.3 | 37.3 | 1.888 | 861
731 | 2022-12-21 12:12 | 11.4 | 21.3 | 39 | 37.1 | 1.885 | 842
732 | 2022-12-21 12:13 | 11.9 | 21.6 | 38.9 | 36.9 | 1.883 | 849
733 | 2022-12-21 12:14 | 12.2 | 21.9 | 38.9 | 37.1 | 1.883 | 839
734 | 2022-12-21 12:15 | 12.7 | 22 | 38.7 | 37.4 | 1.98 | 852
735 | 2022-12-21 12:16 | 12.8 | 22.1 | 38.7 | 36 | 2 | 841
736 | 2022-12-21 12:17 | 12.8 | 22.2 | 38.6 | 37 | 1.992 | 850
737 | 2022-12-21 12:18 | 12.9 | 22.2 | 38.4 | 36.9 | 1.983 | 852
738 | 2022-12-21 12:19 | 12.9 | 22.1 | 38.3 | 37.5 | 1.939 | 860
739 | 2022-12-21 12:20 | 13.1 | 21.8 | 38.2 | 37.5 | 1.829 | 866
740 | 2022-12-21 12:21 | 13.5 | 21.6 | 38.3 | 37.3 | 1.522 | 859
741 | 2022-12-21 12:22 | 13.6 | 21.4 | 38.2 | 37.3 | 1.154 | 861
742 | 2022-12-21 12:23 | 13.6 | 21.3 | 38.2 | 37 | 0.977 | 856
743 | 2022-12-21 12:24 | 13.4 | 21.1 | 38.1 | 36.9 | 0.977 | 853
744 | 2022-12-21 12:25 | 13.3 | 21 | 38 | 36.9 | 0.977 | 850
745 | 2022-12-21 12:26 | 13.3 | 20.9 | 37.9 | 36.8 | 0.973 | 847
746 | 2022-12-21 12:27 | 12.5 | 20.9 | 37.9 | 36.7 | 0.973 | 853
747 | 2022-12-21 12:28 | 12.9 | 20.8 | 37.9 | 36.7 | 0.975 | 136
748 | 2022-12-21 12:29 | 12.6 | 20.7 | 37.8 | 36.7 | 0.972 | 203
749 | 2022-12-21 12:30 | 12.4 | 20.7 | 37.7 | 36.6 | 0.976 | 876
750 | 2022-12-21 12:31 | 12.8 | 20.7 | 37.6 | 36.5 | 1.178 | 866
751 | 2022-12-21 12:32 | 12.9 | 20.7 | 37.6 | 34.1 | 1.5 | 881
752 | 2022-12-21 12:33 | 12.8 | 20.7 | 37.5 | 35.9 | 1.497 | 880
753 | 2022-12-21 12:34 | 12.8 | 20.6 | 37.4 | 35.8 | 1.499 | 846
754 | 2022-12-21 12:35 | 12.6 | 20.5 | 37.7 | 35.8 | 1.499 | 857
755 | 2022-12-21 12:36 | 12.6 | 20.6 | 38.2 | 36.2 | 1.505 | 862
756 | 2022-12-21 12:37 | 12.9 | 20.6 | 38.4 | 36.5 | 1.503 | 858
757 | 2022-12-21 12:38 | 12.6 | 20.6 | 38.8 | 36.7 | 1.508 | 838
758 | 2022-12-21 12:39 | 11.9 | 20.6 | 39.1 | 37.7 | 1.501 | 847
759 | 2022-12-21 12:40 | 12.2 | 20.6 | 39.4 | 38.1 | 1.5 | 844
760 | 2022-12-21 12:41 | 12.5 | 20.6 | 39.9 | 38.4 | 1.501 | 854
761 | 2022-12-21 12:42 | 13 | 20.6 | 40.4 | 38.8 | 1.214 | 858
762 | 2022-12-21 12:43 | 13.3 | 20.6 | 40.8 | 38.9 | 1.089 | 861
763 | 2022-12-21 12:44 | 13 | 20.5 | 41.3 | 39.3 | 1.088 | 864
764 | 2022-12-21 12:45 | 13.1 | 20.6 | 41.7 | 39.7 | 1.092 | 863
765 | 2022-12-21 12:46 | 13.1 | 20.6 | 42.1 | 40.1 | 1.094 | 871
766 | 2022-12-21 12:47 | 13.2 | 20.6 | 42.1 | 40.4 | 1.097 | 865
767 | 2022-12-21 12:48 | 13.2 | 20.5 | 41.7 | 40.5 | 1.094 | 875
768 | 2022-12-21 12:49 | 13.3 | 20.5 | 41.8 | 40 | 1.096 | 881
769 | 2022-12-21 12:50 | 13.2 | 20.5 | 41.8 | 40.1 | 1.093 | 886
770 | 2022-12-21 12:51 | 13.5 | 20.5 | 41.6 | 40.1 | 1.088 | 910
771 | 2022-12-21 12:52 | 13.2 | 20.6 | 41.6 | 40 | 1.096 | 914
772 | 2022-12-21 12:53 | 13.9 | 20.7 | 41.5 | 39.9 | 1.274 | 393
773 | 2022-12-21 12:54 | 13.5 | 20.7 | 41.4 | 35.3 | 1.62 | 744
774 | 2022-12-21 12:55 | 12.9 | 20.8 | 41.3 | 38.8 | 1.625 | 881
775 | 2022-12-21 12:56 | 12.6 | 21 | 41 | 38.9 | 1.621 | 998
776 | 2022-12-21 12:57 | 12.4 | 21.3 | 40.8 | 38.5 | 1.619 | 990
777 | 2022-12-21 12:58 | 12.8 | 21.5 | 40.8 | 38.5 | 1.621 | 776
778 | 2022-12-21 12:59 | 12.9 | 21.7 | 40.7 | 38.5 | 1.62 | 385
779 | 2022-12-21 13:00 | 12.9 | 21.9 | 40.5 | 38.4 | 1.625 | 814
780 | 2022-12-21 13:01 | 12.9 | 22 | 40.4 | 38.9 | 1.622 | 296
781 | 2022-12-21 13:02 | 12.8 | 22.1 | 40.2 | 38.9 | 1.624 | 742
782 | 2022-12-21 13:03 | 12.7 | 22.2 | 40.1 | 38.8 | 1.621 | 216
783 | 2022-12-21 13:04 | 12.4 | 22.2 | 40.2 | 38.7 | 0 | 250
784 | 2022-12-21 13:05 | 12.1 | 22 | 40.1 | 38.6 | 0 | 187
785 | 2022-12-21 13:06 | 11.9 | 21.7 | 39.9 | 38.2 | 0 | 198
786 | 2022-12-21 13:07 | 11.4 | 21.4 | 39.7 | 37.8 | 0 | 179
787 | 2022-12-21 13:08 | 11.5 | 21.3 | 39.5 | 37.4 | 0 | 890
788 | 2022-12-21 13:09 | 12.2 | 21.1 | 39.3 | 37.1 | 0 | 880
789 | 2022-12-21 13:10 | 12 | 21 | 39.1 | 36.8 | 0 | 874
790 | 2022-12-21 13:11 | 11.9 | 20.9 | 38.9 | 36.6 | 0 | 870
791 | 2022-12-21 13:12 | 11.7 | 20.9 | 38.8 | 36.3 | 0 | 867
792 | 2022-12-21 13:13 | 12.4 | 20.8 | 38.6 | 36.1 | 0 | 863
793 | 2022-12-21 13:14 | 12.9 | 20.8 | 38.4 | 36.4 | 0 | 863
794 | 2022-12-21 13:15 | 12.7 | 20.7 | 38.7 | 37.3 | 0.892 | 871
795 | 2022-12-21 13:16 | 12.6 | 20.6 | 41.1 | 36.1 | 1.094 | 857
796 | 2022-12-21 13:17 | 12.5 | 20.6 | 40.6 | 39.4 | 1.091 | 836
797 | 2022-12-21 13:18 | 12.4 | 20.6 | 40.6 | 39 | 1.496 | 716
798 | 2022-12-21 13:19 | 12 | 20.6 | 40.3 | 38.4 | 1.517 | 840
799 | 2022-12-21 13:20 | 11.6 | 20.6 | 40.4 | 38.4 | 1.508 | 843
800 | 2022-12-21 13:21 | 11.5 | 20.6 | 40.3 | 38.5 | 1.513 | 837
801 | 2022-12-21 13:22 | 11.5 | 20.6 | 40.3 | 38.4 | 1.514 | 831
802 | 2022-12-21 13:23 | 11.9 | 20.6 | 40.3 | 38.4 | 1.518 | 827
803 | 2022-12-21 13:24 | 12.3 | 20.6 | 40.2 | 38.4 | 1.507 | 829
804 | 2022-12-21 13:25 | 12.4 | 20.6 | 40.1 | 38.3 | 1.51 | 829
805 | 2022-12-21 13:26 | 12.4 | 20.6 | 40 | 38.2 | 1.512 | 825
806 | 2022-12-21 13:27 | 12.5 | 20.7 | 39.9 | 38.1 | 1.513 | 827
807 | 2022-12-21 13:28 | 12.1 | 20.7 | 39.8 | 38 | 1.517 | 827
808 | 2022-12-21 13:29 | 12.2 | 20.5 | 39.7 | 37.9 | 1.511 | 825
809 | 2022-12-21 13:30 | 12.1 | 20.5 | 39.6 | 37.8 | 1.514 | 822
810 | 2022-12-21 13:31 | 11.9 | 20.5 | 39.4 | 37.8 | 1.512 | 821
811 | 2022-12-21 13:32 | 11.8 | 20.6 | 39.3 | 37.6 | 1.509 | 818
812 | 2022-12-21 13:33 | 12 | 20.6 | 39.2 | 37.5 | 1.512 | 815
813 | 2022-12-21 13:34 | 12.1 | 20.5 | 39.1 | 37.4 | 1.512 | 818
814 | 2022-12-21 13:35 | 11.9 | 20.6 | 39.2 | 37.3 | 1.511 | 814
815 | 2022-12-21 13:36 | 11.9 | 20.5 | 39.5 | 37.5 | 1.508 | 812
816 | 2022-12-21 13:37 | 11.8 | 20.5 | 39.9 | 37.8 | 1.51 | 811
817 | 2022-12-21 13:38 | 12.3 | 20.6 | 40.2 | 38.1 | 1.511 | 806
818 | 2022-12-21 13:39 | 11.9 | 20.5 | 40.6 | 38.4 | 1.517 | 804
819 | 2022-12-21 13:40 | 11.6 | 20.5 | 40.9 | 38.8 | 1.509 | 807
820 | 2022-12-21 13:41 | 11.6 | 20.5 | 40.6 | 39 | 1.515 | 806
821 | 2022-12-21 13:42 | 11.2 | 20.5 | 40.6 | 39.4 | 1.514 | 803
822 | 2022-12-21 13:43 | 11.5 | 20.6 | 40.4 | 39.3 | 1.514 | 804
823 | 2022-12-21 13:44 | 11.4 | 20.6 | 40.4 | 39.2 | 1.484 | 799
824 | 2022-12-21 13:45 | 11.2 | 20.6 | 40.3 | 39 | 1.095 | 795
825 | 2022-12-21 13:46 | 11.3 | 20.6 | 40.3 | 38.8 | 1.092 | 793
826 | 2022-12-21 13:47 | 11.1 | 20.6 | 40.2 | 38.8 | 1.095 | 792
827 | 2022-12-21 13:48 | 11.6 | 20.6 | 40.2 | 38.7 | 1.092 | 789
828 | 2022-12-21 13:49 | 11.4 | 20.6 | 40.2 | 38.6 | 1.087 | 789
829 | 2022-12-21 13:50 | 11.4 | 20.6 | 40 | 38.6 | 1.093 | 786
830 | 2022-12-21 13:51 | 11.5 | 20.6 | 39.9 | 38.4 | 0 | 784
831 | 2022-12-21 13:52 | 11.9 | 20.6 | 39.9 | 38.3 | 0 | 782
832 | 2022-12-21 13:53 | 11.5 | 20.6 | 39.7 | 38 | 0 | 777
833 | 2022-12-21 13:54 | 12 | 20.6 | 39.5 | 37.6 | 1.092 | 779
834 | 2022-12-21 13:55 | 12.2 | 20.6 | 39.7 | 38.6 | 1.076 | 776
835 | 2022-12-21 13:56 | 12.6 | 20.7 | 39.4 | 39.3 | 1.406 | 770
836 | 2022-12-21 13:57 | 12.3 | 20.7 | 39.6 | 37.8 | 1.667 | 769
837 | 2022-12-21 13:58 | 12 | 20.5 | 39.7 | 35.9 | 1.563 | 766
838 | 2022-12-21 13:59 | 12 | 20.7 | 39.4 | 37.4 | 1.562 | 764
839 | 2022-12-21 14:00 | 11.6 | 21 | 39 | 37.2 | 1.561 | 763
840 | 2022-12-21 14:01 | 11.5 | 21.3 | 39 | 36.9 | 1.556 | 764
841 | 2022-12-21 14:02 | 11.7 | 21.7 | 38.8 | 36.8 | 1.568 | 759
842 | 2022-12-21 14:03 | 11.6 | 21.9 | 38.7 | 36.8 | 1.561 | 756
843 | 2022-12-21 14:04 | 11.8 | 22 | 38.7 | 36.7 | 1.562 | 754
844 | 2022-12-21 14:05 | 11.6 | 22.1 | 38.8 | 36.6 | 1.566 | 750
845 | 2022-12-21 14:06 | 11.8 | 22.2 | 39.3 | 37.6 | 1.568 | 749
846 | 2022-12-21 14:07 | 12.1 | 22 | 39.7 | 38.4 | 1.569 | 749
847 | 2022-12-21 14:08 | 11.8 | 21.6 | 40 | 38.7 | 1.564 | 747
848 | 2022-12-21 14:09 | 11.9 | 21.2 | 40.5 | 39.1 | 1.426 | 747
849 | 2022-12-21 14:10 | 11.8 | 21.1 | 40.8 | 39.2 | 0.978 | 744
850 | 2022-12-21 14:11 | 11.6 | 20.9 | 41.4 | 39.3 | 1.096 | 739
851 | 2022-12-21 14:12 | 11.7 | 20.8 | 41.8 | 36.6 | 1.506 | 733
852 | 2022-12-21 14:13 | 11.6 | 20.8 | 41.8 | 40.2 | 1.515 | 725
853 | 2022-12-21 14:14 | 11.5 | 20.7 | 42 | 40.7 | 1.512 | 724
854 | 2022-12-21 14:15 | 11.7 | 20.7 | 42.5 | 40.8 | 1.509 | 719
855 | 2022-12-21 14:16 | 12 | 20.7 | 42.9 | 41.3 | 1.475 | 717
856 | 2022-12-21 14:17 | 11.9 | 20.7 | 42.9 | 41.4 | 1.093 | 714
857 | 2022-12-21 14:18 | 12 | 20.7 | 42.9 | 41.2 | 1.093 | 713
858 | 2022-12-21 14:19 | 11.7 | 20.7 | 42.6 | 41.1 | 1.096 | 716
859 | 2022-12-21 14:20 | 11.5 | 20.7 | 42.6 | 40.9 | 1.091 | 711
860 | 2022-12-21 14:21 | 12 | 20.8 | 42.5 | 40.9 | 1.097 | 705
861 | 2022-12-21 14:22 | 12 | 20.6 | 42.5 | 40.7 | 1.094 | 703
862 | 2022-12-21 14:23 | 12 | 20.6 | 42.3 | 40.7 | 1.097 | 702
863 | 2022-12-21 14:24 | 12.2 | 20.6 | 42.1 | 40.6 | 1.094 | 699
864 | 2022-12-21 14:25 | 12.3 | 20.6 | 42 | 40.5 | 1.092 | 695
865 | 2022-12-21 14:26 | 12 | 20.6 | 42 | 40.4 | 1.089 | 692
866 | 2022-12-21 14:27 | 12 | 20.6 | 41.9 | 40.4 | 1.09 | 692
867 | 2022-12-21 14:28 | 12 | 20.6 | 41.7 | 40.2 | 1.096 | 687
868 | 2022-12-21 14:29 | 12.2 | 20.6 | 41.7 | 40.1 | 1.095 | 682
869 | 2022-12-21 14:30 | 11.8 | 20.6 | 41.6 | 40 | 1.09 | 683
870 | 2022-12-21 14:31 | 12 | 20.6 | 41.4 | 40 | 1.088 | 680
871 | 2022-12-21 14:32 | 11.9 | 20.6 | 41.4 | 39.8 | 1.089 | 672
872 | 2022-12-21 14:33 | 11.7 | 20.6 | 41.3 | 39.8 | 1.494 | 668
873 | 2022-12-21 14:34 | 12 | 20.6 | 41.5 | 39.1 | 1.503 | 666
874 | 2022-12-21 14:35 | 12 | 20.6 | 41.8 | 39.5 | 1.51 | 664
875 | 2022-12-21 14:36 | 11.8 | 20.5 | 42 | 39.9 | 1.513 | 658
876 | 2022-12-21 14:37 | 11.6 | 20.5 | 42.4 | 40 | 1.511 | 654
877 | 2022-12-21 14:38 | 11.4 | 20.5 | 42.7 | 40.4 | 1.514 | 651
878 | 2022-12-21 14:39 | 11.5 | 20.6 | 43.1 | 41.5 | 1.513 | 647
879 | 2022-12-21 14:40 | 11.3 | 20.5 | 43.4 | 42 | 1.519 | 642
880 | 2022-12-21 14:41 | 11.6 | 20.6 | 43.8 | 42.3 | 1.516 | 645
881 | 2022-12-21 14:42 | 11.7 | 20.6 | 44.4 | 42.8 | 1.514 | 645
882 | 2022-12-21 14:43 | 11.8 | 20.5 | 44.7 | 43.1 | 0 | 639
883 | 2022-12-21 14:44 | 11.7 | 20.5 | 44.5 | 43 | 0 | 633
884 | 2022-12-21 14:45 | 11.5 | 20.5 | 44.2 | 42.5 | 0 | 632
885 | 2022-12-21 14:46 | 12 | 20.4 | 45.6 | 42.3 | 0.96 | 629
886 | 2022-12-21 14:47 | 11.9 | 20.6 | 45.4 | 44.9 | 0 | 626
887 | 2022-12-21 14:48 | 12 | 20.7 | 45.2 | 45 | 0.456 | 627
888 | 2022-12-21 14:49 | 12 | 20.6 | 45.4 | 31.4 | 0.945 | 625
889 | 2022-12-21 14:50 | 12 | 20.6 | 45.2 | 42 | 0.967 | 623
890 | 2022-12-21 14:51 | 11.6 | 20.9 | 45.1 | 42.3 | 0.965 | 619
891 | 2022-12-21 14:52 | 11.2 | 21.2 | 45.1 | 42.3 | 0.965 | 615
892 | 2022-12-21 14:53 | 11.5 | 21.6 | 44.6 | 42.2 | 0.961 | 610
893 | 2022-12-21 14:54 | 11.8 | 21.8 | 44.5 | 41.8 | 1.295 | 611
894 | 2022-12-21 14:55 | 11.9 | 21.9 | 44.3 | 38.8 | 1.638 | 609
895 | 2022-12-21 14:56 | 12 | 22.1 | 44 | 41.4 | 1.649 | 603
896 | 2022-12-21 14:57 | 11.9 | 22.2 | 43.8 | 41.3 | 1.646 | 597
897 | 2022-12-21 14:58 | 11.1 | 22.3 | 43.8 | 41.2 | 1.651 | 596
898 | 2022-12-21 14:59 | 11.4 | 22.2 | 43.7 | 42.4 | 1.646 | 594
899 | 2022-12-21 15:00 | 11.6 | 21.8 | 43.7 | 42.4 | 1.647 | 591
900 | 2022-12-21 15:01 | 11.9 | 21.6 | 43.8 | 42.4 | 1.621 | 588
901 | 2022-12-21 15:02 | 11.6 | 21.4 | 43.7 | 42.3 | 1.255 | 581
902 | 2022-12-21 15:03 | 11.7 | 21.3 | 43.6 | 41.9 | 1.098 | 576
903 | 2022-12-21 15:04 | 11.7 | 21.1 | 43.6 | 41.8 | 1.101 | 577
904 | 2022-12-21 15:05 | 11.8 | 21.1 | 43.5 | 41.8 | 1.097 | 573
905 | 2022-12-21 15:06 | 11.8 | 21.1 | 43.4 | 41.7 | 1.103 | 569
906 | 2022-12-21 15:07 | 11.7 | 21.1 | 43.2 | 41.6 | 1.101 | 565
907 | 2022-12-21 15:08 | 11.7 | 21 | 43.1 | 40.2 | 1.521 | 562
908 | 2022-12-21 15:09 | 12 | 21 | 42.9 | 40.9 | 1.528 | 559
909 | 2022-12-21 15:10 | 12.1 | 21 | 42.8 | 41.7 | 1.526 | 556
910 | 2022-12-21 15:11 | 12.2 | 21 | 42.6 | 41.6 | 1.527 | 554
911 | 2022-12-21 15:12 | 11.9 | 21 | 42.6 | 41.5 | 1.528 | 546
912 | 2022-12-21 15:13 | 11.6 | 20.9 | 42.5 | 41.5 | 1.518 | 544
913 | 2022-12-21 15:14 | 11.7 | 20.9 | 42.4 | 41.3 | 1.47 | 541
914 | 2022-12-21 15:15 | 11.3 | 20.9 | 42.4 | 41.2 | 1.294 | 537
915 | 2022-12-21 15:16 | 11.7 | 20.9 | 42.3 | 41.1 | 0.988 | 533
916 | 2022-12-21 15:17 | 11.7 | 20.8 | 42.3 | 40.8 | 0.986 | 531
917 | 2022-12-21 15:18 | 11.8 | 20.8 | 42.3 | 40.7 | 0 | 527
918 | 2022-12-21 15:19 | 12 | 20.8 | 42.2 | 40.5 | 0 | 524
919 | 2022-12-21 15:20 | 12.1 | 20.8 | 41.9 | 40.1 | 0 | 521
920 | 2022-12-21 15:21 | 12 | 20.7 | 41.6 | 39.7 | 0 | 518
921 | 2022-12-21 15:22 | 11.8 | 20.7 | 41.4 | 39.3 | 0 | 516
922 | 2022-12-21 15:23 | 11.7 | 20.7 | 41.1 | 38.9 | 0 | 511
923 | 2022-12-21 15:24 | 12.1 | 20.7 | 40.9 | 38.5 | 0 | 508
924 | 2022-12-21 15:25 | 11.8 | 20.8 | 40.6 | 38.3 | 0 | 502
925 | 2022-12-21 15:26 | 11.7 | 20.7 | 41.5 | 39 | 0.998 | 498
926 | 2022-12-21 15:27 | 11.7 | 20.8 | 41.9 | 39.3 | 1.103 | 494
927 | 2022-12-21 15:28 | 11.4 | 20.8 | 41.4 | 40 | 1.1 | 491
928 | 2022-12-21 15:29 | 11.4 | 20.7 | 41.5 | 39.8 | 1.096 | 487
929 | 2022-12-21 15:30 | 11.2 | 20.8 | 41.3 | 39.8 | 1.1 | 482
930 | 2022-12-21 15:31 | 11.3 | 20.8 | 41.2 | 39.6 | 1.098 | 474
931 | 2022-12-21 15:32 | 11 | 20.8 | 41.2 | 39.6 | 1.097 | 459
932 | 2022-12-21 15:33 | 11.1 | 20.7 | 41.2 | 39.6 | 1.096 | 433
933 | 2022-12-21 15:34 | 11.2 | 20.8 | 41 | 39.5 | 1.097 | 462
934 | 2022-12-21 15:35 | 11.4 | 20.7 | 41 | 39.4 | 1.102 | 459
935 | 2022-12-21 15:36 | 11.7 | 20.7 | 40.8 | 39.4 | 1.097 | 457
936 | 2022-12-21 15:37 | 11.5 | 20.8 | 40.8 | 39.2 | 1.097 | 453
937 | 2022-12-21 15:38 | 11.4 | 20.7 | 40.7 | 39.2 | 1.101 | 443
938 | 2022-12-21 15:39 | 11.3 | 20.7 | 40.6 | 39.1 | 1.097 | 435
939 | 2022-12-21 15:40 | 11.3 | 20.7 | 40.5 | 39 | 1.098 | 428
940 | 2022-12-21 15:41 | 11.4 | 20.7 | 40.4 | 38.9 | 1.097 | 426
941 | 2022-12-21 15:42 | 11.4 | 20.7 | 40.3 | 38.8 | 1.097 | 428
942 | 2022-12-21 15:43 | 11.3 | 20.7 | 40.3 | 38.8 | 1.1 | 424
943 | 2022-12-21 15:44 | 11.4 | 20.7 | 40.2 | 38.7 | 1.1 | 419
944 | 2022-12-21 15:45 | 11.1 | 20.7 | 40.1 | 38.6 | 0 | 415
945 | 2022-12-21 15:46 | 11.1 | 20.7 | 40 | 38.5 | 0 | 410
946 | 2022-12-21 15:47 | 11.1 | 20.6 | 39.7 | 38.1 | 0 | 406
947 | 2022-12-21 15:48 | 11.2 | 20.7 | 39.5 | 37.7 | 0 | 400
948 | 2022-12-21 15:49 | 11.2 | 20.6 | 39.2 | 37.3 | 0 | 392
949 | 2022-12-21 15:50 | 11 | 20.7 | 39 | 36.9 | 0 | 387
950 | 2022-12-21 15:51 | 10.8 | 20.6 | 38.8 | 36.5 | 0 | 383
951 | 2022-12-21 15:52 | 10.6 | 20.6 | 38.5 | 36.2 | 0 | 379
952 | 2022-12-21 15:53 | 10.9 | 20.6 | 38.3 | 35.8 | 0 | 375
953 | 2022-12-21 15:54 | 10.7 | 20.6 | 38.1 | 35.4 | 0 | 371
954 | 2022-12-21 15:55 | 10.7 | 20.5 | 37.8 | 35.1 | 0.067 | 367
955 | 2022-12-21 15:56 | 10.8 | 20.5 | 37.6 | 36.2 | 0 | 363
956 | 2022-12-21 15:57 | 11.1 | 20.6 | 37.3 | 35.7 | 0 | 358
957 | 2022-12-21 15:58 | 10.9 | 20.6 | 37.2 | 37 | 0.514 | 354
958 | 2022-12-21 15:59 | 11.1 | 20.6 | 39.5 | 32.4 | 0.941 | 348
959 | 2022-12-21 16:00 | 10.9 | 20.7 | 39.1 | 37.1 | 0.956 | 343
960 | 2022-12-21 16:01 | 10.8 | 20.9 | 39 | 36.8 | 0.956 | 336
961 | 2022-12-21 16:02 | 10.8 | 21.3 | 39 | 36.9 | 0.954 | 332
962 | 2022-12-21 16:03 | 11 | 21.6 | 38.5 | 36.8 | 0.955 | 328
963 | 2022-12-21 16:04 | 10.7 | 21.9 | 39 | 36.5 | 1.17 | 320
964 | 2022-12-21 16:05 | 10.6 | 22 | 39.4 | 35 | 1.621 | 315
965 | 2022-12-21 16:06 | 10.3 | 22.2 | 39.6 | 37.1 | 1.638 | 311
966 | 2022-12-21 16:07 | 10.4 | 22.3 | 39.9 | 38.4 | 1.639 | 306
967 | 2022-12-21 16:08 | 10.2 | 22 | 40.2 | 38.8 | 1.633 | 301
968 | 2022-12-21 16:09 | 9.8 | 21.7 | 40.8 | 39.2 | 1.627 | 296
969 | 2022-12-21 16:10 | 9.8 | 21.5 | 41.2 | 39.6 | 1.436 | 290
970 | 2022-12-21 16:11 | 9.7 | 21.3 | 41.5 | 39.6 | 1.091 | 285
971 | 2022-12-21 16:12 | 9.8 | 21.2 | 41.9 | 39.9 | 1.099 | 278
972 | 2022-12-21 16:13 | 9.6 | 21.1 | 42.3 | 40.2 | 1.096 | 274
973 | 2022-12-21 16:14 | 9.6 | 21.1 | 41.7 | 40.4 | 1.091 | 268
974 | 2022-12-21 16:15 | 9.6 | 21 | 41.9 | 40 | 1.096 | 258
975 | 2022-12-21 16:16 | 9.6 | 21.1 | 41.6 | 40.3 | 1.094 | 243
976 | 2022-12-21 16:17 | 9.6 | 21 | 41.6 | 39.9 | 1.095 | 215
977 | 2022-12-21 16:18 | 9.5 | 21 | 41.5 | 39.9 | 1.092 | 205
978 | 2022-12-21 16:19 | 9.4 | 21 | 41.4 | 39.8 | 0 | 110
979 | 2022-12-21 16:20 | 9.4 | 21 | 41.3 | 39.6 | 0 | 66
980 | 2022-12-21 16:21 | 9.4 | 21 | 41 | 39.2 | 0 | 144
981 | 2022-12-21 16:22 | 9.3 | 20.9 | 40.7 | 38.8 | 0 | 192
982 | 2022-12-21 16:23 | 9.2 | 20.8 | 40.4 | 38.3 | 0 | 156
983 | 2022-12-21 16:24 | 9.4 | 20.8 | 40.2 | 37.9 | 0 | 194
984 | 2022-12-21 16:25 | 9.2 | 20.7 | 39.9 | 37.4 | 0 | 206
985 | 2022-12-21 16:26 | 9.2 | 20.8 | 39.6 | 37 | 0 | 201
986 | 2022-12-21 16:27 | 9.2 | 20.8 | 39.4 | 36.6 | 0 | 194
987 | 2022-12-21 16:28 | 9.2 | 20.8 | 39.1 | 36.2 | 0 | 188
988 | 2022-12-21 16:29 | 9.3 | 20.7 | 38.8 | 37.2 | 0 | 181
989 | 2022-12-21 16:30 | 9.3 | 20.7 | 38.6 | 36.7 | 0 | 175
990 | 2022-12-21 16:31 | 9.3 | 20.7 | 38.3 | 36.4 | 0 | 167
991 | 2022-12-21 16:32 | 9 | 20.6 | 39.6 | 37.2 | 0.921 | 154
992 | 2022-12-21 16:33 | 8.9 | 20.6 | 40.8 | 36.8 | 0.981 | 152
993 | 2022-12-21 16:34 | 8.9 | 20.6 | 40.1 | 39.1 | 0.982 | 148
994 | 2022-12-21 16:35 | 8.8 | 20.6 | 40.4 | 38.6 | 1.433 | 143
995 | 2022-12-21 16:36 | 8.8 | 20.5 | 40.2 | 38.1 | 1.519 | 116
996 | 2022-12-21 16:37 | 9 | 20.4 | 40.3 | 38.2 | 1.513 | 79
997 | 2022-12-21 16:38 | 8.9 | 20.4 | 40.2 | 38.3 | 1.518 | 50
998 | 2022-12-21 16:39 | 9 | 20.4 | 40.2 | 38.3 | 1.52 | 41
999 | 2022-12-21 16:40 | 9 | 20.3 | 40.2 | 38.3 | 1.517 | 29
1000 | 2022-12-21 16:41 | 9 | 20.3 | 40.1 | 38.3 | 1.514 | 27
1001 | 2022-12-21 16:42 | 9 | 20.3 | 40.1 | 38.2 | 1.521 | 26
1002 | 2022-12-21 16:43 | 8.9 | 20.4 | 40.1 | 38.2 | 1.541 | 24
1003 | 2022-12-21 16:44 | 8.8 | 20.5 | 40 | 35.4 | 1.844 | 23
1004 | 2022-12-21 16:45 | 9 | 20.5 | 39.8 | 37.3 | 1.85 | 22
1005 | 2022-12-21 16:46 | 8.8 | 20.6 | 39.4 | 37.2 | 1.851 | 22
1006 | 2022-12-21 16:47 | 8.9 | 21 | 39.2 | 36.8 | 1.845 | 21
1007 | 2022-12-21 16:48 | 8.8 | 21.3 | 39.1 | 36.7 | 1.847 | 20
1008 | 2022-12-21 16:49 | 8.7 | 21.5 | 38.9 | 36.6 | 1.847 | 19
1009 | 2022-12-21 16:50 | 8.7 | 21.7 | 38.7 | 36.4 | 1.843 | 18
1010 | 2022-12-21 16:51 | 8.8 | 21.7 | 38.6 | 36.3 | 1.853 | 18
1011 | 2022-12-21 16:52 | 8.5 | 21.8 | 38.4 | 36.2 | 1.85 | 17
1012 | 2022-12-21 16:53 | 8.5 | 21.9 | 38.2 | 36 | 1.85 | 16
1013 | 2022-12-21 16:54 | 8.4 | 21.9 | 38.1 | 36.6 | 1.848 | 15
1014 | 2022-12-21 16:55 | 8.6 | 21.6 | 37.9 | 36.5 | 1.848 | 14
1015 | 2022-12-21 16:56 | 8.5 | 21.3 | 37.9 | 36.4 | 1.843 | 14
1016 | 2022-12-21 16:57 | 8.5 | 21.1 | 37.8 | 36.4 | 1.697 | 13
1017 | 2022-12-21 16:58 | 8.5 | 21 | 37.7 | 36 | 1.511 | 12
1018 | 2022-12-21 16:59 | 8.6 | 20.8 | 37.6 | 36 | 1.512 | 11
1019 | 2022-12-21 17:00 | 8.4 | 20.8 | 37.4 | 35.9 | 1.511 | 10
1020 | 2022-12-21 17:01 | 8.1 | 20.7 | 37.3 | 35.8 | 1.511 | 9
1021 | 2022-12-21 17:02 | 8.1 | 20.6 | 37.2 | 35.7 | 1.509 | 8
1022 | 2022-12-21 17:03 | 7.9 | 20.6 | 37.1 | 35.6 | 1.508 | 8
1023 | 2022-12-21 17:04 | 7.8 | 20.5 | 37.1 | 35.4 | 1.512 | 7
1024 | 2022-12-21 17:05 | 7.9 | 20.5 | 37.2 | 36 | 1.516 | 6
1025 | 2022-12-21 17:06 | 7.8 | 20.5 | 37.6 | 36.2 | 1.509 | 5
1026 | 2022-12-21 17:07 | 7.6 | 20.5 | 38 | 36.6 | 1.497 | 4
1027 | 2022-12-21 17:08 | 7.6 | 20.5 | 38.3 | 37 | 1.115 | 3
1028 | 2022-12-21 17:09 | 7.6 | 20.5 | 38.7 | 36.9 | 1.088 | 3
1029 | 2022-12-21 17:10 | 7.3 | 20.4 | 39.1 | 37.2 | 1.092 | 2
1030 | 2022-12-21 17:11 | 7.3 | 20.4 | 39.6 | 37.6 | 1.096 | 1
1031 | 2022-12-21 17:12 | 7.3 | 20.5 | 40.1 | 38 | 1.093 | 1
1032 | 2022-12-21 17:13 | 7.3 | 20.4 | 39.6 | 38.5 | 1.09 | 0
1033 | 2022-12-21 17:14 | 7.3 | 20.4 | 39.5 | 38 | 1.095 | 0
1034 | 2022-12-21 17:15 | 7.5 | 20.4 | 39.5 | 38 | 1.092 | 0
1035 | 2022-12-21 17:16 | 7.5 | 20.3 | 39.2 | 37.9 | 1.09 | 0
1036 | 2022-12-21 17:17 | 7.9 | 20.4 | 39.3 | 37.7 | 1.093 | 0
1037 | 2022-12-21 17:18 | 7.9 | 20.5 | 39.2 | 37.7 | 1.307 | 0
1038 | 2022-12-21 17:19 | 7.8 | 20.5 | 39.1 | 35.6 | 1.629 | 0
1039 | 2022-12-21 17:20 | 7.8 | 20.5 | 39 | 36.8 | 1.637 | 0
1040 | 2022-12-21 17:21 | 7.7 | 20.8 | 38.7 | 36.3 | 1.838 | 0
1041 | 2022-12-21 17:22 | 7.7 | 21.1 | 38.8 | 36.8 | 1.847 | 0
1042 | 2022-12-21 17:23 | 7.7 | 21.3 | 38.6 | 37 | 1.847 | 0
1043 | 2022-12-21 17:24 | 7.7 | 21.5 | 38.5 | 36.7 | 1.848 | 0
1044 | 2022-12-21 17:25 | 7.2 | 21.6 | 38.5 | 36.7 | 1.842 | 0
1045 | 2022-12-21 17:26 | 7 | 21.5 | 38.3 | 36.6 | 1.807 | 0
1046 | 2022-12-21 17:27 | 7.1 | 21.7 | 38.2 | 36.5 | 1.713 | 0
1047 | 2022-12-21 17:28 | 7.1 | 21.8 | 38.1 | 36.2 | 1.564 | 0
1048 | 2022-12-21 17:29 | 7.4 | 21.7 | 37.9 | 36 | 1.57 | 0
1049 | 2022-12-21 17:30 | 7.2 | 21.8 | 37.8 | 35.9 | 1.562 | 0
1050 | 2022-12-21 17:31 | 7.3 | 21.8 | 37.7 | 36 | 1.567 | 0
1051 | 2022-12-21 17:32 | 7.4 | 21.6 | 37.5 | 36.7 | 1.567 | 0
1052 | 2022-12-21 17:33 | 7.3 | 21.2 | 37.5 | 36.6 | 1.561 | 0
1053 | 2022-12-21 17:34 | 7.5 | 20.9 | 37.5 | 36.6 | 1.547 | 0
1054 | 2022-12-21 17:35 | 7.2 | 20.7 | 37.7 | 36.6 | 1.184 | 0
1055 | 2022-12-21 17:36 | 7 | 20.6 | 38.2 | 36.5 | 1.285 | 0
1056 | 2022-12-21 17:37 | 7.1 | 20.5 | 38.6 | 35.8 | 1.505 | 0
1057 | 2022-12-21 17:38 | 7.1 | 20.5 | 39 | 36.9 | 1.517 | 0
1058 | 2022-12-21 17:39 | 6.8 | 20.5 | 39.3 | 37.2 | 1.511 | 0
1059 | 2022-12-21 17:40 | 6.8 | 20.4 | 39.5 | 37.5 | 1.513 | 0
1060 | 2022-12-21 17:41 | 6.6 | 20.4 | 39.9 | 38.3 | 1.512 | 0
1061 | 2022-12-21 17:42 | 6.4 | 20.4 | 40.2 | 38.8 | 1.515 | 0
1062 | 2022-12-21 17:43 | 6.2 | 20.4 | 40.2 | 38.9 | 1.508 | 0
1063 | 2022-12-21 17:44 | 6.1 | 20.4 | 40.2 | 39 | 1.475 | 0
1064 | 2022-12-21 17:45 | 6.1 | 20.3 | 40.1 | 38.8 | 1.092 | 0
1065 | 2022-12-21 17:46 | 6.1 | 20.4 | 40.1 | 38.5 | 1.099 | 0
1066 | 2022-12-21 17:47 | 6.2 | 20.4 | 40 | 38.5 | 1.09 | 0
1067 | 2022-12-21 17:48 | 6.2 | 20.3 | 39.9 | 38.4 | 1.09 | 0
1068 | 2022-12-21 17:49 | 6.3 | 20.3 | 39.8 | 38.3 | 1.094 | 0
1069 | 2022-12-21 17:50 | 6.7 | 20.4 | 39.7 | 38.2 | 1.357 | 0
1070 | 2022-12-21 17:51 | 6.5 | 20.5 | 39.6 | 34.9 | 1.629 | 0
1071 | 2022-12-21 17:52 | 6.5 | 20.5 | 39.5 | 37.2 | 1.639 | 0
1072 | 2022-12-21 17:53 | 6.6 | 20.7 | 39.2 | 37.2 | 1.635 | 0
1073 | 2022-12-21 17:54 | 6.4 | 21 | 39 | 36.9 | 1.633 | 0
1074 | 2022-12-21 17:55 | 6.2 | 21.4 | 39 | 36.9 | 1.636 | 0
1075 | 2022-12-21 17:56 | 6.2 | 21.5 | 38.8 | 36.8 | 1.63 | 0
1076 | 2022-12-21 17:57 | 6.3 | 21.7 | 38.7 | 36.7 | 1.629 | 0
1077 | 2022-12-21 17:58 | 6.3 | 21.1 | 38.5 | 36.5 | 1.63 | 0
1078 | 2022-12-21 17:59 | 6.4 | 21.9 | 38.3 | 36.4 | 1.766 | 0
1079 | 2022-12-21 18:00 | 6.2 | 21.9 | 38.2 | 35.4 | 1.843 | 0
1080 | 2022-12-21 18:01 | 6.2 | 21.6 | 38 | 36.6 | 1.842 | 0
1081 | 2022-12-21 18:02 | 6.2 | 20.9 | 37.9 | 36.5 | 1.842 | 0
1082 | 2022-12-21 18:03 | 6.7 | 21 | 37.9 | 36.4 | 1.788 | 0
1083 | 2022-12-21 18:04 | 6.8 | 20.7 | 37.9 | 36.2 | 1.503 | 0
1084 | 2022-12-21 18:05 | 6.8 | 20.6 | 38 | 36.2 | 1.508 | 0
1085 | 2022-12-21 18:06 | 6.9 | 20.5 | 38.4 | 36.3 | 1.509 | 0
1086 | 2022-12-21 18:07 | 7 | 20.5 | 38.8 | 36.7 | 1.508 | 0
1087 | 2022-12-21 18:08 | 6.7 | 20.4 | 39.1 | 37 | 1.506 | 0
1088 | 2022-12-21 18:09 | 6.7 | 20.4 | 39.6 | 37.4 | 1.51 | 0
1089 | 2022-12-21 18:10 | 6.5 | 20.5 | 39.8 | 37.8 | 1.52 | 0
1090 | 2022-12-21 18:11 | 6.7 | 20.5 | 39.8 | 38 | 1.513 | 0
1091 | 2022-12-21 18:12 | 6.8 | 20.4 | 39.8 | 38 | 1.52 | 0
1092 | 2022-12-21 18:13 | 6.9 | 20.3 | 39.6 | 37.9 | 1.511 | 0
1093 | 2022-12-21 18:14 | 6.9 | 20.4 | 39.6 | 37.7 | 1.509 | 0
1094 | 2022-12-21 18:15 | 6.6 | 20.3 | 39.5 | 37.7 | 1.517 | 0
1095 | 2022-12-21 18:16 | 6.5 | 20.3 | 39.3 | 38.2 | 1.511 | 0
1096 | 2022-12-21 18:17 | 6.2 | 20.3 | 39.3 | 38.1 | 1.515 | 0
1097 | 2022-12-21 18:18 | 6.3 | 20.4 | 39.2 | 38.1 | 1.5 | 0
1098 | 2022-12-21 18:19 | 6.4 | 20.5 | 39.1 | 37.9 | 1.697 | 0
1099 | 2022-12-21 18:20 | 6.2 | 20.5 | 39.1 | 36.5 | 1.63 | 0
1100 | 2022-12-21 18:21 | 5.9 | 20.6 | 39 | 36.8 | 1.627 | 0
1101 | 2022-12-21 18:22 | 6.4 | 20.9 | 38.7 | 36.8 | 1.627 | 0
1102 | 2022-12-21 18:23 | 6.4 | 21.1 | 38.5 | 36.5 | 1.628 | 0
1103 | 2022-12-21 18:24 | 6 | 21.3 | 38.4 | 37 | 1.629 | 0
1104 | 2022-12-21 18:25 | 5.8 | 21.5 | 38.2 | 37 | 1.629 | 0
1105 | 2022-12-21 18:26 | 5.6 | 21.6 | 38.2 | 36.8 | 1.628 | 0
1106 | 2022-12-21 18:27 | 5.5 | 21.6 | 38.1 | 36.8 | 1.62 | 0
1107 | 2022-12-21 18:28 | 5.4 | 21.6 | 38 | 36.7 | 1.585 | 0
1108 | 2022-12-21 18:29 | 5.4 | 21.6 | 38 | 36.6 | 1.402 | 0
1109 | 2022-12-21 18:30 | 5.4 | 21.7 | 37.9 | 36.3 | 0.955 | 0
1110 | 2022-12-21 18:31 | 5.3 | 21.6 | 37.8 | 35.8 | 0.952 | 0
1111 | 2022-12-21 18:32 | 5.2 | 21.7 | 37.7 | 35.7 | 0.947 | 0
1112 | 2022-12-21 18:33 | 5.3 | 21.7 | 37.5 | 35.7 | 1.538 | 0
1113 | 2022-12-21 18:34 | 5.3 | 21.7 | 37.4 | 35 | 1.562 | 0
1114 | 2022-12-21 18:35 | 5.3 | 21.6 | 37.6 | 35.4 | 1.568 | 0
1115 | 2022-12-21 18:36 | 5.2 | 21.6 | 37.8 | 35.7 | 1.565 | 0
1116 | 2022-12-21 18:37 | 5.1 | 21.7 | 38.2 | 35.9 | 1.829 | 0
1117 | 2022-12-21 18:38 | 5.1 | 21.7 | 38.6 | 36.5 | 1.845 | 0
1118 | 2022-12-21 18:39 | 5 | 21.3 | 39 | 37 | 1.843 | 0
1119 | 2022-12-21 18:40 | 4.9 | 21 | 39.4 | 37.4 | 1.841 | 0
1120 | 2022-12-21 18:41 | 4.9 | 20.8 | 39.8 | 37.8 | 1.791 | 0
1121 | 2022-12-21 18:42 | 4.9 | 20.5 | 40.1 | 38 | 1.515 | 0
1122 | 2022-12-21 18:43 | 4.9 | 20.5 | 40.4 | 38.3 | 1.517 | 0
1123 | 2022-12-21 18:44 | 5 | 20.3 | 40.6 | 38.5 | 1.515 | 0
1124 | 2022-12-21 18:45 | 5 | 20.3 | 40.9 | 38.7 | 1.807 | 0
1125 | 2022-12-21 18:46 | 4.9 | 20.3 | 41.3 | 37.9 | 1.856 | 0
1126 | 2022-12-21 18:47 | 4.6 | 20.3 | 41.4 | 39.3 | 1.854 | 0
1127 | 2022-12-21 18:48 | 4.8 | 20.2 | 41.1 | 39.3 | 1.856 | 0
1128 | 2022-12-21 18:49 | 4.8 | 20.3 | 41.2 | 39.6 | 1.856 | 0
1129 | 2022-12-21 18:50 | 4.7 | 20.2 | 41.1 | 39.8 | 1.854 | 0
1130 | 2022-12-21 18:51 | 4.6 | 20.2 | 41.1 | 39.7 | 1.855 | 0
1131 | 2022-12-21 18:52 | 4.7 | 20.3 | 41 | 39.7 | 1.825 | 0
1132 | 2022-12-21 18:53 | 4.6 | 20.5 | 41 | 38.8 | 1.903 | 0
1133 | 2022-12-21 18:54 | 4.6 | 20.5 | 40.8 | 38.5 | 1.905 | 0
1134 | 2022-12-21 18:55 | 4.5 | 20.6 | 40.4 | 38.4 | 1.905 | 0
1135 | 2022-12-21 18:56 | 4.4 | 21 | 40.3 | 38.1 | 1.903 | 0
1136 | 2022-12-21 18:57 | 4.4 | 21.3 | 40.1 | 38 | 1.908 | 0
1137 | 2022-12-21 18:58 | 4.4 | 21.4 | 39.9 | 37.8 | 1.912 | 0
1138 | 2022-12-21 18:59 | 4.5 | 21.6 | 39.8 | 37.7 | 1.91 | 0
1139 | 2022-12-21 19:00 | 4.5 | 21.8 | 39.6 | 37.5 | 1.896 | 0
1140 | 2022-12-21 19:01 | 4.5 | 21.8 | 39.5 | 37.4 | 1.906 | 0
1141 | 2022-12-21 19:02 | 4.4 | 21.9 | 39.3 | 37.3 | 1.905 | 0
1142 | 2022-12-21 19:03 | 4.5 | 21.9 | 39.1 | 37.4 | 1.899 | 0
1143 | 2022-12-21 19:04 | 4.4 | 21.6 | 39 | 37.8 | 1.906 | 0
1144 | 2022-12-21 19:05 | 4.6 | 21.4 | 39.3 | 37.8 | 1.904 | 0
1145 | 2022-12-21 19:06 | 4.5 | 21.1 | 39.7 | 38.1 | 1.888 | 0
1146 | 2022-12-21 19:07 | 4.4 | 20.9 | 40.2 | 38.4 | 1.683 | 0
1147 | 2022-12-21 19:08 | 4.7 | 20.8 | 40.6 | 38 | 1.847 | 0
1148 | 2022-12-21 19:09 | 5 | 20.6 | 40.9 | 38.7 | 1.854 | 0
1149 | 2022-12-21 19:10 | 5.1 | 20.6 | 41.1 | 38.9 | 1.846 | 0
1150 | 2022-12-21 19:11 | 5 | 20.6 | 41.5 | 39.2 | 1.852 | 0
1151 | 2022-12-21 19:12 | 4.8 | 20.4 | 41.7 | 39.5 | 1.855 | 0
1152 | 2022-12-21 19:13 | 4.8 | 20.4 | 41.9 | 39.8 | 1.854 | 0
1153 | 2022-12-21 19:14 | 4.6 | 20.5 | 41.7 | 39.8 | 1.852 | 0
1154 | 2022-12-21 19:15 | 4.4 | 20.4 | 41.6 | 39.7 | 1.854 | 0
1155 | 2022-12-21 19:16 | 4.5 | 20.4 | 41.5 | 39.6 | 1.855 | 0
1156 | 2022-12-21 19:17 | 4.4 | 20.4 | 41.4 | 39.9 | 1.85 | 0
1157 | 2022-12-21 19:18 | 4.3 | 20.3 | 41.3 | 40.1 | 1.853 | 0
1158 | 2022-12-21 19:19 | 4.2 | 20.3 | 41.2 | 40 | 1.859 | 0
1159 | 2022-12-21 19:20 | 4.2 | 20.3 | 41.2 | 40 | 1.847 | 0
1160 | 2022-12-21 19:21 | 4.3 | 20.3 | 41.1 | 39.9 | 1.983 | 0
1161 | 2022-12-21 19:22 | 4.2 | 20.4 | 41 | 38.2 | 1.982 | 0
1162 | 2022-12-21 19:23 | 4.2 | 20.5 | 40.8 | 38.7 | 1.877 | 0
1163 | 2022-12-21 19:24 | 4.3 | 20.7 | 40.5 | 38.8 | 1.872 | 0
1164 | 2022-12-21 19:25 | 4.1 | 20.9 | 40.4 | 38.8 | 1.868 | 0
1165 | 2022-12-21 19:26 | 4.1 | 21.2 | 40.3 | 38.8 | 1.869 | 0
1166 | 2022-12-21 19:27 | 4 | 21.4 | 40.2 | 38.7 | 1.83 | 0
1167 | 2022-12-21 19:28 | 4 | 21.5 | 40.1 | 38.3 | 1.559 | 0
1168 | 2022-12-21 19:29 | 4.1 | 21.6 | 39.9 | 38.3 | 1.551 | 0
1169 | 2022-12-21 19:30 | 4.1 | 21.7 | 39.8 | 38.1 | 1.776 | 0
1170 | 2022-12-21 19:31 | 4 | 21.8 | 39.7 | 36.3 | 1.899 | 0
1171 | 2022-12-21 19:32 | 4.2 | 21.8 | 39.5 | 37.4 | 1.903 | 0
1172 | 2022-12-21 19:33 | 4 | 21.8 | 39.3 | 37.3 | 1.902 | 0
1173 | 2022-12-21 19:34 | 4 | 21.8 | 39.2 | 37.1 | 1.906 | 0
1174 | 2022-12-21 19:35 | 4 | 21.8 | 39.4 | 37.6 | 1.903 | 0
1175 | 2022-12-21 19:36 | 3.9 | 21.6 | 39.8 | 38.1 | 1.905 | 0
1176 | 2022-12-21 19:37 | 4.1 | 21.3 | 40.2 | 38.6 | 1.902 | 0
1177 | 2022-12-21 19:38 | 3.9 | 21.2 | 40.2 | 38.9 | 1.895 | 0
1178 | 2022-12-21 19:39 | 3.8 | 21 | 40.1 | 38.7 | 1.679 | 0
1179 | 2022-12-21 19:40 | 3.8 | 20.9 | 40 | 38.6 | 1.84 | 0
1180 | 2022-12-21 19:41 | 4 | 20.8 | 39.9 | 37.9 | 1.846 | 0
1181 | 2022-12-21 19:42 | 3.9 | 20.7 | 39.7 | 38 | 1.855 | 0
1182 | 2022-12-21 19:43 | 4 | 20.7 | 39.5 | 37.8 | 1.854 | 0
1183 | 2022-12-21 19:44 | 3.8 | 20.6 | 39.4 | 37.6 | 1.853 | 0
1184 | 2022-12-21 19:45 | 4 | 20.6 | 39.3 | 37.6 | 1.847 | 0
1185 | 2022-12-21 19:46 | 3.8 | 20.5 | 39.2 | 37.4 | 1.852 | 0
1186 | 2022-12-21 19:47 | 3.9 | 20.5 | 39.1 | 37.4 | 1.857 | 0
1187 | 2022-12-21 19:48 | 4 | 20.5 | 38.9 | 37.2 | 1.842 | 0
1188 | 2022-12-21 19:49 | 4.1 | 20.5 | 38.8 | 37.1 | 1.845 | 0
1189 | 2022-12-21 19:50 | 3.8 | 20.4 | 38.7 | 37 | 1.842 | 0
1190 | 2022-12-21 19:51 | 3.8 | 20.5 | 38.6 | 36.9 | 1.848 | 0
1191 | 2022-12-21 19:52 | 4.1 | 20.4 | 38.4 | 36.8 | 1.849 | 0
1192 | 2022-12-21 19:53 | 4 | 20.4 | 38.3 | 36.7 | 1.854 | 0
1193 | 2022-12-21 19:54 | 4 | 20.4 | 38.2 | 36.5 | 1.846 | 0
1194 | 2022-12-21 19:55 | 3.8 | 20.4 | 38 | 36.4 | 1.849 | 0
1195 | 2022-12-21 19:56 | 3.9 | 20.4 | 37.9 | 36.3 | 1.84 | 0
1196 | 2022-12-21 19:57 | 3.7 | 20.6 | 37.8 | 36.2 | 1.967 | 0
1197 | 2022-12-21 19:58 | 3.9 | 20.6 | 37.6 | 34.6 | 2.009 | 0
1198 | 2022-12-21 19:59 | 4.1 | 20.6 | 37.4 | 35.3 | 2.015 | 0
1199 | 2022-12-21 20:00 | 4 | 20.8 | 37.1 | 35.1 | 2.006 | 0
1200 | 2022-12-21 20:01 | 4.1 | 21.1 | 37 | 34.8 | 2.008 | 0
1201 | 2022-12-21 20:02 | 4.1 | 21.2 | 36.8 | 34.7 | 2.013 | 0
1202 | 2022-12-21 20:03 | 4 | 21.4 | 36.7 | 34.5 | 2.007 | 0
1203 | 2022-12-21 20:04 | 3.9 | 21.4 | 36.9 | 34.5 | 2.01 | 0
1204 | 2022-12-21 20:05 | 4.1 | 21.6 | 37.4 | 34.7 | 2.007 | 0
1205 | 2022-12-21 20:06 | 4.5 | 21.6 | 37.5 | 35.4 | 2.008 | 0
1206 | 2022-12-21 20:07 | 4.2 | 21.7 | 37.9 | 35.7 | 2.007 | 0
1207 | 2022-12-21 20:08 | 4.3 | 21.7 | 38.2 | 36.1 | 2.007 | 0
1208 | 2022-12-21 20:09 | 4.1 | 21.7 | 38.6 | 36.3 | 2.009 | 0
1209 | 2022-12-21 20:10 | 4 | 21.7 | 38.9 | 36.7 | 2.002 | 0
1210 | 2022-12-21 20:11 | 4.3 | 21.7 | 39.2 | 37 | 1.977 | 0
1211 | 2022-12-21 20:12 | 4.1 | 21.7 | 39.5 | 37.2 | 1.862 | 0
1212 | 2022-12-21 20:13 | 4.1 | 21.6 | 39.8 | 38.3 | 1.876 | 0
1213 | 2022-12-21 20:14 | 4.1 | 21.3 | 40.2 | 38.7 | 1.874 | 0
1214 | 2022-12-21 20:15 | 4.2 | 21 | 40.4 | 39 | 1.864 | 0
1215 | 2022-12-21 20:16 | 4 | 20.8 | 40.4 | 39.2 | 1.768 | 0
1216 | 2022-12-21 20:17 | 4 | 20.7 | 40.4 | 39.6 | 1.582 | 0
1217 | 2022-12-21 20:18 | 4 | 20.6 | 40.3 | 39.7 | 1.585 | 0
1218 | 2022-12-21 20:19 | 3.9 | 20.5 | 40.3 | 39.6 | 1.571 | 0
1219 | 2022-12-21 20:20 | 3.9 | 20.4 | 40.3 | 39.6 | 1.393 | 0
1220 | 2022-12-21 20:21 | 4 | 20.4 | 40.2 | 39.5 | 1.624 | 0
1221 | 2022-12-21 20:22 | 4 | 20.3 | 40.2 | 38.6 | 1.644 | 0
1222 | 2022-12-21 20:23 | 4.1 | 20.3 | 40.1 | 38.7 | 1.641 | 0
1223 | 2022-12-21 20:24 | 3.9 | 20.3 | 39.8 | 38.6 | 1.637 | 0
1224 | 2022-12-21 20:25 | 4 | 20.4 | 39.8 | 38.4 | 1.644 | 0
1225 | 2022-12-21 20:26 | 4 | 20.3 | 39.7 | 38.3 | 1.64 | 0
1226 | 2022-12-21 20:27 | 3.9 | 20.4 | 39.6 | 38.3 | 1.642 | 0
1227 | 2022-12-21 20:28 | 4.1 | 20.4 | 39.5 | 38.2 | 1.644 | 0
1228 | 2022-12-21 20:29 | 3.9 | 20.5 | 39.4 | 36 | 1.958 | 0
1229 | 2022-12-21 20:30 | 4.2 | 20.5 | 39.3 | 35.7 | 2.014 | 0
1230 | 2022-12-21 20:31 | 3.9 | 20.7 | 38.9 | 36.6 | 2.011 | 0
1231 | 2022-12-21 20:32 | 4 | 21 | 38.7 | 36.4 | 2.015 | 0
1232 | 2022-12-21 20:33 | 4 | 21.3 | 38.5 | 36.2 | 2.014 | 0
1233 | 2022-12-21 20:34 | 4 | 21.5 | 38.4 | 36 | 2.013 | 0
1234 | 2022-12-21 20:35 | 3.8 | 21.6 | 38.5 | 36 | 2.011 | 0
1235 | 2022-12-21 20:36 | 3.9 | 21.7 | 38.8 | 36.1 | 2.011 | 0
1236 | 2022-12-21 20:37 | 3.9 | 21.7 | 39.3 | 36.4 | 2.012 | 0
1237 | 2022-12-21 20:38 | 4 | 21.7 | 39.5 | 36.7 | 2.01 | 0
1238 | 2022-12-21 20:39 | 3.9 | 21.8 | 39.8 | 36.9 | 2.015 | 0
1239 | 2022-12-21 20:40 | 3.8 | 21.9 | 40 | 37.2 | 2.02 | 0
1240 | 2022-12-21 20:41 | 4 | 21.8 | 40.3 | 38.2 | 2.009 | 0
1241 | 2022-12-21 20:42 | 3.8 | 21.6 | 40.2 | 38.5 | 2.015 | 0
1242 | 2022-12-21 20:43 | 3.8 | 21.3 | 40.2 | 38.4 | 2.011 | 0
1243 | 2022-12-21 20:44 | 3.9 | 21.2 | 40.1 | 38.4 | 1.971 | 0
1244 | 2022-12-21 20:45 | 4 | 20.9 | 40 | 38.1 | 1.849 | 0
1245 | 2022-12-21 20:46 | 3.9 | 20.8 | 39.9 | 38.1 | 1.848 | 0
1246 | 2022-12-21 20:47 | 3.8 | 20.8 | 39.8 | 38 | 1.849 | 0
1247 | 2022-12-21 20:48 | 4 | 20.7 | 39.7 | 37.9 | 1.851 | 0
1248 | 2022-12-21 20:49 | 4.1 | 20.7 | 39.5 | 37.8 | 1.841 | 0
1249 | 2022-12-21 20:50 | 3.9 | 20.7 | 39.4 | 37.6 | 1.849 | 0
1250 | 2022-12-21 20:51 | 4 | 20.6 | 39.3 | 37.5 | 1.844 | 0
1251 | 2022-12-21 20:52 | 4.1 | 20.6 | 39.1 | 37.4 | 1.847 | 0
1252 | 2022-12-21 20:53 | 3.9 | 20.5 | 39 | 37.3 | 1.847 | 0
1253 | 2022-12-21 20:54 | 3.8 | 20.5 | 38.9 | 37.2 | 1.843 | 0
1254 | 2022-12-21 20:55 | 3.8 | 20.5 | 38.7 | 37.1 | 1.838 | 0
1255 | 2022-12-21 20:56 | 3.9 | 20.5 | 38.6 | 36.9 | 1.844 | 0
1256 | 2022-12-21 20:57 | 3.8 | 20.5 | 38.5 | 37.2 | 1.848 | 0
1257 | 2022-12-21 20:58 | 3.8 | 20.5 | 38.4 | 37.2 | 1.845 | 0
1258 | 2022-12-21 20:59 | 4.2 | 20.4 | 38.3 | 37.1 | 1.843 | 0
1259 | 2022-12-21 21:00 | 4.1 | 20.4 | 38.2 | 37 | 0 | 0
1260 | 2022-12-21 21:01 | 4.1 | 20.4 | 38.1 | 36.9 | 0 | 0
1261 | 2022-12-21 21:02 | 4 | 20.4 | 37.9 | 36.5 | 0 | 0
1262 | 2022-12-21 21:03 | 3.9 | 20.3 | 37.6 | 35.9 | 0 | 0
1263 | 2022-12-21 21:04 | 4 | 20.3 | 37.4 | 35.4 | 0 | 0
1264 | 2022-12-21 21:05 | 4 | 20.3 | 37.1 | 34.8 | 0 | 0
1265 | 2022-12-21 21:06 | 4 | 20.2 | 36.8 | 34.3 | 0 | 0
1266 | 2022-12-21 21:07 | 3.9 | 20.2 | 36.6 | 33.8 | 0 | 0
1267 | 2022-12-21 21:08 | 4 | 20.1 | 36.3 | 33.4 | 0 | 0
1268 | 2022-12-21 21:09 | 3.9 | 20.1 | 36.1 | 32.9 | 0 | 0
1269 | 2022-12-21 21:10 | 4 | 20.1 | 35.8 | 32.5 | 0 | 0
1270 | 2022-12-21 21:11 | 3.9 | 20.1 | 35.5 | 32.1 | 0 | 0
1271 | 2022-12-21 21:12 | 3.8 | 20 | 35.3 | 31.7 | 0 | 0
1272 | 2022-12-21 21:13 | 3.8 | 20 | 35 | 31.3 | 0 | 0
1273 | 2022-12-21 21:14 | 4 | 20 | 34.8 | 30.9 | 0 | 0
1274 | 2022-12-21 21:15 | 3.8 | 20 | 34.5 | 30.5 | 0 | 0
1275 | 2022-12-21 21:16 | 3.9 | 19.9 | 34.3 | 30.2 | 0 | 0
1276 | 2022-12-21 21:17 | 3.9 | 19.9 | 34 | 29.8 | 0 | 0
1277 | 2022-12-21 21:18 | 3.8 | 19.9 | 33.8 | 29.5 | 0 | 0
1278 | 2022-12-21 21:19 | 3.8 | 19.9 | 33.5 | 29.2 | 0 | 0
1279 | 2022-12-21 21:20 | 3.9 | 19.8 | 33.3 | 28.9 | 0 | 0
1280 | 2022-12-21 21:21 | 3.8 | 19.8 | 33.1 | 28.6 | 0 | 0
1281 | 2022-12-21 21:22 | 3.9 | 19.8 | 32.8 | 28.3 | 0 | 0
1282 | 2022-12-21 21:23 | 3.9 | 19.8 | 32.6 | 28 | 0 | 0
1283 | 2022-12-21 21:24 | 4 | 19.8 | 32.3 | 27.7 | 0 | 0
1284 | 2022-12-21 21:25 | 4 | 19.8 | 32.1 | 27.5 | 0 | 0
1285 | 2022-12-21 21:26 | 4 | 19.8 | 31.9 | 27.2 | 0 | 0
1286 | 2022-12-21 21:27 | 4 | 19.7 | 31.7 | 26.9 | 0 | 0
1287 | 2022-12-21 21:28 | 4.3 | 19.7 | 31.4 | 26.7 | 0 | 0
1288 | 2022-12-21 21:29 | 4.2 | 19.7 | 31.2 | 26.4 | 0 | 0
1289 | 2022-12-21 21:30 | 4.1 | 19.7 | 31 | 26.2 | 0 | 0
1290 | 2022-12-21 21:31 | 4 | 19.7 | 30.8 | 26 | 0 | 0
1291 | 2022-12-21 21:32 | 3.9 | 19.7 | 30.6 | 25.7 | 0 | 0
1292 | 2022-12-21 21:33 | 3.8 | 19.7 | 30.4 | 25.5 | 0 | 0
1293 | 2022-12-21 21:34 | 3.8 | 19.7 | 30.1 | 25.3 | 0 | 0
1294 | 2022-12-21 21:35 | 3.7 | 19.6 | 29.9 | 25.1 | 0 | 0
1295 | 2022-12-21 21:36 | 3.9 | 19.7 | 29.7 | 24.8 | 0 | 0
1296 | 2022-12-21 21:37 | 3.7 | 19.7 | 29.5 | 24.6 | 0 | 0
1297 | 2022-12-21 21:38 | 3.8 | 19.6 | 29.3 | 24.4 | 0 | 0
1298 | 2022-12-21 21:39 | 3.6 | 19.7 | 29.1 | 24.2 | 0 | 0
1299 | 2022-12-21 21:40 | 3.5 | 19.7 | 28.9 | 24 | 0 | 0
1300 | 2022-12-21 21:41 | 3.5 | 19.6 | 28.7 | 23.9 | 0 | 0
1301 | 2022-12-21 21:42 | 3.7 | 19.6 | 28.5 | 23.7 | 0 | 0
1302 | 2022-12-21 21:43 | 3.5 | 19.6 | 28.3 | 23.5 | 0 | 0
1303 | 2022-12-21 21:44 | 3.6 | 19.6 | 28.1 | 23.3 | 0 | 0
1304 | 2022-12-21 21:45 | 3.5 | 19.6 | 27.9 | 23.1 | 0 | 0
1305 | 2022-12-21 21:46 | 3.4 | 19.6 | 27.7 | 23 | 0 | 0
1306 | 2022-12-21 21:47 | 3.5 | 19.6 | 27.5 | 22.8 | 0 | 0
1307 | 2022-12-21 21:48 | 3.4 | 19.5 | 27.3 | 22.6 | 0 | 0
1308 | 2022-12-21 21:49 | 3.2 | 19.5 | 27.1 | 22.4 | 0 | 0
1309 | 2022-12-21 21:50 | 3.2 | 19.5 | 26.9 | 22.2 | 0 | 0
1310 | 2022-12-21 21:51 | 3.3 | 19.6 | 26.7 | 22.1 | 0 | 0
1311 | 2022-12-21 21:52 | 3.2 | 19.5 | 26.5 | 21.9 | 0 | 0
1312 | 2022-12-21 21:53 | 3.1 | 19.5 | 26.3 | 21.7 | 0 | 0
1313 | 2022-12-21 21:54 | 3.3 | 19.5 | 26.1 | 21.5 | 0 | 0
1314 | 2022-12-21 21:55 | 3.3 | 19.5 | 26 | 21.4 | 0 | 0
1315 | 2022-12-21 21:56 | 3.2 | 19.5 | 25.8 | 21.2 | 0 | 0
1316 | 2022-12-21 21:57 | 3.1 | 19.5 | 25.6 | 21 | 0 | 0
1317 | 2022-12-21 21:58 | 3.2 | 19.5 | 25.4 | 20.9 | 0 | 0
1318 | 2022-12-21 21:59 | 2.9 | 19.4 | 25.2 | 20.7 | 0 | 0
1319 | 2022-12-21 22:00 | 2.9 | 19.4 | 25 | 20.6 | 0 | 0
1320 | 2022-12-21 22:01 | 2.9 | 19.4 | 24.9 | 20.4 | 0 | 0
1321 | 2022-12-21 22:02 | 2.9 | 19.4 | 24.7 | 20.2 | 0 | 0
1322 | 2022-12-21 22:03 | 2.9 | 19.4 | 24.5 | 20.1 | 0 | 0
1323 | 2022-12-21 22:04 | 2.7 | 19.4 | 24.3 | 19.9 | 0 | 0
1324 | 2022-12-21 22:05 | 2.7 | 19.4 | 24.2 | 19.8 | 0 | 0
1325 | 2022-12-21 22:06 | 2.7 | 19.4 | 24 | 19.6 | 0 | 0
1326 | 2022-12-21 22:07 | 2.7 | 19.4 | 23.8 | 19.5 | 0 | 0
1327 | 2022-12-21 22:08 | 2.8 | 19.4 | 23.7 | 19.3 | 0 | 0
1328 | 2022-12-21 22:09 | 2.7 | 19.4 | 23.5 | 19.2 | 0 | 0
1329 | 2022-12-21 22:10 | 2.6 | 19.4 | 23.3 | 19.1 | 0 | 0
1330 | 2022-12-21 22:11 | 2.6 | 19.3 | 23.2 | 19 | 0 | 0
1331 | 2022-12-21 22:12 | 2.9 | 19.4 | 23 | 18.8 | 0 | 0
1332 | 2022-12-21 22:13 | 2.8 | 19.4 | 22.9 | 18.7 | 0 | 0
1333 | 2022-12-21 22:14 | 2.6 | 19.4 | 22.7 | 18.6 | 0 | 0
1334 | 2022-12-21 22:15 | 2.6 | 19.4 | 22.5 | 18.5 | 0 | 0
1335 | 2022-12-21 22:16 | 2.7 | 19.3 | 22.4 | 18.3 | 0 | 0
1336 | 2022-12-21 22:17 | 2.5 | 19.3 | 22.2 | 18.2 | 0 | 0
1337 | 2022-12-21 22:18 | 2.7 | 19.3 | 22.1 | 18.1 | 0 | 0
1338 | 2022-12-21 22:19 | 2.5 | 19.4 | 21.9 | 18 | 0 | 0
1339 | 2022-12-21 22:20 | 2.5 | 19.4 | 21.7 | 17.9 | 0 | 0
1340 | 2022-12-21 22:21 | 2.5 | 19.3 | 21.6 | 17.7 | 0 | 0
1341 | 2022-12-21 22:22 | 2.6 | 19.3 | 21.4 | 17.6 | 0 | 0
1342 | 2022-12-21 22:23 | 2.6 | 19.3 | 21.3 | 17.5 | 0 | 0
1343 | 2022-12-21 22:24 | 2.6 | 19.3 | 21.1 | 17.4 | 0 | 0
1344 | 2022-12-21 22:25 | 2.4 | 19.3 | 21 | 17.3 | 0 | 0
1345 | 2022-12-21 22:26 | 2.6 | 19.3 | 20.9 | 17.2 | 0 | 0
1346 | 2022-12-21 22:27 | 2.4 | 19.3 | 20.7 | 17.1 | 0 | 0
1347 | 2022-12-21 22:28 | 2.6 | 19.4 | 20.6 | 17 | 0 | 0
1348 | 2022-12-21 22:29 | 2.5 | 19.3 | 20.4 | 16.9 | 0 | 0
1349 | 2022-12-21 22:30 | 2.6 | 19.3 | 20.3 | 16.7 | 0 | 0
1350 | 2022-12-21 22:31 | 2.4 | 19.3 | 20.2 | 16.6 | 0 | 0
1351 | 2022-12-21 22:32 | 2.6 | 19.3 | 20 | 16.5 | 0 | 0
1352 | 2022-12-21 22:33 | 2.4 | 19.3 | 19.9 | 16.4 | 0 | 0
1353 | 2022-12-21 22:34 | 2.3 | 19.4 | 19.8 | 16.3 | 0 | 0
1354 | 2022-12-21 22:35 | 2.5 | 19.3 | 19.7 | 16.2 | 0 | 0
1355 | 2022-12-21 22:36 | 2.4 | 19.2 | 19.5 | 16.1 | 0 | 0
1356 | 2022-12-21 22:37 | 2.5 | 19.2 | 19.4 | 16 | 0 | 0
1357 | 2022-12-21 22:38 | 2.4 | 19.1 | 19.3 | 15.9 | 0 | 0
1358 | 2022-12-21 22:39 | 2.4 | 19.2 | 19.1 | 15.8 | 0 | 0
1359 | 2022-12-21 22:40 | 2.5 | 19.2 | 19 | 15.7 | 0 | 0
1360 | 2022-12-21 22:41 | 2.3 | 19.2 | 18.9 | 15.6 | 0 | 0
1361 | 2022-12-21 22:42 | 2.3 | 19.1 | 18.8 | 15.5 | 0 | 0
1362 | 2022-12-21 22:43 | 2.3 | 19.2 | 18.7 | 15.4 | 0 | 0
1363 | 2022-12-21 22:44 | 2.3 | 19.2 | 18.6 | 15.3 | 0 | 0
1364 | 2022-12-21 22:45 | 2.3 | 19.2 | 18.5 | 15.3 | 0 | 0
1365 | 2022-12-21 22:46 | 2.4 | 19.2 | 18.3 | 15.2 | 0 | 0
1366 | 2022-12-21 22:47 | 2.4 | 19.1 | 18.2 | 15.1 | 0 | 0
1367 | 2022-12-21 22:48 | 2.4 | 19.2 | 18.1 | 15 | 0 | 0
1368 | 2022-12-21 22:49 | 2.5 | 19.2 | 18 | 14.9 | 0 | 0
1369 | 2022-12-21 22:50 | 2.4 | 19.1 | 17.9 | 14.8 | 0 | 0
1370 | 2022-12-21 22:51 | 2.3 | 19.1 | 17.8 | 14.7 | 0 | 0
1371 | 2022-12-21 22:52 | 2.3 | 19.1 | 17.7 | 14.6 | 0 | 0
1372 | 2022-12-21 22:53 | 2.2 | 19.1 | 17.6 | 14.6 | 0 | 0
1373 | 2022-12-21 22:54 | 2.4 | 19.1 | 17.5 | 14.5 | 0 | 0
1374 | 2022-12-21 22:55 | 2.5 | 19.1 | 17.4 | 14.4 | 0 | 0
1375 | 2022-12-21 22:56 | 2.5 | 19.2 | 17.4 | 14.3 | 0 | 0
1376 | 2022-12-21 22:57 | 2.5 | 19.2 | 17.2 | 14.2 | 0 | 0
1377 | 2022-12-21 22:58 | 2.3 | 19.2 | 17.1 | 14.1 | 0 | 0
1378 | 2022-12-21 22:59 | 2.2 | 19.1 | 17 | 14.1 | 0 | 0
1379 | 2022-12-21 23:00 | 2.3 | 19.1 | 16.9 | 14 | 0 | 0
1380 | 2022-12-21 23:01 | 2.1 | 19.1 | 16.8 | 13.9 | 0 | 0
1381 | 2022-12-21 23:02 | 2.3 | 19 | 16.7 | 13.8 | 0 | 0
1382 | 2022-12-21 23:03 | 2.2 | 19 | 16.7 | 13.7 | 0 | 0
1383 | 2022-12-21 23:04 | 2.3 | 19 | 16.6 | 13.7 | 0 | 0
1384 | 2022-12-21 23:05 | 2.3 | 19 | 16.5 | 13.6 | 0 | 0
1385 | 2022-12-21 23:06 | 2.1 | 19 | 16.4 | 13.5 | 0 | 0
1386 | 2022-12-21 23:07 | 2.2 | 19 | 16.3 | 13.4 | 0 | 0
1387 | 2022-12-21 23:08 | 2 | 19 | 16.3 | 13.4 | 0 | 0
1388 | 2022-12-21 23:09 | 2 | 19 | 16.2 | 13.3 | 0 | 0
1389 | 2022-12-21 23:10 | 2 | 19 | 16.1 | 13.2 | 0 | 0
1390 | 2022-12-21 23:11 | 2.2 | 19 | 16 | 13.1 | 0 | 0
1391 | 2022-12-21 23:12 | 2.1 | 19 | 16 | 13.1 | 0 | 0
1392 | 2022-12-21 23:13 | 2 | 19 | 15.9 | 13 | 0 | 0
1393 | 2022-12-21 23:14 | 2.2 | 19 | 15.8 | 12.9 | 0 | 0
1394 | 2022-12-21 23:15 | 2.1 | 19 | 15.8 | 12.9 | 0 | 0
1395 | 2022-12-21 23:16 | 2 | 19 | 15.7 | 12.8 | 0 | 0
1396 | 2022-12-21 23:17 | 2.1 | 19 | 15.6 | 12.7 | 0 | 0
1397 | 2022-12-21 23:18 | 2 | 19 | 15.6 | 12.7 | 0 | 0
1398 | 2022-12-21 23:19 | 2.1 | 19 | 15.5 | 12.6 | 0 | 0
1399 | 2022-12-21 23:20 | 2.2 | 19 | 15.5 | 12.5 | 0 | 0
1400 | 2022-12-21 23:21 | 2 | 19 | 15.4 | 12.5 | 0 | 0
1401 | 2022-12-21 23:22 | 2 | 19 | 15.4 | 12.4 | 0 | 0
1402 | 2022-12-21 23:23 | 2.1 | 19 | 15.3 | 12.3 | 0 | 0
1403 | 2022-12-21 23:24 | 2 | 18.9 | 15.2 | 12.3 | 0 | 0
1404 | 2022-12-21 23:25 | 2.2 | 18.9 | 15.2 | 12.2 | 0 | 0
1405 | 2022-12-21 23:26 | 2.1 | 19 | 15.1 | 12.2 | 0 | 0
1406 | 2022-12-21 23:27 | 2.3 | 18.9 | 15 | 12.1 | 0 | 0
1407 | 2022-12-21 23:28 | 2.1 | 18.9 | 15 | 12 | 0 | 0
1408 | 2022-12-21 23:29 | 2.2 | 18.9 | 14.9 | 12 | 0 | 0
1409 | 2022-12-21 23:30 | 2.4 | 18.9 | 14.9 | 11.9 | 0 | 0
1410 | 2022-12-21 23:31 | 2.2 | 18.9 | 14.8 | 11.9 | 0 | 0
1411 | 2022-12-21 23:32 | 2.3 | 18.8 | 14.7 | 11.8 | 0 | 0
1412 | 2022-12-21 23:33 | 2.3 | 18.9 | 14.7 | 11.7 | 0 | 0
1413 | 2022-12-21 23:34 | 2.2 | 18.9 | 14.6 | 11.7 | 0 | 0
1414 | 2022-12-21 23:35 | 2.1 | 18.9 | 14.6 | 11.6 | 0 | 0
1415 | 2022-12-21 23:36 | 2.1 | 19 | 14.5 | 11.6 | 0 | 0
1416 | 2022-12-21 23:37 | 2.1 | 18.9 | 14.4 | 11.5 | 0 | 0
1417 | 2022-12-21 23:38 | 2 | 18.9 | 14.4 | 11.5 | 0 | 0
1418 | 2022-12-21 23:39 | 1.9 | 18.9 | 14.4 | 11.4 | 0 | 0
1419 | 2022-12-21 23:40 | 1.9 | 18.8 | 14.3 | 11.4 | 0 | 0
1420 | 2022-12-21 23:41 | 1.9 | 18.9 | 14.3 | 11.3 | 0 | 0
1421 | 2022-12-21 23:42 | 2 | 18.9 | 14.2 | 11.2 | 0 | 0
1422 | 2022-12-21 23:43 | 1.9 | 18.8 | 14.2 | 11.2 | 0 | 0
1423 | 2022-12-21 23:44 | 1.9 | 18.9 | 14.1 | 11.1 | 0 | 0
1424 | 2022-12-21 23:45 | 2 | 18.8 | 14.1 | 11.1 | 0 | 0
1425 | 2022-12-21 23:46 | 2 | 18.8 | 14.1 | 11 | 0 | 0
1426 | 2022-12-21 23:47 | 2 | 18.9 | 14 | 11 | 0 | 0
1427 | 2022-12-21 23:48 | 2.2 | 18.9 | 14 | 10.9 | 0 | 0
1428 | 2022-12-21 23:49 | 2 | 18.8 | 13.9 | 10.9 | 0 | 0
1429 | 2022-12-21 23:50 | 2.1 | 18.8 | 13.8 | 10.8 | 0 | 0
1430 | 2022-12-21 23:51 | 2.1 | 18.8 | 13.8 | 10.8 | 0 | 0
1431 | 2022-12-21 23:52 | 2.2 | 18.8 | 13.7 | 10.7 | 0 | 0
1432 | 2022-12-21 23:53 | 2 | 18.7 | 13.7 | 10.7 | 0 | 0
1433 | 2022-12-21 23:54 | 2.1 | 18.8 | 13.6 | 10.6 | 0 | 0
1434 | 2022-12-21 23:55 | 2 | 18.8 | 13.6 | 10.6 | 0 | 0
1435 | 2022-12-21 23:56 | 1.8 | 18.8 | 13.6 | 10.5 | 0 | 0
1436 | 2022-12-21 23:57 | 1.9 | 18.8 | 13.5 | 10.5 | 0 | 0
1437 | 2022-12-21 23:58 | 2.3 | 18.7 | 13.5 | 10.4 | 0 | 0
1438 | 2022-12-21 23:59 | 2.1 | 18.8 | 13.4 | 10.4 | 0 | 0
1439 | 2022-12-22 | 2.1 | 18.7 | 13.4 | 10.4 | 0 | 0

## 22-12-2022_WITH HEAT
| Date&time_x | OUTDOOR_TEMP | INDOOR_TEMP | SH_INLET | SH_RETURN | FLOW_FAN_COILS_INDOOR | PYRANOMETER
0 | 2022-12-22 00:01 | 2.1 | 18.8 | 13.4 | 10.3 | 0 | 0
1 | 2022-12-22 00:02 | 2.1 | 18.7 | 13.4 | 10.3 | 0 | 0
2 | 2022-12-22 00:03 | 2.1 | 18.7 | 13.3 | 10.2 | 0 | 0
3 | 2022-12-22 00:04 | 2.2 | 18.7 | 13.3 | 10.2 | 0 | 0
4 | 2022-12-22 00:05 | 2.1 | 18.7 | 13.3 | 10.1 | 0 | 0
5 | 2022-12-22 00:06 | 1.9 | 18.7 | 13.2 | 10.1 | 0 | 0
6 | 2022-12-22 00:07 | 1.9 | 18.8 | 13.2 | 10.1 | 0 | 0
7 | 2022-12-22 00:08 | 1.9 | 18.7 | 13.2 | 10 | 0 | 0
8 | 2022-12-22 00:09 | 1.9 | 18.7 | 13.1 | 10 | 0 | 0
9 | 2022-12-22 00:10 | 1.9 | 18.7 | 13.1 | 9.9 | 0 | 0
10 | 2022-12-22 00:11 | 1.9 | 18.7 | 13.1 | 9.9 | 0 | 0
11 | 2022-12-22 00:12 | 2.1 | 18.7 | 13 | 9.9 | 0 | 0
12 | 2022-12-22 00:13 | 2 | 18.7 | 13 | 9.9 | 0.019 | 0
13 | 2022-12-22 00:14 | 2 | 18.7 | 13 | 11.4 | 0 | 0
14 | 2022-12-22 00:15 | 2 | 18.7 | 12.9 | 11.4 | 0 | 0
15 | 2022-12-22 00:16 | 1.9 | 18.6 | 19.4 | 12.9 | 0.852 | 0
16 | 2022-12-22 00:17 | 1.9 | 18.7 | 40.6 | 17.3 | 0.37 | 0
17 | 2022-12-22 00:18 | 2 | 18.6 | 41.5 | 35.8 | 0.567 | 0
18 | 2022-12-22 00:19 | 2 | 18.7 | 40.7 | 38.2 | 0.945 | 0
19 | 2022-12-22 00:20 | 2.1 | 18.7 | 39.2 | 38.7 | 0.943 | 0
20 | 2022-12-22 00:21 | 1.9 | 18.7 | 38.7 | 38 | 0.941 | 0
21 | 2022-12-22 00:22 | 1.8 | 18.7 | 38.7 | 37.7 | 0.928 | 0
22 | 2022-12-22 00:23 | 2 | 18.7 | 39.4 | 38 | 0.938 | 0
23 | 2022-12-22 00:24 | 2.1 | 18.7 | 39.9 | 38.7 | 0.979 | 0
24 | 2022-12-22 00:25 | 1.7 | 18.8 | 39.5 | 38.9 | 0.981 | 0
25 | 2022-12-22 00:26 | 1.7 | 18.7 | 39.1 | 38.5 | 0.977 | 0
26 | 2022-12-22 00:27 | 1.6 | 18.7 | 39 | 38.3 | 0.977 | 0
27 | 2022-12-22 00:28 | 1.6 | 18.7 | 38.9 | 38.1 | 0.985 | 0
28 | 2022-12-22 00:29 | 1.7 | 18.7 | 38.9 | 38.1 | 0.98 | 0
29 | 2022-12-22 00:30 | 1.7 | 18.7 | 38.9 | 38.1 | 0.975 | 0
30 | 2022-12-22 00:31 | 1.6 | 18.8 | 38.9 | 38.1 | 0.974 | 0
31 | 2022-12-22 00:32 | 1.8 | 18.7 | 38.8 | 38 | 0.98 | 0
32 | 2022-12-22 00:33 | 1.9 | 18.7 | 38.8 | 38 | 0.977 | 0
33 | 2022-12-22 00:34 | 1.8 | 18.8 | 38.8 | 38 | 0.98 | 0
34 | 2022-12-22 00:35 | 2 | 18.7 | 38.8 | 38 | 0.98 | 0
35 | 2022-12-22 00:36 | 1.9 | 18.7 | 38.7 | 38 | 0.98 | 0
36 | 2022-12-22 00:37 | 1.7 | 18.7 | 38.7 | 37.9 | 0.976 | 0
37 | 2022-12-22 00:38 | 1.9 | 18.7 | 38.7 | 37.9 | 0.976 | 0
38 | 2022-12-22 00:39 | 1.8 | 18.7 | 38.7 | 37.9 | 0.979 | 0
39 | 2022-12-22 00:40 | 1.7 | 18.7 | 38.7 | 37.9 | 0.974 | 0
40 | 2022-12-22 00:41 | 1.9 | 18.7 | 38.6 | 37.8 | 0.975 | 0
41 | 2022-12-22 00:42 | 1.9 | 18.7 | 38.6 | 37.8 | 0.975 | 0
42 | 2022-12-22 00:43 | 1.8 | 18.6 | 38.6 | 37.8 | 0.979 | 0
43 | 2022-12-22 00:44 | 1.7 | 18.7 | 38.6 | 37.8 | 0.98 | 0
44 | 2022-12-22 00:45 | 1.7 | 18.6 | 38.6 | 37.8 | 0.977 | 0
45 | 2022-12-22 00:46 | 1.8 | 18.8 | 38.5 | 37.8 | 0.975 | 0
46 | 2022-12-22 00:47 | 1.6 | 18.8 | 38.5 | 37.7 | 0.975 | 0
47 | 2022-12-22 00:48 | 1.7 | 18.7 | 38.5 | 37.7 | 0.976 | 0
48 | 2022-12-22 00:49 | 1.6 | 18.7 | 38.5 | 37.7 | 0.975 | 0
49 | 2022-12-22 00:50 | 1.6 | 18.6 | 38.5 | 37.7 | 0.976 | 0
50 | 2022-12-22 00:51 | 1.7 | 18.6 | 38.4 | 37.7 | 0.975 | 0
51 | 2022-12-22 00:52 | 1.7 | 18.7 | 38.4 | 37.6 | 0.979 | 0
52 | 2022-12-22 00:53 | 1.7 | 18.7 | 38.4 | 37.6 | 0.974 | 0
53 | 2022-12-22 00:54 | 1.6 | 18.7 | 38.4 | 37.6 | 0.974 | 0
54 | 2022-12-22 00:55 | 1.8 | 18.6 | 38.3 | 37.6 | 0.975 | 0
55 | 2022-12-22 00:56 | 1.6 | 18.6 | 38.3 | 37.5 | 0.976 | 0
56 | 2022-12-22 00:57 | 1.5 | 18.6 | 38.3 | 37.5 | 0.98 | 0
57 | 2022-12-22 00:58 | 1.5 | 18.6 | 38.2 | 37.5 | 0.976 | 0
58 | 2022-12-22 00:59 | 1.5 | 18.6 | 38.2 | 37.5 | 0.978 | 0
59 | 2022-12-22 01:00 | 1.7 | 18.7 | 38.2 | 37.4 | 0.975 | 0
60 | 2022-12-22 01:01 | 1.5 | 18.6 | 38.1 | 37.4 | 0.976 | 0
61 | 2022-12-22 01:02 | 1.6 | 18.6 | 38.1 | 37.4 | 0.975 | 0
62 | 2022-12-22 01:03 | 1.6 | 18.6 | 38.1 | 37.3 | 0.976 | 0
63 | 2022-12-22 01:04 | 1.5 | 18.6 | 38.1 | 37.3 | 0.981 | 0
64 | 2022-12-22 01:05 | 1.6 | 18.6 | 38 | 37.3 | 0.978 | 0
65 | 2022-12-22 01:06 | 1.5 | 18.6 | 38 | 37.3 | 0.973 | 0
66 | 2022-12-22 01:07 | 1.7 | 18.6 | 38 | 37.2 | 0.981 | 0
67 | 2022-12-22 01:08 | 1.6 | 18.6 | 37.9 | 37.2 | 0.976 | 0
68 | 2022-12-22 01:09 | 1.7 | 18.6 | 37.9 | 37.2 | 0.978 | 0
69 | 2022-12-22 01:10 | 1.7 | 18.6 | 37.9 | 37.1 | 0.978 | 0
70 | 2022-12-22 01:11 | 1.6 | 18.6 | 37.8 | 37.1 | 0.976 | 0
71 | 2022-12-22 01:12 | 1.5 | 18.6 | 37.8 | 37.1 | 0.978 | 0
72 | 2022-12-22 01:13 | 1.7 | 18.5 | 37.8 | 37 | 0.975 | 0
73 | 2022-12-22 01:14 | 1.5 | 18.5 | 37.7 | 37 | 0.978 | 0
74 | 2022-12-22 01:15 | 1.4 | 18.6 | 37.7 | 37 | 0 | 0
75 | 2022-12-22 01:16 | 1.6 | 18.6 | 37.7 | 36.9 | 0.976 | 0
76 | 2022-12-22 01:17 | 1.5 | 18.5 | 37.6 | 36.9 | 0.975 | 0
77 | 2022-12-22 01:18 | 1.6 | 18.5 | 37.6 | 36.9 | 0.978 | 0
78 | 2022-12-22 01:19 | 1.5 | 18.5 | 37.6 | 36.8 | 0.977 | 0
79 | 2022-12-22 01:20 | 1.7 | 18.6 | 37.5 | 36.8 | 0.976 | 0
80 | 2022-12-22 01:21 | 1.5 | 18.6 | 37.5 | 36.8 | 0.976 | 0
81 | 2022-12-22 01:22 | 1.5 | 18.6 | 37.5 | 36.7 | 0.973 | 0
82 | 2022-12-22 01:23 | 1.5 | 18.6 | 37.4 | 36.7 | 0.975 | 0
83 | 2022-12-22 01:24 | 1.5 | 18.6 | 37.4 | 36.7 | 0.971 | 0
84 | 2022-12-22 01:25 | 1.4 | 18.6 | 37.4 | 36.7 | 0.973 | 0
85 | 2022-12-22 01:26 | 1.3 | 18.6 | 37.3 | 36.6 | 0.974 | 0
86 | 2022-12-22 01:27 | 1.4 | 18.6 | 37.3 | 36.6 | 0.974 | 0
87 | 2022-12-22 01:28 | 1.5 | 18.6 | 37.3 | 36.6 | 0.974 | 0
88 | 2022-12-22 01:29 | 1.7 | 18.5 | 37.2 | 36.5 | 0.977 | 0
89 | 2022-12-22 01:30 | 1.6 | 18.5 | 37.2 | 36.5 | 0.975 | 0
90 | 2022-12-22 01:31 | 1.8 | 18.5 | 37 | 36.4 | 0.972 | 0
91 | 2022-12-22 01:32 | 1.4 | 18.6 | 36.9 | 36.1 | 0.971 | 0
92 | 2022-12-22 01:33 | 1.6 | 18.5 | 37.1 | 36.2 | 0.97 | 0
93 | 2022-12-22 01:34 | 1.6 | 18.6 | 37.4 | 36.4 | 0.977 | 0
94 | 2022-12-22 01:35 | 1.4 | 18.6 | 37.7 | 36.9 | 0.974 | 0
95 | 2022-12-22 01:36 | 1.6 | 18.6 | 37.3 | 36.8 | 0.974 | 0
96 | 2022-12-22 01:37 | 1.5 | 18.5 | 37.2 | 36.6 | 0.977 | 0
97 | 2022-12-22 01:38 | 1.3 | 18.6 | 37.2 | 36.5 | 0.977 | 0
98 | 2022-12-22 01:39 | 1.5 | 18.5 | 37.2 | 36.5 | 0.974 | 0
99 | 2022-12-22 01:40 | 1.5 | 18.6 | 37.1 | 36.4 | 0.973 | 0
100 | 2022-12-22 01:41 | 1.4 | 18.6 | 37.1 | 36.4 | 0.975 | 0
101 | 2022-12-22 01:42 | 1.6 | 18.5 | 37.1 | 36.4 | 0.976 | 0
102 | 2022-12-22 01:43 | 1.3 | 18.5 | 37.1 | 36.4 | 0.973 | 0
103 | 2022-12-22 01:44 | 1.2 | 18.5 | 36.9 | 36.3 | 0.973 | 0
104 | 2022-12-22 01:45 | 1.3 | 18.5 | 37.1 | 36.2 | 0.97 | 0
105 | 2022-12-22 01:46 | 1.3 | 18.5 | 37.3 | 36.4 | 0.977 | 0
106 | 2022-12-22 01:47 | 1.4 | 18.6 | 37.8 | 36.7 | 0.977 | 0
107 | 2022-12-22 01:48 | 1.3 | 18.5 | 37.7 | 37.1 | 0.975 | 0
108 | 2022-12-22 01:49 | 1.4 | 18.6 | 37.5 | 36.8 | 0.976 | 0
109 | 2022-12-22 01:50 | 1.3 | 18.5 | 37.4 | 36.7 | 0.975 | 0
110 | 2022-12-22 01:51 | 1.2 | 18.5 | 37.4 | 36.7 | 0.977 | 0
111 | 2022-12-22 01:52 | 1.4 | 18.6 | 37.4 | 36.7 | 0.972 | 0
112 | 2022-12-22 01:53 | 1.4 | 18.5 | 37.3 | 36.6 | 0.975 | 0
113 | 2022-12-22 01:54 | 1.2 | 18.5 | 37.3 | 36.6 | 0.976 | 0
114 | 2022-12-22 01:55 | 1.3 | 18.6 | 37.2 | 36.5 | 0.971 | 0
115 | 2022-12-22 01:56 | 1.3 | 18.6 | 37.3 | 36.5 | 0.973 | 0
116 | 2022-12-22 01:57 | 1.5 | 18.6 | 37.2 | 36.5 | 0.974 | 0
117 | 2022-12-22 01:58 | 1.4 | 18.5 | 37.2 | 36.5 | 0.975 | 0
118 | 2022-12-22 01:59 | 1.4 | 18.6 | 37.2 | 36.5 | 0.974 | 0
119 | 2022-12-22 02:00 | 1.4 | 18.5 | 37.1 | 36.4 | 0.975 | 0
120 | 2022-12-22 02:01 | 1.4 | 18.4 | 37.3 | 36.4 | 0.975 | 0
121 | 2022-12-22 02:02 | 1.4 | 18.5 | 37.5 | 36.5 | 0.976 | 0
122 | 2022-12-22 02:03 | 1.2 | 18.5 | 37.8 | 37 | 0.975 | 0
123 | 2022-12-22 02:04 | 1.4 | 18.5 | 37.6 | 36.9 | 0.979 | 0
124 | 2022-12-22 02:05 | 1.3 | 18.4 | 37.5 | 36.8 | 0.973 | 0
125 | 2022-12-22 02:06 | 1.4 | 18.4 | 37.4 | 36.7 | 0.97 | 0
126 | 2022-12-22 02:07 | 1.3 | 18.4 | 37.4 | 36.7 | 0.974 | 0
127 | 2022-12-22 02:08 | 1.3 | 18.5 | 37.3 | 36.6 | 0.976 | 0
128 | 2022-12-22 02:09 | 1.3 | 18.4 | 37.3 | 36.6 | 0.972 | 0
129 | 2022-12-22 02:10 | 1.2 | 18.4 | 37.3 | 36.5 | 0.974 | 0
130 | 2022-12-22 02:11 | 1.2 | 18.4 | 37.2 | 36.5 | 0.977 | 0
131 | 2022-12-22 02:12 | 1.2 | 18.4 | 37.2 | 36.5 | 0.973 | 0
132 | 2022-12-22 02:13 | 1.3 | 18.4 | 37.2 | 36.5 | 0.973 | 0
133 | 2022-12-22 02:14 | 1.3 | 18.5 | 37.2 | 36.5 | 0.973 | 0
134 | 2022-12-22 02:15 | 1.4 | 18.4 | 37.1 | 36.4 | 0.974 | 0
135 | 2022-12-22 02:16 | 1.1 | 18.4 | 37.1 | 36.3 | 0.973 | 0
136 | 2022-12-22 02:17 | 1.4 | 18.4 | 37.3 | 36.4 | 0.973 | 0
137 | 2022-12-22 02:18 | 1.2 | 18.4 | 37.7 | 36.6 | 0.974 | 0
138 | 2022-12-22 02:19 | 1.4 | 18.4 | 37.6 | 37 | 0.974 | 0
139 | 2022-12-22 02:20 | 1.5 | 18.4 | 37.5 | 36.8 | 0.976 | 0
140 | 2022-12-22 02:21 | 1.6 | 18.4 | 37.4 | 36.7 | 0.975 | 0
141 | 2022-12-22 02:22 | 1.5 | 18.4 | 37.4 | 36.7 | 0.973 | 0
142 | 2022-12-22 02:23 | 1.3 | 18.4 | 37.3 | 36.6 | 0.974 | 0
143 | 2022-12-22 02:24 | 1.5 | 18.4 | 37.3 | 36.6 | 0.974 | 0
144 | 2022-12-22 02:25 | 1.5 | 18.5 | 37.2 | 36.5 | 0.972 | 0
145 | 2022-12-22 02:26 | 1.3 | 18.4 | 37.2 | 36.5 | 0.975 | 0
146 | 2022-12-22 02:27 | 1.2 | 18.4 | 37.2 | 36.5 | 0.977 | 0
147 | 2022-12-22 02:28 | 1.5 | 18.4 | 37.2 | 36.4 | 0.977 | 0
148 | 2022-12-22 02:29 | 1.5 | 18.5 | 37.1 | 36.4 | 0.972 | 0
149 | 2022-12-22 02:30 | 1.4 | 18.5 | 37.2 | 36.3 | 0.972 | 0
150 | 2022-12-22 02:31 | 1.5 | 18.4 | 37.4 | 36.5 | 0.976 | 0
151 | 2022-12-22 02:32 | 1.4 | 18.4 | 37.8 | 36.7 | 0.979 | 0
152 | 2022-12-22 02:33 | 1.5 | 18.4 | 37.6 | 37 | 0.983 | 0
153 | 2022-12-22 02:34 | 1.5 | 18.3 | 37.5 | 36.8 | 0.973 | 0
154 | 2022-12-22 02:35 | 1.6 | 18.4 | 37.4 | 36.7 | 0.974 | 0
155 | 2022-12-22 02:36 | 1.4 | 18.4 | 37.5 | 36.7 | 0.974 | 0
156 | 2022-12-22 02:37 | 1.5 | 18.4 | 37.4 | 36.7 | 0.973 | 0
157 | 2022-12-22 02:38 | 1.6 | 18.4 | 37.3 | 36.6 | 0.977 | 0
158 | 2022-12-22 02:39 | 1.5 | 18.3 | 37.3 | 36.6 | 0.97 | 0
159 | 2022-12-22 02:40 | 1.6 | 18.4 | 37.2 | 36.5 | 0.976 | 0
160 | 2022-12-22 02:41 | 1.5 | 18.4 | 37.2 | 36.5 | 0.974 | 0
161 | 2022-12-22 02:42 | 1.4 | 18.3 | 37.2 | 36.5 | 0.979 | 0
162 | 2022-12-22 02:43 | 1.6 | 18.3 | 37.2 | 36.5 | 0.974 | 0
163 | 2022-12-22 02:44 | 1.4 | 18.4 | 37.1 | 36.4 | 0.972 | 0
164 | 2022-12-22 02:45 | 1.5 | 18.3 | 37 | 36.4 | 0.975 | 0
165 | 2022-12-22 02:46 | 1.6 | 18.4 | 37.1 | 27.8 | 1.577 | 0
166 | 2022-12-22 02:47 | 1.5 | 18.4 | 37.3 | 35.4 | 1.634 | 0
167 | 2022-12-22 02:48 | 1.5 | 18.4 | 36.9 | 35.9 | 1.636 | 0
168 | 2022-12-22 02:49 | 1.5 | 18.3 | 36.8 | 35.3 | 1.635 | 0
169 | 2022-12-22 02:50 | 1.5 | 18.4 | 36.9 | 35.5 | 1.636 | 0
170 | 2022-12-22 02:51 | 1.5 | 18.4 | 36.9 | 35.5 | 1.637 | 0
171 | 2022-12-22 02:52 | 1.3 | 18.3 | 37.1 | 35.6 | 1.637 | 0
172 | 2022-12-22 02:53 | 1.3 | 18.3 | 37.2 | 35.7 | 1.637 | 0
173 | 2022-12-22 02:54 | 1.3 | 18.4 | 37.1 | 35.8 | 1.633 | 0
174 | 2022-12-22 02:55 | 1.2 | 18.3 | 37 | 35.7 | 1.636 | 0
175 | 2022-12-22 02:56 | 1.2 | 18.4 | 37 | 35.7 | 1.638 | 0
176 | 2022-12-22 02:57 | 1.5 | 18.3 | 36.9 | 35.6 | 1.63 | 0
177 | 2022-12-22 02:58 | 1.6 | 18.4 | 36.9 | 35.6 | 1.636 | 0
178 | 2022-12-22 02:59 | 1.6 | 18.3 | 36.8 | 35.5 | 1.637 | 0
179 | 2022-12-22 03:00 | 1.3 | 18.4 | 36.8 | 35.5 | 1.639 | 0
180 | 2022-12-22 03:01 | 1.5 | 18.3 | 36.8 | 35.4 | 1.634 | 0
181 | 2022-12-22 03:02 | 1.4 | 18.3 | 37.2 | 35.5 | 1.642 | 0
182 | 2022-12-22 03:03 | 1.6 | 18.3 | 37.3 | 35.9 | 1.638 | 0
183 | 2022-12-22 03:04 | 1.5 | 18.3 | 37.2 | 33.6 | 1.815 | 0
184 | 2022-12-22 03:05 | 1.4 | 18.4 | 37.1 | 35.2 | 1.841 | 0
185 | 2022-12-22 03:06 | 1.3 | 18.3 | 36.8 | 35.2 | 1.84 | 0
186 | 2022-12-22 03:07 | 1.4 | 18.3 | 36.7 | 34.9 | 1.839 | 0
187 | 2022-12-22 03:08 | 1.4 | 18.3 | 36.7 | 34.9 | 1.841 | 0
188 | 2022-12-22 03:09 | 1.4 | 18.4 | 36.6 | 34.9 | 1.841 | 0
189 | 2022-12-22 03:10 | 1.3 | 18.3 | 36.9 | 35 | 1.84 | 0
190 | 2022-12-22 03:11 | 1.2 | 18.4 | 37 | 35.1 | 1.836 | 0
191 | 2022-12-22 03:12 | 1.3 | 18.4 | 36.9 | 35.1 | 1.839 | 0
192 | 2022-12-22 03:13 | 1.3 | 18.3 | 36.8 | 35.1 | 1.841 | 0
193 | 2022-12-22 03:14 | 1.4 | 18.4 | 36.8 | 35 | 1.84 | 0
194 | 2022-12-22 03:15 | 1.4 | 18.4 | 36.7 | 35 | 1.836 | 0
195 | 2022-12-22 03:16 | 1.2 | 18.3 | 36.8 | 34.9 | 1.842 | 0
196 | 2022-12-22 03:17 | 1.4 | 18.4 | 37 | 35.1 | 1.843 | 0
197 | 2022-12-22 03:18 | 1.4 | 18.4 | 37 | 35.3 | 1.843 | 0
198 | 2022-12-22 03:19 | 1.3 | 18.4 | 37 | 35.2 | 1.838 | 0
199 | 2022-12-22 03:20 | 1.3 | 18.4 | 36.9 | 35.2 | 1.841 | 0
200 | 2022-12-22 03:21 | 1.3 | 18.4 | 36.8 | 35.1 | 1.836 | 0
201 | 2022-12-22 03:22 | 1.2 | 18.3 | 36.8 | 35 | 1.841 | 0
202 | 2022-12-22 03:23 | 1.2 | 18.4 | 36.6 | 35 | 1.84 | 0
203 | 2022-12-22 03:24 | 1.3 | 18.4 | 36.5 | 34.9 | 1.845 | 0
204 | 2022-12-22 03:25 | 1.2 | 18.3 | 36.7 | 34.8 | 1.843 | 0
205 | 2022-12-22 03:26 | 1.2 | 18.4 | 36.9 | 35 | 1.842 | 0
206 | 2022-12-22 03:27 | 1.4 | 18.4 | 36.8 | 35.1 | 1.835 | 0
207 | 2022-12-22 03:28 | 1.3 | 18.4 | 36.7 | 35 | 1.845 | 0
208 | 2022-12-22 03:29 | 1.4 | 18.4 | 36.6 | 35 | 1.844 | 0
209 | 2022-12-22 03:30 | 1.3 | 18.3 | 36.6 | 34.9 | 1.838 | 0
210 | 2022-12-22 03:31 | 1.3 | 18.4 | 36.5 | 34.9 | 1.845 | 0
211 | 2022-12-22 03:32 | 1.3 | 18.4 | 36.6 | 34.8 | 1.843 | 0
212 | 2022-12-22 03:33 | 1.3 | 18.4 | 37 | 35.5 | 1.838 | 0
213 | 2022-12-22 03:34 | 1.4 | 18.4 | 37.5 | 36.1 | 1.839 | 0
214 | 2022-12-22 03:35 | 1.3 | 18.4 | 37.9 | 37 | 1.847 | 0
215 | 2022-12-22 03:36 | 1.5 | 18.4 | 38.4 | 37.4 | 1.849 | 0
216 | 2022-12-22 03:37 | 1.5 | 18.4 | 38.5 | 37.7 | 1.829 | 0
217 | 2022-12-22 03:38 | 1.3 | 18.4 | 38.5 | 37.7 | 1.677 | 0
218 | 2022-12-22 03:39 | 1.4 | 18.4 | 38.4 | 37.7 | 1.055 | 0
219 | 2022-12-22 03:40 | 1.2 | 18.3 | 38.4 | 37.7 | 0.977 | 0
220 | 2022-12-22 03:41 | 1.3 | 18.3 | 38.3 | 37.6 | 0.974 | 0
221 | 2022-12-22 03:42 | 1.2 | 18.4 | 38.2 | 37.5 | 0.98 | 0
222 | 2022-12-22 03:43 | 1.3 | 18.3 | 38.2 | 37.5 | 0.976 | 0
223 | 2022-12-22 03:44 | 1.4 | 18.4 | 38.2 | 37.4 | 0.972 | 0
224 | 2022-12-22 03:45 | 1.2 | 18.3 | 38.2 | 37.4 | 0.976 | 0
225 | 2022-12-22 03:46 | 1.3 | 18.4 | 38.1 | 37.4 | 0.973 | 0
226 | 2022-12-22 03:47 | 1.4 | 18.4 | 38 | 37.3 | 0.978 | 0
227 | 2022-12-22 03:48 | 1.5 | 18.3 | 38 | 37.3 | 0.974 | 0
228 | 2022-12-22 03:49 | 1.4 | 18.3 | 38 | 37.3 | 0.976 | 0
229 | 2022-12-22 03:50 | 1.3 | 18.3 | 37.9 | 37.2 | 0.976 | 0
230 | 2022-12-22 03:51 | 1.5 | 18.3 | 37.9 | 37.2 | 0.977 | 0
231 | 2022-12-22 03:52 | 1.4 | 18.3 | 37.9 | 37.1 | 0.973 | 0
232 | 2022-12-22 03:53 | 1.4 | 18.3 | 37.8 | 37.1 | 0.971 | 0
233 | 2022-12-22 03:54 | 1.5 | 18.3 | 37.8 | 37 | 0.976 | 0
234 | 2022-12-22 03:55 | 1.5 | 18.3 | 37.7 | 37 | 0.975 | 0
235 | 2022-12-22 03:56 | 1.4 | 18.3 | 37.7 | 37 | 0.976 | 0
236 | 2022-12-22 03:57 | 1.3 | 18.3 | 37.7 | 36.9 | 0.975 | 0
237 | 2022-12-22 03:58 | 1.4 | 18.2 | 37.6 | 36.9 | 0.977 | 0
238 | 2022-12-22 03:59 | 1.4 | 18.2 | 37.6 | 36.8 | 0.975 | 0
239 | 2022-12-22 04:00 | 1.4 | 18.2 | 37.5 | 36.8 | 0.975 | 0
240 | 2022-12-22 04:01 | 1.4 | 18.3 | 37.5 | 36.7 | 0.972 | 0
241 | 2022-12-22 04:02 | 1.3 | 18.2 | 37.4 | 36.7 | 0.974 | 0
242 | 2022-12-22 04:03 | 1.3 | 18.2 | 37.3 | 36.7 | 0.976 | 0
243 | 2022-12-22 04:04 | 1.2 | 18.2 | 37.2 | 36.5 | 0.974 | 0
244 | 2022-12-22 04:05 | 1.4 | 18.2 | 37.4 | 36.5 | 0.971 | 0
245 | 2022-12-22 04:06 | 1.5 | 18.2 | 37.8 | 36.8 | 0.972 | 0
246 | 2022-12-22 04:07 | 1.2 | 18.2 | 38.4 | 37.2 | 0.973 | 0
247 | 2022-12-22 04:08 | 1.2 | 18.2 | 38.8 | 37.8 | 0.974 | 0
248 | 2022-12-22 04:09 | 1.3 | 18.2 | 39 | 38.1 | 0.977 | 0
249 | 2022-12-22 04:10 | 1.4 | 18.2 | 39.7 | 38.4 | 0.973 | 0
250 | 2022-12-22 04:11 | 1.4 | 18.2 | 39.2 | 38.8 | 0.976 | 0
251 | 2022-12-22 04:12 | 1.2 | 18.2 | 39.2 | 38.4 | 0.976 | 0
252 | 2022-12-22 04:13 | 1.3 | 18.1 | 39.4 | 38.5 | 0.973 | 0
253 | 2022-12-22 04:14 | 1.2 | 18.2 | 39.2 | 38.5 | 0.975 | 0
254 | 2022-12-22 04:15 | 1.3 | 18.2 | 39.2 | 38.4 | 0.978 | 0
255 | 2022-12-22 04:16 | 1.2 | 18.1 | 39.2 | 38.4 | 0.974 | 0
256 | 2022-12-22 04:17 | 1.2 | 18.1 | 39.1 | 38.3 | 0.977 | 0
257 | 2022-12-22 04:18 | 1.2 | 18.2 | 39.1 | 38.3 | 0.973 | 0
258 | 2022-12-22 04:19 | 1.3 | 18.2 | 39.1 | 38.3 | 0.974 | 0
259 | 2022-12-22 04:20 | 1.3 | 18.1 | 39 | 38.3 | 0.974 | 0
260 | 2022-12-22 04:21 | 1.2 | 18.1 | 39 | 38.2 | 0.979 | 0
261 | 2022-12-22 04:22 | 1.3 | 18.1 | 39 | 38.2 | 0.976 | 0
262 | 2022-12-22 04:23 | 1.5 | 18.2 | 39 | 38.2 | 0.974 | 0
263 | 2022-12-22 04:24 | 1.5 | 18.2 | 38.9 | 38.1 | 0.979 | 0
264 | 2022-12-22 04:25 | 1.4 | 18.1 | 38.9 | 38.1 | 0.978 | 0
265 | 2022-12-22 04:26 | 1.4 | 18.1 | 38.8 | 38.1 | 0.978 | 0
266 | 2022-12-22 04:27 | 1.3 | 18.2 | 38.8 | 38 | 0.974 | 0
267 | 2022-12-22 04:28 | 1.3 | 18.1 | 38.8 | 38 | 0.976 | 0
268 | 2022-12-22 04:29 | 1.4 | 18.2 | 38.7 | 37.9 | 0.976 | 0
269 | 2022-12-22 04:30 | 1.5 | 18.2 | 38.7 | 37.9 | 0.976 | 0
270 | 2022-12-22 04:31 | 1.3 | 18.1 | 38.6 | 37.9 | 0.98 | 0
271 | 2022-12-22 04:32 | 1.4 | 18.1 | 38.6 | 37.8 | 0.981 | 0
272 | 2022-12-22 04:33 | 1.3 | 18.2 | 38.5 | 37.8 | 0.973 | 0
273 | 2022-12-22 04:34 | 1.6 | 18.2 | 38.5 | 37.7 | 0.973 | 0
274 | 2022-12-22 04:35 | 1.3 | 18.1 | 38.7 | 31.9 | 1.555 | 0
275 | 2022-12-22 04:36 | 1.5 | 18.1 | 39 | 37.1 | 1.643 | 0
276 | 2022-12-22 04:37 | 1.5 | 18.2 | 39.1 | 37.6 | 1.643 | 0
277 | 2022-12-22 04:38 | 1.2 | 18.1 | 39.5 | 37.6 | 1.644 | 0
278 | 2022-12-22 04:39 | 1.2 | 18.1 | 40 | 38.1 | 1.638 | 0
279 | 2022-12-22 04:40 | 1.4 | 18.1 | 40.1 | 38.5 | 1.637 | 0
280 | 2022-12-22 04:41 | 1.4 | 18.1 | 40 | 38.5 | 1.646 | 0
281 | 2022-12-22 04:42 | 1.2 | 18.1 | 39.9 | 38.4 | 1.638 | 0
282 | 2022-12-22 04:43 | 1.2 | 18.1 | 39.9 | 38.4 | 1.643 | 0
283 | 2022-12-22 04:44 | 1.2 | 18.1 | 39.8 | 38.3 | 1.641 | 0
284 | 2022-12-22 04:45 | 1.3 | 18.1 | 39.7 | 38.2 | 1.64 | 0
285 | 2022-12-22 04:46 | 1.3 | 18.2 | 39.7 | 38.1 | 1.639 | 0
286 | 2022-12-22 04:47 | 1.3 | 18.1 | 39.5 | 35.3 | 1.829 | 0
287 | 2022-12-22 04:48 | 1.1 | 18.2 | 39.4 | 37.4 | 1.848 | 0
288 | 2022-12-22 04:49 | 1.2 | 18.2 | 39.1 | 37.4 | 1.848 | 0
289 | 2022-12-22 04:50 | 1.2 | 18.1 | 39 | 37 | 1.846 | 0
290 | 2022-12-22 04:51 | 1.3 | 18.1 | 38.9 | 37 | 1.838 | 0
291 | 2022-12-22 04:52 | 1.2 | 18.2 | 38.7 | 36.9 | 1.84 | 0
292 | 2022-12-22 04:53 | 1.3 | 18.1 | 38.6 | 36.8 | 1.847 | 0
293 | 2022-12-22 04:54 | 1.4 | 18.1 | 38.4 | 36.6 | 1.841 | 0
294 | 2022-12-22 04:55 | 1.2 | 18.3 | 38.3 | 36.5 | 1.842 | 0
295 | 2022-12-22 04:56 | 1.3 | 18.1 | 38.2 | 36.4 | 1.838 | 0
296 | 2022-12-22 04:57 | 1.3 | 18.2 | 38 | 36.3 | 1.847 | 0
297 | 2022-12-22 04:58 | 1.1 | 18.1 | 37.9 | 36.1 | 1.846 | 0
298 | 2022-12-22 04:59 | 1.3 | 18.1 | 37.8 | 36 | 1.838 | 0
299 | 2022-12-22 05:00 | 1.1 | 18.1 | 37.6 | 35.9 | 1.842 | 0
300 | 2022-12-22 05:01 | 1.1 | 18.2 | 37.5 | 35.8 | 1.843 | 0
301 | 2022-12-22 05:02 | 1.1 | 18.3 | 37.3 | 35.6 | 1.844 | 0
302 | 2022-12-22 05:03 | 1.3 | 18.3 | 37.2 | 35.5 | 1.843 | 0
303 | 2022-12-22 05:04 | 1.1 | 18.2 | 37.1 | 35.4 | 1.838 | 0
304 | 2022-12-22 05:05 | 1.2 | 18.3 | 37.3 | 35.3 | 1.843 | 0
305 | 2022-12-22 05:06 | 1.1 | 18.1 | 37.6 | 35.5 | 1.839 | 0
306 | 2022-12-22 05:07 | 1.2 | 18.2 | 37.8 | 35.9 | 1.84 | 0
307 | 2022-12-22 05:08 | 1.2 | 18.2 | 37.7 | 35.9 | 1.842 | 0
308 | 2022-12-22 05:09 | 1.2 | 18.2 | 37.6 | 35.8 | 1.84 | 0
309 | 2022-12-22 05:10 | 1.2 | 18.2 | 37.5 | 35.8 | 1.844 | 0
310 | 2022-12-22 05:11 | 1.2 | 18.2 | 37.4 | 35.7 | 1.842 | 0
311 | 2022-12-22 05:12 | 1.2 | 18.2 | 37.3 | 35.6 | 1.843 | 0
312 | 2022-12-22 05:13 | 1.2 | 18.2 | 37.2 | 35.5 | 1.84 | 0
313 | 2022-12-22 05:14 | 1.3 | 18.3 | 37.1 | 35.4 | 1.839 | 0
314 | 2022-12-22 05:15 | 1.2 | 18.2 | 36.9 | 35.3 | 1.845 | 0
315 | 2022-12-22 05:16 | 1.2 | 18.2 | 36.8 | 35.1 | 1.836 | 0
316 | 2022-12-22 05:17 | 1.3 | 18.2 | 36.7 | 35.1 | 1.842 | 0
317 | 2022-12-22 05:18 | 1.3 | 18.2 | 36.7 | 35 | 1.84 | 0
318 | 2022-12-22 05:19 | 1.2 | 18.2 | 36.9 | 35.7 | 1.845 | 0
319 | 2022-12-22 05:20 | 1.2 | 18.3 | 37 | 36.3 | 1.838 | 0
320 | 2022-12-22 05:21 | 1.2 | 18.3 | 37.1 | 36.5 | 1.84 | 0
321 | 2022-12-22 05:22 | 1.3 | 18.3 | 37.2 | 36.5 | 1.794 | 0
322 | 2022-12-22 05:23 | 1.3 | 18.2 | 37.2 | 36.5 | 1.629 | 0
323 | 2022-12-22 05:24 | 1.3 | 18.2 | 37.2 | 36.5 | 1.553 | 0
324 | 2022-12-22 05:25 | 1.3 | 18.2 | 37.1 | 36.4 | 1.307 | 0
325 | 2022-12-22 05:26 | 1.3 | 18.1 | 37.1 | 36.4 | 0.97 | 0
326 | 2022-12-22 05:27 | 1.2 | 18.1 | 37 | 36.3 | 0.978 | 0
327 | 2022-12-22 05:28 | 1.4 | 18.1 | 37 | 36.2 | 0.97 | 0
328 | 2022-12-22 05:29 | 1.2 | 18.1 | 37.2 | 36.3 | 0.97 | 0
329 | 2022-12-22 05:30 | 1.4 | 18.1 | 37.8 | 36.6 | 0.978 | 0
330 | 2022-12-22 05:31 | 1.4 | 18.1 | 37.7 | 37.1 | 0.976 | 0
331 | 2022-12-22 05:32 | 1.3 | 18.1 | 37.4 | 36.8 | 0.975 | 0
332 | 2022-12-22 05:33 | 1.3 | 18.1 | 37.3 | 36.7 | 0.975 | 0
333 | 2022-12-22 05:34 | 1.4 | 18.1 | 37.4 | 36.6 | 0.969 | 0
334 | 2022-12-22 05:35 | 1.2 | 18.1 | 37.7 | 36.7 | 0.97 | 0
335 | 2022-12-22 05:36 | 1.4 | 18.1 | 38.2 | 37.1 | 0.974 | 0
336 | 2022-12-22 05:37 | 1.2 | 18.1 | 38.7 | 37.6 | 0.976 | 0
337 | 2022-12-22 05:38 | 1.4 | 18.1 | 39.2 | 38.1 | 0.978 | 0
338 | 2022-12-22 05:39 | 1.4 | 18 | 38.6 | 38 | 0.976 | 0
339 | 2022-12-22 05:40 | 1.3 | 18.1 | 38.6 | 37.9 | 0.975 | 0
340 | 2022-12-22 05:41 | 1.2 | 18.1 | 38.7 | 37.9 | 0.976 | 0
341 | 2022-12-22 05:42 | 1.3 | 18.1 | 38.6 | 37.9 | 0.974 | 0
342 | 2022-12-22 05:43 | 1.3 | 18 | 38.7 | 37.8 | 0.974 | 0
343 | 2022-12-22 05:44 | 1.4 | 18 | 38.6 | 37.9 | 0.978 | 0
344 | 2022-12-22 05:45 | 1.3 | 18 | 38.6 | 37.8 | 0.98 | 0
345 | 2022-12-22 05:46 | 1.4 | 18 | 38.6 | 37.8 | 0.98 | 0
346 | 2022-12-22 05:47 | 1.4 | 18 | 38.5 | 37.8 | 0.974 | 0
347 | 2022-12-22 05:48 | 1.2 | 18.1 | 38.5 | 37.7 | 0.976 | 0
348 | 2022-12-22 05:49 | 1.4 | 18 | 38.5 | 37.7 | 0.97 | 0
349 | 2022-12-22 05:50 | 1.3 | 18 | 38.4 | 37.7 | 0.976 | 0
350 | 2022-12-22 05:51 | 1.2 | 18.1 | 38.4 | 37.6 | 0.979 | 0
351 | 2022-12-22 05:52 | 1.3 | 18.1 | 38.3 | 37.6 | 0.975 | 0
352 | 2022-12-22 05:53 | 1.4 | 18.1 | 38.3 | 37.5 | 0.979 | 0
353 | 2022-12-22 05:54 | 1.2 | 18 | 38.3 | 37.5 | 0.978 | 0
354 | 2022-12-22 05:55 | 1.2 | 18 | 38.2 | 37.5 | 0.97 | 0
355 | 2022-12-22 05:56 | 1.2 | 18 | 38.2 | 37.4 | 0.975 | 0
356 | 2022-12-22 05:57 | 1.3 | 18 | 38.1 | 37.4 | 0.973 | 0
357 | 2022-12-22 05:58 | 1.2 | 17.9 | 38.1 | 37.4 | 0.974 | 0
358 | 2022-12-22 05:59 | 1.5 | 18 | 38.1 | 37.4 | 0.977 | 0
359 | 2022-12-22 06:00 | 1.4 | 18 | 38 | 37.3 | 0.973 | 0
360 | 2022-12-22 06:01 | 1.4 | 18 | 38 | 37.2 | 0.977 | 0
361 | 2022-12-22 06:02 | 1.5 | 17.9 | 37.9 | 37.2 | 0.975 | 0
362 | 2022-12-22 06:03 | 1.3 | 17.8 | 37.8 | 34.7 | 1.185 | 0
363 | 2022-12-22 06:04 | 1.4 | 17.9 | 37.8 | 35.4 | 1.534 | 0
364 | 2022-12-22 06:05 | 1.4 | 17.9 | 37.9 | 35.9 | 1.544 | 0
365 | 2022-12-22 06:06 | 1.3 | 18.1 | 37.9 | 35.4 | 1.704 | 0
366 | 2022-12-22 06:07 | 1.1 | 18.4 | 38.4 | 33.7 | 1.88 | 0
367 | 2022-12-22 06:08 | 1.4 | 18.6 | 38.6 | 36 | 1.889 | 0
368 | 2022-12-22 06:09 | 1.3 | 18.9 | 38.8 | 36.3 | 1.898 | 0
369 | 2022-12-22 06:10 | 1.2 | 19.2 | 39.3 | 36.5 | 1.892 | 0
370 | 2022-12-22 06:11 | 1.4 | 19.3 | 39.6 | 37 | 1.898 | 0
371 | 2022-12-22 06:12 | 1.2 | 19.3 | 39.9 | 37.2 | 1.899 | 0
372 | 2022-12-22 06:13 | 1.2 | 19.4 | 40.1 | 37.5 | 1.898 | 0
373 | 2022-12-22 06:14 | 1.4 | 19.5 | 39.9 | 37.7 | 1.89 | 0
374 | 2022-12-22 06:15 | 1.2 | 19.7 | 39.9 | 37.5 | 1.902 | 0
375 | 2022-12-22 06:16 | 1.2 | 19.6 | 39.8 | 35.5 | 2 | 0
376 | 2022-12-22 06:17 | 1.2 | 19.7 | 39.6 | 36.8 | 2.002 | 0
377 | 2022-12-22 06:18 | 1.3 | 19.8 | 39.2 | 36.7 | 2.005 | 0
378 | 2022-12-22 06:19 | 1.1 | 19.8 | 39 | 36.4 | 2.022 | 0
379 | 2022-12-22 06:20 | 1.3 | 19.9 | 38.9 | 36.3 | 2.008 | 0
380 | 2022-12-22 06:21 | 1.3 | 19.9 | 38.7 | 36.2 | 2.012 | 0
381 | 2022-12-22 06:22 | 1.2 | 20 | 38.5 | 35.9 | 2.001 | 0
382 | 2022-12-22 06:23 | 1.3 | 19.9 | 38.3 | 36.5 | 2.006 | 0
383 | 2022-12-22 06:24 | 1.2 | 19.6 | 38 | 36.4 | 2.004 | 0
384 | 2022-12-22 06:25 | 1.3 | 19.4 | 37.9 | 36.2 | 2.004 | 0
385 | 2022-12-22 06:26 | 1.1 | 19.2 | 37.8 | 36.1 | 2.004 | 0
386 | 2022-12-22 06:27 | 1.2 | 19 | 37.7 | 35.8 | 1.844 | 0
387 | 2022-12-22 06:28 | 1.1 | 18.9 | 37.5 | 35.8 | 1.835 | 0
388 | 2022-12-22 06:29 | 1.1 | 18.9 | 37.4 | 35.7 | 1.839 | 0
389 | 2022-12-22 06:30 | 1.1 | 18.8 | 37.2 | 35.5 | 1.84 | 0
390 | 2022-12-22 06:31 | 1.3 | 18.7 | 37.1 | 35.4 | 1.838 | 0
391 | 2022-12-22 06:32 | 1.1 | 18.7 | 37 | 35.3 | 1.842 | 0
392 | 2022-12-22 06:33 | 1.1 | 18.7 | 36.9 | 35.2 | 1.829 | 0
393 | 2022-12-22 06:34 | 1.1 | 18.6 | 36.8 | 35.1 | 1.831 | 0
394 | 2022-12-22 06:35 | 1.2 | 18.5 | 36.9 | 35.1 | 1.838 | 0
395 | 2022-12-22 06:36 | 1.4 | 18.6 | 37.4 | 35.3 | 1.845 | 0
396 | 2022-12-22 06:37 | 1.1 | 18.5 | 37.8 | 35.7 | 1.844 | 0
397 | 2022-12-22 06:38 | 1.2 | 18.4 | 38.1 | 36 | 1.834 | 0
398 | 2022-12-22 06:39 | 1.2 | 18.4 | 38.4 | 36.3 | 1.838 | 0
399 | 2022-12-22 06:40 | 1.3 | 18.5 | 38.8 | 36.6 | 1.838 | 0
400 | 2022-12-22 06:41 | 1.2 | 18.5 | 39.2 | 36.9 | 1.843 | 0
401 | 2022-12-22 06:42 | 1.4 | 18.5 | 39.5 | 37.3 | 1.838 | 0
402 | 2022-12-22 06:43 | 1.4 | 18.4 | 39.8 | 37.6 | 1.841 | 0
403 | 2022-12-22 06:44 | 1.1 | 18.5 | 40.2 | 37.9 | 1.832 | 0
404 | 2022-12-22 06:45 | 1.2 | 18.5 | 40.1 | 38.2 | 1.847 | 0
405 | 2022-12-22 06:46 | 1.4 | 18.5 | 40 | 38.1 | 1.84 | 0
406 | 2022-12-22 06:47 | 1.3 | 18.5 | 39.9 | 38 | 1.841 | 0
407 | 2022-12-22 06:48 | 1.2 | 18.5 | 39.9 | 37.9 | 1.842 | 0
408 | 2022-12-22 06:49 | 1.2 | 18.4 | 39.7 | 38.4 | 1.842 | 0
409 | 2022-12-22 06:50 | 1.4 | 18.4 | 39.6 | 38.3 | 1.843 | 0
410 | 2022-12-22 06:51 | 1.1 | 18.5 | 39.6 | 38.2 | 1.839 | 0
411 | 2022-12-22 06:52 | 1.1 | 18.4 | 39.5 | 38.8 | 1.824 | 0
412 | 2022-12-22 06:53 | 1.3 | 18.5 | 39.4 | 38.8 | 1.641 | 0
413 | 2022-12-22 06:54 | 1.3 | 18.4 | 39.4 | 38.7 | 1.64 | 0
414 | 2022-12-22 06:55 | 1.2 | 18.4 | 39.4 | 38.7 | 1.632 | 0
415 | 2022-12-22 06:56 | 1.2 | 18.4 | 39.3 | 38.7 | 1.594 | 0
416 | 2022-12-22 06:57 | 1.2 | 18.3 | 39.3 | 38.6 | 1.432 | 0
417 | 2022-12-22 06:58 | 1.3 | 18.3 | 39.2 | 38.5 | 0.979 | 0
418 | 2022-12-22 06:59 | 1.2 | 18.3 | 39.2 | 38.4 | 0.98 | 0
419 | 2022-12-22 07:00 | 1.3 | 18.2 | 39 | 38.3 | 0.979 | 0
420 | 2022-12-22 07:01 | 1.2 | 18.2 | 39 | 38.2 | 0.975 | 0
421 | 2022-12-22 07:02 | 1.3 | 18.2 | 38.9 | 38.2 | 0.978 | 0
422 | 2022-12-22 07:03 | 1.3 | 18.3 | 38.9 | 38.1 | 0.977 | 0
423 | 2022-12-22 07:04 | 1.3 | 18.2 | 38.9 | 38.1 | 0.973 | 0
424 | 2022-12-22 07:05 | 1.2 | 18.2 | 39.1 | 38.2 | 0.974 | 0
425 | 2022-12-22 07:06 | 1.4 | 18.1 | 39.5 | 38.4 | 0.976 | 0
426 | 2022-12-22 07:07 | 1.3 | 18.1 | 39.8 | 38.8 | 0.977 | 0
427 | 2022-12-22 07:08 | 1.3 | 18.2 | 40.5 | 39.2 | 0.981 | 0
428 | 2022-12-22 07:09 | 1.5 | 18.1 | 39.9 | 39.4 | 0.979 | 0
429 | 2022-12-22 07:10 | 1.4 | 18.2 | 39.9 | 39.1 | 0.977 | 0
430 | 2022-12-22 07:11 | 1.6 | 18.1 | 40 | 39.1 | 0.977 | 0
431 | 2022-12-22 07:12 | 1.5 | 18.1 | 40 | 39.1 | 0.977 | 0
432 | 2022-12-22 07:13 | 1.4 | 18.1 | 39.8 | 39.1 | 0.976 | 0
433 | 2022-12-22 07:14 | 1.6 | 18.1 | 39.7 | 39 | 0.978 | 0
434 | 2022-12-22 07:15 | 1.4 | 18.1 | 39.7 | 38.9 | 0.977 | 0
435 | 2022-12-22 07:16 | 1.5 | 18.1 | 39.7 | 38.9 | 0.975 | 0
436 | 2022-12-22 07:17 | 1.4 | 18.1 | 39.6 | 38.8 | 0.979 | 0
437 | 2022-12-22 07:18 | 1.5 | 18.1 | 39.6 | 38.8 | 0.976 | 0
438 | 2022-12-22 07:19 | 1.3 | 18.2 | 39.5 | 38.8 | 0.973 | 0
439 | 2022-12-22 07:20 | 1.4 | 18.1 | 39.4 | 38.7 | 0.975 | 0
440 | 2022-12-22 07:21 | 1.6 | 18.1 | 39.5 | 38.6 | 0.976 | 0
441 | 2022-12-22 07:22 | 1.4 | 18.1 | 39.5 | 38.6 | 0.976 | 0
442 | 2022-12-22 07:23 | 1.5 | 18 | 39.4 | 38.6 | 0.977 | 0
443 | 2022-12-22 07:24 | 1.6 | 18.1 | 39.4 | 38.6 | 0.974 | 0
444 | 2022-12-22 07:25 | 1.7 | 18 | 39.3 | 38.5 | 0.977 | 0
445 | 2022-12-22 07:26 | 1.7 | 18 | 39.3 | 38.5 | 0.971 | 0
446 | 2022-12-22 07:27 | 1.6 | 18 | 39.3 | 38.5 | 0.974 | 0
447 | 2022-12-22 07:28 | 1.5 | 18 | 39.2 | 38.4 | 0.979 | 0
448 | 2022-12-22 07:29 | 1.5 | 18 | 39.2 | 38.4 | 0.975 | 0
449 | 2022-12-22 07:30 | 1.7 | 18 | 39.1 | 38.4 | 0.98 | 0
450 | 2022-12-22 07:31 | 1.4 | 18 | 39 | 38.3 | 0.978 | 0
451 | 2022-12-22 07:32 | 1.4 | 18 | 39 | 38.2 | 0.976 | 0
452 | 2022-12-22 07:33 | 1.4 | 18 | 38.8 | 32.9 | 1.464 | 1
453 | 2022-12-22 07:34 | 1.5 | 17.9 | 38.9 | 37.1 | 1.628 | 1
454 | 2022-12-22 07:35 | 1.5 | 18 | 39 | 37.4 | 1.628 | 1
455 | 2022-12-22 07:36 | 1.5 | 18 | 39.2 | 37.4 | 1.635 | 2
456 | 2022-12-22 07:37 | 1.4 | 18 | 39.6 | 37.8 | 1.638 | 2
457 | 2022-12-22 07:38 | 1.4 | 18 | 40.1 | 38.2 | 1.636 | 2
458 | 2022-12-22 07:39 | 1.5 | 18 | 40.5 | 35.3 | 1.837 | 3
459 | 2022-12-22 07:40 | 1.6 | 18 | 40.8 | 38.5 | 1.841 | 3
460 | 2022-12-22 07:41 | 1.4 | 18 | 41.2 | 38.8 | 1.849 | 4
461 | 2022-12-22 07:42 | 1.4 | 18 | 41.6 | 39.1 | 1.847 | 4
462 | 2022-12-22 07:43 | 1.5 | 18 | 41.9 | 39.5 | 1.848 | 5
463 | 2022-12-22 07:44 | 1.4 | 18 | 42.2 | 39.7 | 1.852 | 5
464 | 2022-12-22 07:45 | 1.5 | 18 | 42.6 | 40 | 1.844 | 5
465 | 2022-12-22 07:46 | 1.4 | 18 | 42.9 | 40.3 | 1.857 | 6
466 | 2022-12-22 07:47 | 1.6 | 18 | 43.1 | 40.6 | 1.853 | 6
467 | 2022-12-22 07:48 | 1.4 | 18.1 | 43.5 | 40.9 | 1.847 | 7
468 | 2022-12-22 07:49 | 1.5 | 18 | 43.7 | 41.2 | 1.852 | 7
469 | 2022-12-22 07:50 | 1.5 | 18 | 43.9 | 41.4 | 1.849 | 8
470 | 2022-12-22 07:51 | 1.6 | 18 | 43.8 | 41.5 | 1.854 | 8
471 | 2022-12-22 07:52 | 1.8 | 18.1 | 43.9 | 41.5 | 1.851 | 9
472 | 2022-12-22 07:53 | 1.8 | 18 | 43.9 | 41.5 | 1.851 | 9
473 | 2022-12-22 07:54 | 1.7 | 18 | 44.3 | 41.6 | 1.849 | 10
474 | 2022-12-22 07:55 | 1.8 | 18.1 | 44.5 | 41.9 | 1.853 | 11
475 | 2022-12-22 07:56 | 1.6 | 18.1 | 44.9 | 42.1 | 1.85 | 11
476 | 2022-12-22 07:57 | 1.8 | 18.1 | 45.2 | 42.4 | 1.858 | 12
477 | 2022-12-22 07:58 | 1.8 | 18.1 | 45.4 | 42.8 | 1.851 | 12
478 | 2022-12-22 07:59 | 1.8 | 18 | 45.7 | 43 | 1.857 | 13
479 | 2022-12-22 08:00 | 1.8 | 18.1 | 45.6 | 43.2 | 1.853 | 13
480 | 2022-12-22 08:01 | 1.8 | 18.1 | 45.6 | 43.3 | 1.854 | 14
481 | 2022-12-22 08:02 | 1.8 | 18.2 | 45.5 | 43.1 | 1.845 | 14
482 | 2022-12-22 08:03 | 1.8 | 18.2 | 45.5 | 43 | 1.854 | 15
483 | 2022-12-22 08:04 | 1.8 | 18.3 | 45.7 | 38.7 | 1.978 | 15
484 | 2022-12-22 08:05 | 1.9 | 18.2 | 45.9 | 41.9 | 2.011 | 16
485 | 2022-12-22 08:06 | 2 | 18.5 | 45.6 | 42.3 | 2.02 | 16
486 | 2022-12-22 08:07 | 2 | 18.8 | 45.9 | 42 | 2.018 | 17
487 | 2022-12-22 08:08 | 1.9 | 19.2 | 46.1 | 42.4 | 2.014 | 17
488 | 2022-12-22 08:09 | 1.9 | 19.4 | 46.4 | 42.5 | 2.021 | 18
489 | 2022-12-22 08:10 | 2.1 | 19.6 | 46.5 | 42.7 | 2.012 | 18
490 | 2022-12-22 08:11 | 2.2 | 19.8 | 46.7 | 42.9 | 2.014 | 19
491 | 2022-12-22 08:12 | 2.1 | 19.9 | 46.6 | 43 | 2.023 | 19
492 | 2022-12-22 08:13 | 2.2 | 20 | 46.4 | 42.9 | 2.014 | 20
493 | 2022-12-22 08:14 | 2.2 | 20.2 | 46.1 | 42.7 | 2.014 | 20
494 | 2022-12-22 08:15 | 2.1 | 20.3 | 45.8 | 42.5 | 2.011 | 21
495 | 2022-12-22 08:16 | 2.1 | 20.4 | 45.5 | 42.3 | 2.011 | 21
496 | 2022-12-22 08:17 | 2.3 | 20.4 | 45.3 | 42 | 2.01 | 22
497 | 2022-12-22 08:18 | 2.1 | 20.4 | 45 | 41.8 | 2.018 | 22
498 | 2022-12-22 08:19 | 2.3 | 20.5 | 44.7 | 41.5 | 2.023 | 23
499 | 2022-12-22 08:20 | 2.3 | 20.5 | 44.5 | 41.3 | 2.013 | 23
500 | 2022-12-22 08:21 | 2.2 | 20.5 | 44.3 | 41.1 | 2.013 | 24
501 | 2022-12-22 08:22 | 2.2 | 20.6 | 43.9 | 40.9 | 2.015 | 24
502 | 2022-12-22 08:23 | 2.2 | 20.5 | 43.7 | 40.6 | 2.011 | 25
503 | 2022-12-22 08:24 | 2.2 | 20.6 | 43.4 | 40.4 | 2.012 | 25
504 | 2022-12-22 08:25 | 2.2 | 20.5 | 43.2 | 40.2 | 2.012 | 26
505 | 2022-12-22 08:26 | 2.3 | 20.6 | 42.9 | 40 | 2.017 | 26
506 | 2022-12-22 08:27 | 2.2 | 20.6 | 42.7 | 39.7 | 2.011 | 26
507 | 2022-12-22 08:28 | 2.2 | 20.6 | 42.4 | 39.6 | 2.008 | 27
508 | 2022-12-22 08:29 | 2.4 | 20.6 | 42.2 | 39.3 | 2.014 | 28
509 | 2022-12-22 08:30 | 2.5 | 20.6 | 42 | 39.1 | 2.006 | 28
510 | 2022-12-22 08:31 | 2.2 | 20.7 | 41.7 | 38.9 | 2.002 | 28
511 | 2022-12-22 08:32 | 2.2 | 20.7 | 41.5 | 38.7 | 2.008 | 29
512 | 2022-12-22 08:33 | 2.2 | 20.6 | 41.3 | 38.5 | 2.006 | 29
513 | 2022-12-22 08:34 | 2.4 | 20.6 | 41.2 | 38.3 | 2.009 | 29
514 | 2022-12-22 08:35 | 2.4 | 20.6 | 41.3 | 38.3 | 2.014 | 30
515 | 2022-12-22 08:36 | 2.2 | 20.6 | 41.6 | 38.3 | 2.012 | 30
516 | 2022-12-22 08:37 | 2.3 | 20.6 | 41.8 | 38.6 | 2.006 | 31
517 | 2022-12-22 08:38 | 2.5 | 20.7 | 42 | 38.8 | 2.013 | 31
518 | 2022-12-22 08:39 | 2.3 | 20.7 | 42.2 | 39 | 2.011 | 32
519 | 2022-12-22 08:40 | 2.3 | 20.7 | 42.4 | 39.1 | 2.01 | 32
520 | 2022-12-22 08:41 | 2.2 | 20.7 | 42.6 | 39.4 | 2.009 | 32
521 | 2022-12-22 08:42 | 2.5 | 20.8 | 42.8 | 39.5 | 2.018 | 33
522 | 2022-12-22 08:43 | 2.6 | 20.8 | 42.9 | 39.7 | 2.013 | 33
523 | 2022-12-22 08:44 | 2.4 | 20.8 | 43 | 39.8 | 2.013 | 33
524 | 2022-12-22 08:45 | 2.7 | 20.9 | 42.6 | 39.8 | 2.007 | 33
525 | 2022-12-22 08:46 | 2.5 | 20.9 | 42.4 | 39.5 | 2.013 | 34
526 | 2022-12-22 08:47 | 2.5 | 21 | 42.2 | 39.3 | 2.013 | 34
527 | 2022-12-22 08:48 | 2.7 | 20.9 | 42 | 39.1 | 2.009 | 34
528 | 2022-12-22 08:49 | 2.7 | 20.9 | 41.7 | 38.9 | 2.002 | 35
529 | 2022-12-22 08:50 | 2.6 | 20.9 | 41.5 | 38.7 | 2.006 | 36
530 | 2022-12-22 08:51 | 2.7 | 20.9 | 41.2 | 38.5 | 2.007 | 36
531 | 2022-12-22 08:52 | 2.8 | 20.9 | 41 | 38.3 | 2.016 | 37
532 | 2022-12-22 08:53 | 2.6 | 20.9 | 40.8 | 38.1 | 2.011 | 37
533 | 2022-12-22 08:54 | 2.8 | 20.9 | 40.6 | 37.9 | 2.009 | 38
534 | 2022-12-22 08:55 | 2.9 | 20.9 | 40.3 | 37.7 | 2.004 | 38
535 | 2022-12-22 08:56 | 2.7 | 20.9 | 40.1 | 37.5 | 2.01 | 39
536 | 2022-12-22 08:57 | 2.7 | 21 | 39.9 | 37.3 | 2.004 | 39
537 | 2022-12-22 08:58 | 2.7 | 21 | 39.7 | 37.1 | 2 | 40
538 | 2022-12-22 08:59 | 2.8 | 21 | 39.5 | 36.9 | 2.007 | 42
539 | 2022-12-22 09:00 | 3 | 20.9 | 39.2 | 36.8 | 1.999 | 44
540 | 2022-12-22 09:01 | 3 | 20.9 | 39 | 36.5 | 2 | 45
541 | 2022-12-22 09:02 | 2.9 | 20.9 | 38.8 | 36.4 | 2.002 | 45
542 | 2022-12-22 09:03 | 3 | 20.9 | 38.6 | 36.2 | 2.003 | 46
543 | 2022-12-22 09:04 | 2.9 | 20.9 | 38.5 | 36 | 1.999 | 47
544 | 2022-12-22 09:05 | 3.1 | 20.8 | 38.5 | 35.9 | 2.001 | 49
545 | 2022-12-22 09:06 | 3 | 20.8 | 38.7 | 36 | 1.99 | 51
546 | 2022-12-22 09:07 | 3 | 20.8 | 39 | 36.2 | 2.003 | 52
547 | 2022-12-22 09:08 | 3 | 20.8 | 39.3 | 36.4 | 2.009 | 52
548 | 2022-12-22 09:09 | 3 | 20.7 | 39.7 | 36.6 | 2.007 | 53
549 | 2022-12-22 09:10 | 3.2 | 20.7 | 39.9 | 37 | 2.001 | 55
550 | 2022-12-22 09:11 | 3.1 | 20.7 | 40.2 | 37.1 | 2.003 | 61
551 | 2022-12-22 09:12 | 3.2 | 20.7 | 40.3 | 37.4 | 2.007 | 71
552 | 2022-12-22 09:13 | 3.3 | 20.8 | 40.5 | 37.6 | 2.002 | 82
553 | 2022-12-22 09:14 | 3.1 | 20.9 | 40.8 | 37.7 | 2.007 | 92
554 | 2022-12-22 09:15 | 3.3 | 20.9 | 40.7 | 38 | 2.007 | 97
555 | 2022-12-22 09:16 | 3.1 | 20.9 | 40.7 | 37.9 | 2.006 | 102
556 | 2022-12-22 09:17 | 3.3 | 20.9 | 40.5 | 37.8 | 2.012 | 104
557 | 2022-12-22 09:18 | 3.4 | 20.8 | 40.3 | 37.6 | 2.003 | 103
558 | 2022-12-22 09:19 | 3.4 | 21 | 40.1 | 37.5 | 2.006 | 96
559 | 2022-12-22 09:20 | 3.4 | 21 | 39.9 | 37.3 | 2.002 | 93
560 | 2022-12-22 09:21 | 3.6 | 21 | 40.1 | 37.1 | 1.946 | 97
561 | 2022-12-22 09:22 | 3.5 | 21 | 39.9 | 37.2 | 1.946 | 103
562 | 2022-12-22 09:23 | 3.6 | 21 | 39.7 | 37.1 | 1.932 | 111
563 | 2022-12-22 09:24 | 3.7 | 21 | 39.5 | 36.8 | 1.913 | 120
564 | 2022-12-22 09:25 | 3.7 | 21 | 39.3 | 36.6 | 1.946 | 123
565 | 2022-12-22 09:26 | 3.8 | 20.9 | 39 | 36.5 | 1.944 | 126
566 | 2022-12-22 09:27 | 3.9 | 21 | 38.6 | 36.3 | 1.928 | 134
567 | 2022-12-22 09:28 | 4 | 21 | 38.3 | 35.9 | 1.933 | 127
568 | 2022-12-22 09:29 | 4 | 20.9 | 38.1 | 35.7 | 1.917 | 130
569 | 2022-12-22 09:30 | 4.1 | 21 | 37.9 | 35.2 | 1.926 | 155
570 | 2022-12-22 09:31 | 4.3 | 20.8 | 37.6 | 35 | 1.917 | 179
571 | 2022-12-22 09:32 | 4.2 | 20.9 | 37.4 | 34.8 | 1.917 | 194
572 | 2022-12-22 09:33 | 4.5 | 20.9 | 37.2 | 34.6 | 1.923 | 177
573 | 2022-12-22 09:34 | 4.5 | 20.9 | 37.1 | 34.4 | 1.912 | 151
574 | 2022-12-22 09:35 | 4.3 | 20.9 | 37.3 | 34.3 | 1.916 | 145
575 | 2022-12-22 09:36 | 4.5 | 20.8 | 37.6 | 34.5 | 1.919 | 144
576 | 2022-12-22 09:37 | 4.5 | 20.9 | 37.8 | 34.8 | 1.914 | 213
577 | 2022-12-22 09:38 | 4.8 | 21 | 38 | 35 | 1.917 | 238
578 | 2022-12-22 09:39 | 5 | 21.1 | 38.3 | 35.1 | 1.917 | 376
579 | 2022-12-22 09:40 | 5 | 21.1 | 38.5 | 35.4 | 1.925 | 516
580 | 2022-12-22 09:41 | 5.3 | 21.1 | 38.8 | 35.6 | 1.92 | 572
581 | 2022-12-22 09:42 | 5.9 | 21 | 39 | 35.8 | 1.922 | 635
582 | 2022-12-22 09:43 | 6.3 | 21.1 | 39.2 | 35.9 | 1.918 | 630
583 | 2022-12-22 09:44 | 6.9 | 21 | 39.5 | 36.2 | 1.924 | 648
584 | 2022-12-22 09:45 | 6.4 | 21.1 | 39.6 | 36.4 | 1.922 | 644
585 | 2022-12-22 09:46 | 6.6 | 21.1 | 39.9 | 36.5 | 1.918 | 647
586 | 2022-12-22 09:47 | 6.9 | 21.1 | 40.1 | 36.7 | 1.92 | 648
587 | 2022-12-22 09:48 | 7.2 | 21.2 | 40.3 | 36.9 | 1.92 | 654
588 | 2022-12-22 09:49 | 7.6 | 21.1 | 40.5 | 37.1 | 1.923 | 666
589 | 2022-12-22 09:50 | 8 | 21.1 | 40.7 | 37.2 | 1.921 | 669
590 | 2022-12-22 09:51 | 8.4 | 21.3 | 40.9 | 37.4 | 1.928 | 671
591 | 2022-12-22 09:52 | 8.3 | 21.3 | 41.1 | 37.6 | 1.929 | 682
592 | 2022-12-22 09:53 | 8.2 | 21.4 | 41.2 | 37.8 | 1.929 | 676
593 | 2022-12-22 09:54 | 8.3 | 21.4 | 41.4 | 37.9 | 1.931 | 627
594 | 2022-12-22 09:55 | 8.3 | 21.4 | 41.6 | 38 | 1.927 | 672
595 | 2022-12-22 09:56 | 8.6 | 21.4 | 41.8 | 38.2 | 1.928 | 555
596 | 2022-12-22 09:57 | 9 | 21.5 | 42 | 38.4 | 1.932 | 400
597 | 2022-12-22 09:58 | 9.4 | 21.5 | 42.1 | 38.6 | 1.934 | 609
598 | 2022-12-22 09:59 | 9.7 | 21.6 | 42.1 | 38.6 | 1.927 | 304
599 | 2022-12-22 10:00 | 9.6 | 21.6 | 41.7 | 38.6 | 1.928 | 527
600 | 2022-12-22 10:01 | 9.5 | 21.6 | 41.5 | 38.3 | 1.925 | 692
601 | 2022-12-22 10:02 | 9.8 | 21.7 | 41.2 | 38.1 | 1.93 | 613
602 | 2022-12-22 10:03 | 10.5 | 21.8 | 41 | 37.9 | 1.935 | 246
603 | 2022-12-22 10:04 | 10.7 | 21.8 | 41 | 37.8 | 1.928 | 420
604 | 2022-12-22 10:05 | 10.9 | 21.7 | 41.2 | 37.7 | 1.929 | 291
605 | 2022-12-22 10:06 | 10.7 | 21.6 | 41.4 | 37.9 | 1.934 | 506
606 | 2022-12-22 10:07 | 10.8 | 21.6 | 41.5 | 38 | 1.935 | 441
607 | 2022-12-22 10:08 | 10.5 | 21.7 | 41.7 | 38.1 | 1.932 | 375
608 | 2022-12-22 10:09 | 10.5 | 21.6 | 41.9 | 38.4 | 1.934 | 576
609 | 2022-12-22 10:10 | 10.7 | 21.6 | 41.8 | 38.5 | 1.932 | 730
610 | 2022-12-22 10:11 | 10.8 | 21.7 | 41.6 | 38.5 | 1.932 | 135
611 | 2022-12-22 10:12 | 10.5 | 21.7 | 41.4 | 38.5 | 1.939 | 127
612 | 2022-12-22 10:13 | 10.3 | 21.8 | 41.1 | 38.7 | 1.937 | 215
613 | 2022-12-22 10:14 | 10.3 | 21.9 | 41 | 38.4 | 1.935 | 123
614 | 2022-12-22 10:15 | 10.1 | 21.8 | 40.8 | 38.3 | 1.932 | 116
615 | 2022-12-22 10:16 | 9.3 | 21.8 | 40.7 | 38.2 | 1.929 | 113
616 | 2022-12-22 10:17 | 8.9 | 21.7 | 40.5 | 37.7 | 1.788 | 117
617 | 2022-12-22 10:18 | 8.6 | 21.6 | 40.3 | 37.7 | 1.78 | 132
618 | 2022-12-22 10:19 | 8.3 | 21.6 | 40 | 37.4 | 1.777 | 130
619 | 2022-12-22 10:20 | 8 | 21.7 | 39.8 | 37.2 | 1.781 | 138
620 | 2022-12-22 10:21 | 8 | 21.7 | 39.6 | 37 | 1.781 | 561
621 | 2022-12-22 10:22 | 8.2 | 21.7 | 39.4 | 36.9 | 1.776 | 733
622 | 2022-12-22 10:23 | 8.4 | 21.7 | 39.2 | 36.7 | 1.778 | 765
623 | 2022-12-22 10:24 | 8.9 | 21.7 | 39.1 | 36.6 | 1.78 | 167
624 | 2022-12-22 10:25 | 9 | 21.6 | 38.9 | 36.5 | 1.776 | 169
625 | 2022-12-22 10:26 | 9.1 | 21.6 | 38.7 | 36.2 | 1.777 | 268
626 | 2022-12-22 10:27 | 9 | 21.6 | 38.5 | 36.1 | 1.781 | 593
627 | 2022-12-22 10:28 | 8.5 | 21.6 | 38.4 | 36 | 1.776 | 244
628 | 2022-12-22 10:29 | 8.2 | 21.6 | 38.1 | 35.8 | 1.775 | 141
629 | 2022-12-22 10:30 | 7.8 | 21.6 | 37.9 | 35.6 | 1.775 | 129
630 | 2022-12-22 10:31 | 7.8 | 21.6 | 37.8 | 35.4 | 1.775 | 134
631 | 2022-12-22 10:32 | 7.7 | 21.6 | 37.6 | 35.3 | 1.773 | 144
632 | 2022-12-22 10:33 | 7.5 | 21.6 | 37.5 | 35.2 | 1.772 | 154
633 | 2022-12-22 10:34 | 7.7 | 21.5 | 37.4 | 35.1 | 1.776 | 315
634 | 2022-12-22 10:35 | 7.5 | 21.5 | 37.5 | 35 | 1.776 | 289
635 | 2022-12-22 10:36 | 7.9 | 21.6 | 38 | 35.2 | 1.775 | 466
636 | 2022-12-22 10:37 | 8.1 | 21.6 | 38.3 | 35.6 | 1.769 | 641
637 | 2022-12-22 10:38 | 8.7 | 21.5 | 38.5 | 35.8 | 1.772 | 249
638 | 2022-12-22 10:39 | 8.5 | 21.6 | 38.8 | 36 | 1.776 | 180
639 | 2022-12-22 10:40 | 8.5 | 21.6 | 39 | 36.1 | 1.823 | 442
640 | 2022-12-22 10:41 | 8.7 | 21.6 | 39.3 | 35.9 | 1.926 | 385
641 | 2022-12-22 10:42 | 9.1 | 21.6 | 39.5 | 36.3 | 1.937 | 776
642 | 2022-12-22 10:43 | 9.2 | 21.6 | 39.7 | 36.5 | 1.929 | 196
643 | 2022-12-22 10:44 | 9.5 | 21.8 | 39.8 | 36.7 | 1.926 | 158
644 | 2022-12-22 10:45 | 9.4 | 21.8 | 39.6 | 36.7 | 1.934 | 155
645 | 2022-12-22 10:46 | 9.5 | 21.9 | 39.3 | 36.5 | 1.935 | 206
646 | 2022-12-22 10:47 | 9.5 | 22 | 39.1 | 36.3 | 1.932 | 238
647 | 2022-12-22 10:48 | 9.6 | 21.8 | 39 | 36.9 | 1.935 | 168
648 | 2022-12-22 10:49 | 9.5 | 21.5 | 38.8 | 36.8 | 1.933 | 164
649 | 2022-12-22 10:50 | 8.9 | 21.3 | 38.7 | 36.7 | 1.936 | 157
650 | 2022-12-22 10:51 | 8.7 | 21.1 | 38.6 | 36.6 | 1.931 | 149
651 | 2022-12-22 10:52 | 8.3 | 21 | 38.5 | 36.2 | 1.808 | 146
652 | 2022-12-22 10:53 | 8.3 | 20.9 | 38.3 | 36.2 | 1.783 | 155
653 | 2022-12-22 10:54 | 8.3 | 20.8 | 38.1 | 36.1 | 1.781 | 161
654 | 2022-12-22 10:55 | 8.2 | 20.7 | 38 | 35.9 | 1.788 | 411
655 | 2022-12-22 10:56 | 8.4 | 20.7 | 37.8 | 35.8 | 1.783 | 372
656 | 2022-12-22 10:57 | 9 | 20.7 | 37.7 | 35.7 | 1.784 | 319
657 | 2022-12-22 10:58 | 9.2 | 20.6 | 37.5 | 35.6 | 1.777 | 612
658 | 2022-12-22 10:59 | 9.6 | 20.6 | 37.4 | 35.4 | 1.781 | 770
659 | 2022-12-22 11:00 | 9.7 | 20.6 | 37.3 | 35.3 | 1.779 | 263
660 | 2022-12-22 11:01 | 9.3 | 20.6 | 37.1 | 35.2 | 1.778 | 327
661 | 2022-12-22 11:02 | 8.9 | 20.6 | 37 | 35 | 1.784 | 177
662 | 2022-12-22 11:03 | 8.5 | 20.5 | 36.8 | 35 | 1.783 | 185
663 | 2022-12-22 11:04 | 8.5 | 20.5 | 36.9 | 34.8 | 1.782 | 192
664 | 2022-12-22 11:05 | 8.2 | 20.5 | 37.2 | 34.9 | 1.777 | 237
665 | 2022-12-22 11:06 | 8.5 | 20.4 | 37.6 | 35.2 | 1.78 | 434
666 | 2022-12-22 11:07 | 8.6 | 20.5 | 38.1 | 35.5 | 1.776 | 317
667 | 2022-12-22 11:08 | 8.6 | 20.7 | 38.3 | 36 | 1.779 | 342
668 | 2022-12-22 11:09 | 8.7 | 20.7 | 38.6 | 35.9 | 1.895 | 569
669 | 2022-12-22 11:10 | 8.7 | 20.8 | 38.9 | 35.6 | 1.928 | 697
670 | 2022-12-22 11:11 | 9.3 | 20.9 | 39.1 | 36 | 1.928 | 887
671 | 2022-12-22 11:12 | 10 | 21.1 | 39.2 | 36.1 | 1.938 | 896
672 | 2022-12-22 11:13 | 10.4 | 21.3 | 39.4 | 36.8 | 1.936 | 893
673 | 2022-12-22 11:14 | 10.9 | 21.5 | 38.9 | 36.9 | 1.932 | 864
674 | 2022-12-22 11:15 | 11.1 | 21.6 | 38.9 | 36.5 | 1.932 | 852
675 | 2022-12-22 11:16 | 11.1 | 21.6 | 38.8 | 36.5 | 1.93 | 857
676 | 2022-12-22 11:17 | 11.1 | 21.6 | 38.7 | 36.1 | 1.774 | 859
677 | 2022-12-22 11:18 | 11.2 | 21.6 | 38.5 | 36.1 | 1.779 | 858
678 | 2022-12-22 11:19 | 11.4 | 21.7 | 38.3 | 35.9 | 1.772 | 860
679 | 2022-12-22 11:20 | 11.9 | 21.8 | 38.2 | 35.8 | 1.772 | 855
680 | 2022-12-22 11:21 | 12 | 21.8 | 38 | 35.7 | 1.773 | 865
681 | 2022-12-22 11:22 | 12.2 | 21.8 | 37.8 | 35.5 | 1.776 | 872
682 | 2022-12-22 11:23 | 12.3 | 21.8 | 37.6 | 35.3 | 1.77 | 712
683 | 2022-12-22 11:24 | 11.9 | 21.8 | 37.5 | 35.2 | 1.775 | 411
684 | 2022-12-22 11:25 | 11.9 | 21.8 | 37.3 | 35.1 | 1.769 | 355
685 | 2022-12-22 11:26 | 11.3 | 21.9 | 37.1 | 34.9 | 1.772 | 385
686 | 2022-12-22 11:27 | 11.4 | 21.8 | 37 | 34.8 | 1.772 | 319
687 | 2022-12-22 11:28 | 11.3 | 21.8 | 36.9 | 34.6 | 1.771 | 600
688 | 2022-12-22 11:29 | 11.2 | 21.8 | 36.8 | 34.5 | 1.778 | 335
689 | 2022-12-22 11:30 | 10.9 | 21.5 | 36.8 | 35.3 | 1.775 | 281
690 | 2022-12-22 11:31 | 11.2 | 21.3 | 37.1 | 35.3 | 1.771 | 301
691 | 2022-12-22 11:32 | 11.2 | 21.1 | 37.2 | 35.6 | 1.77 | 287
692 | 2022-12-22 11:33 | 11.1 | 20.9 | 37.2 | 35.6 | 1.741 | 314
693 | 2022-12-22 11:34 | 11.1 | 20.7 | 37.2 | 35.4 | 1.475 | 298
694 | 2022-12-22 11:35 | 11.2 | 20.7 | 37.4 | 35.5 | 1.47 | 331
695 | 2022-12-22 11:36 | 10.9 | 20.6 | 37.8 | 35.8 | 1.476 | 347
696 | 2022-12-22 11:37 | 11.2 | 20.6 | 38.1 | 36.1 | 1.474 | 440
697 | 2022-12-22 11:38 | 11.1 | 20.4 | 38.5 | 36.4 | 1.474 | 388
698 | 2022-12-22 11:39 | 11 | 20.5 | 38.9 | 36.7 | 1.472 | 312
699 | 2022-12-22 11:40 | 10.8 | 20.4 | 39.2 | 37.1 | 1.475 | 280
700 | 2022-12-22 11:41 | 10.7 | 20.4 | 39.6 | 37.4 | 1.476 | 266
701 | 2022-12-22 11:42 | 10.7 | 20.4 | 40 | 37.8 | 1.482 | 264
702 | 2022-12-22 11:43 | 10.6 | 20.4 | 40.5 | 38.1 | 1.477 | 264
703 | 2022-12-22 11:44 | 10.7 | 20.4 | 40.8 | 38.7 | 1.477 | 254
704 | 2022-12-22 11:45 | 10.7 | 20.4 | 40.4 | 38.7 | 1.479 | 244
705 | 2022-12-22 11:46 | 10.6 | 20.3 | 40.4 | 38.4 | 1.475 | 242
706 | 2022-12-22 11:47 | 10.6 | 20.3 | 40.4 | 38.4 | 1.481 | 259
707 | 2022-12-22 11:48 | 10.5 | 20.3 | 40.3 | 38.4 | 1.479 | 293
708 | 2022-12-22 11:49 | 10.5 | 20.4 | 40.2 | 38.3 | 1.501 | 348
709 | 2022-12-22 11:50 | 10.5 | 20.5 | 40.1 | 34.7 | 1.897 | 649
710 | 2022-12-22 11:51 | 10.8 | 20.6 | 39.9 | 36.9 | 1.94 | 705
711 | 2022-12-22 11:52 | 11.1 | 20.9 | 39.2 | 36.8 | 1.943 | 312
712 | 2022-12-22 11:53 | 11.2 | 21.1 | 39.1 | 36.3 | 1.934 | 293
713 | 2022-12-22 11:54 | 10.9 | 21.3 | 38.9 | 36.2 | 1.94 | 254
714 | 2022-12-22 11:55 | 10.8 | 21.4 | 38.7 | 36 | 1.937 | 251
715 | 2022-12-22 11:56 | 10.6 | 21.6 | 38.5 | 35.9 | 1.935 | 245
716 | 2022-12-22 11:57 | 10.7 | 21.7 | 38.3 | 35.7 | 1.93 | 245
717 | 2022-12-22 11:58 | 10.7 | 21.8 | 38.1 | 35.5 | 1.934 | 266
718 | 2022-12-22 11:59 | 10.4 | 22 | 37.9 | 35.3 | 1.928 | 268
719 | 2022-12-22 12:00 | 10.6 | 22 | 37.7 | 35.2 | 1.93 | 297
720 | 2022-12-22 12:01 | 10.4 | 22 | 37.5 | 35 | 1.934 | 301
721 | 2022-12-22 12:02 | 10.6 | 22 | 37.3 | 35.5 | 1.937 | 460
722 | 2022-12-22 12:03 | 10.7 | 21.6 | 37.2 | 35.4 | 1.933 | 346
723 | 2022-12-22 12:04 | 10.8 | 21.4 | 37.3 | 35.3 | 1.928 | 350
724 | 2022-12-22 12:05 | 11 | 21.2 | 37.6 | 35.3 | 1.909 | 359
725 | 2022-12-22 12:06 | 10.9 | 21.1 | 38 | 35.6 | 1.779 | 787
726 | 2022-12-22 12:07 | 10.9 | 21 | 38.2 | 35.9 | 1.782 | 359
727 | 2022-12-22 12:08 | 10.9 | 20.9 | 38.5 | 36.2 | 1.787 | 318
728 | 2022-12-22 12:09 | 10.8 | 20.8 | 38.9 | 36.4 | 1.783 | 441
729 | 2022-12-22 12:10 | 10.8 | 20.8 | 39.2 | 37 | 1.788 | 408
730 | 2022-12-22 12:11 | 10.9 | 20.8 | 39.3 | 37.6 | 1.789 | 622
731 | 2022-12-22 12:12 | 10.9 | 20.7 | 39.1 | 37.6 | 1.787 | 390
732 | 2022-12-22 12:13 | 11 | 20.8 | 39.1 | 37.5 | 1.786 | 370
733 | 2022-12-22 12:14 | 11 | 20.6 | 39.1 | 37.5 | 1.756 | 838
734 | 2022-12-22 12:15 | 11.2 | 20.5 | 39 | 37.2 | 1.484 | 487
735 | 2022-12-22 12:16 | 11.2 | 20.6 | 38.8 | 37.1 | 1.474 | 793
736 | 2022-12-22 12:17 | 11.2 | 20.5 | 38.7 | 37 | 1.472 | 383
737 | 2022-12-22 12:18 | 11 | 20.4 | 38.7 | 36.9 | 1.481 | 324
738 | 2022-12-22 12:19 | 11 | 20.4 | 38.6 | 36.9 | 1.477 | 367
739 | 2022-12-22 12:20 | 11.4 | 20.4 | 38.5 | 36.8 | 1.471 | 843
740 | 2022-12-22 12:21 | 11.4 | 20.3 | 38.4 | 36.7 | 1.476 | 833
741 | 2022-12-22 12:22 | 11.7 | 20.4 | 38.3 | 36.6 | 1.473 | 815
742 | 2022-12-22 12:23 | 12 | 20.5 | 38.2 | 36.2 | 1.475 | 498
743 | 2022-12-22 12:24 | 11.6 | 20.6 | 38 | 35.4 | 1.773 | 378
744 | 2022-12-22 12:25 | 11.5 | 20.8 | 37.8 | 35.5 | 1.778 | 483
745 | 2022-12-22 12:26 | 11.8 | 20.9 | 37.4 | 35.3 | 1.783 | 285
746 | 2022-12-22 12:27 | 11.7 | 21.2 | 37.3 | 35 | 1.779 | 313
747 | 2022-12-22 12:28 | 11.6 | 21.4 | 37.2 | 35 | 1.781 | 286
748 | 2022-12-22 12:29 | 11.5 | 21.5 | 37 | 34.8 | 1.777 | 313
749 | 2022-12-22 12:30 | 11.6 | 21.6 | 36.9 | 34.7 | 1.78 | 648
750 | 2022-12-22 12:31 | 11.8 | 21.7 | 36.8 | 34.6 | 1.77 | 494
751 | 2022-12-22 12:32 | 11.6 | 21.6 | 36.7 | 34.5 | 1.773 | 569
752 | 2022-12-22 12:33 | 11.3 | 21.6 | 36.9 | 34.4 | 1.777 | 373
753 | 2022-12-22 12:34 | 11.4 | 21.6 | 37.3 | 34.7 | 1.776 | 547
754 | 2022-12-22 12:35 | 11.7 | 21.7 | 37.6 | 35 | 1.781 | 897
755 | 2022-12-22 12:36 | 12.1 | 21.6 | 37.9 | 35.3 | 1.776 | 830
756 | 2022-12-22 12:37 | 12.2 | 21.6 | 38.2 | 35.5 | 1.771 | 771
757 | 2022-12-22 12:38 | 11.8 | 21.7 | 38.5 | 35.8 | 1.777 | 700
758 | 2022-12-22 12:39 | 12.1 | 21.8 | 38.8 | 36.1 | 1.781 | 387
759 | 2022-12-22 12:40 | 12.2 | 21.7 | 38.8 | 36.3 | 1.779 | 859
760 | 2022-12-22 12:41 | 12.2 | 21.8 | 38.7 | 36.3 | 1.779 | 413
761 | 2022-12-22 12:42 | 11.6 | 21.9 | 38.5 | 36.1 | 1.776 | 880
762 | 2022-12-22 12:43 | 12.1 | 21.9 | 38.3 | 36 | 1.776 | 822
763 | 2022-12-22 12:44 | 12.4 | 21.8 | 38.2 | 36.7 | 1.783 | 894
764 | 2022-12-22 12:45 | 12 | 21.4 | 38.1 | 36.6 | 1.784 | 891
765 | 2022-12-22 12:46 | 12.4 | 21.3 | 38.1 | 36.6 | 1.784 | 803
766 | 2022-12-22 12:47 | 12.6 | 21.1 | 38 | 36.5 | 1.75 | 860
767 | 2022-12-22 12:48 | 12.7 | 21 | 37.9 | 36.2 | 1.477 | 825
768 | 2022-12-22 12:49 | 13.2 | 20.8 | 37.8 | 36.2 | 1.475 | 833
769 | 2022-12-22 12:50 | 13.5 | 20.7 | 37.7 | 36.1 | 1.477 | 817
770 | 2022-12-22 12:51 | 13 | 20.7 | 37.6 | 36 | 1.476 | 573
771 | 2022-12-22 12:52 | 12.9 | 20.7 | 37.6 | 35.9 | 1.476 | 720
772 | 2022-12-22 12:53 | 13.1 | 20.6 | 37.4 | 35.9 | 1.473 | 872
773 | 2022-12-22 12:54 | 13 | 20.6 | 37.3 | 35.7 | 1.474 | 421
774 | 2022-12-22 12:55 | 12.9 | 20.5 | 37.3 | 35.6 | 1.475 | 853
775 | 2022-12-22 12:56 | 13.2 | 20.5 | 37.2 | 35.6 | 1.474 | 646
776 | 2022-12-22 12:57 | 12.9 | 20.6 | 37.1 | 35.5 | 1.472 | 828
777 | 2022-12-22 12:58 | 13.1 | 20.5 | 37.1 | 35.4 | 1.469 | 661
778 | 2022-12-22 12:59 | 13.5 | 20.4 | 37.4 | 35.5 | 1.473 | 830
779 | 2022-12-22 13:00 | 13.7 | 20.4 | 37.4 | 35.8 | 1.473 | 522
780 | 2022-12-22 13:01 | 13.8 | 20.5 | 37.3 | 35.7 | 1.476 | 746
781 | 2022-12-22 13:02 | 14 | 20.4 | 37.2 | 35.6 | 1.472 | 701
782 | 2022-12-22 13:03 | 14 | 20.5 | 37.1 | 35.5 | 1.471 | 791
783 | 2022-12-22 13:04 | 13.6 | 20.5 | 37.2 | 35.4 | 1.471 | 572
784 | 2022-12-22 13:05 | 13.3 | 20.5 | 37.6 | 35.6 | 1.468 | 816
785 | 2022-12-22 13:06 | 13.2 | 20.7 | 37.9 | 35.6 | 1.658 | 828
786 | 2022-12-22 13:07 | 13.7 | 20.7 | 38 | 35.4 | 1.779 | 839
787 | 2022-12-22 13:08 | 14.1 | 20.8 | 38 | 35.6 | 1.777 | 877
788 | 2022-12-22 13:09 | 14.1 | 21.1 | 37.8 | 35.5 | 1.779 | 844
789 | 2022-12-22 13:10 | 14.1 | 21.2 | 38.1 | 35.4 | 1.784 | 716
790 | 2022-12-22 13:11 | 13.7 | 21.6 | 38.5 | 35.8 | 1.783 | 839
791 | 2022-12-22 13:12 | 13.7 | 21.6 | 38.8 | 36.1 | 1.777 | 842
792 | 2022-12-22 13:13 | 13.7 | 21.8 | 39.2 | 36.3 | 1.775 | 841
793 | 2022-12-22 13:14 | 14.1 | 22 | 39.4 | 36.6 | 1.782 | 837
794 | 2022-12-22 13:15 | 13.8 | 22 | 39.7 | 36.9 | 1.781 | 830
795 | 2022-12-22 13:16 | 14.1 | 22.1 | 39.9 | 37.1 | 1.779 | 832
796 | 2022-12-22 13:17 | 14.2 | 22.1 | 39.9 | 38.1 | 1.787 | 827
797 | 2022-12-22 13:18 | 14.1 | 21.8 | 39.7 | 38.2 | 1.785 | 842
798 | 2022-12-22 13:19 | 14 | 21.5 | 39.6 | 38 | 1.785 | 829
799 | 2022-12-22 13:20 | 13.4 | 21.3 | 39.6 | 37.9 | 1.762 | 814
800 | 2022-12-22 13:21 | 12.7 | 21.1 | 39.5 | 38.3 | 1.578 | 810
801 | 2022-12-22 13:22 | 12.1 | 21 | 39.4 | 38.3 | 1.478 | 798
802 | 2022-12-22 13:23 | 12.4 | 20.8 | 39.3 | 38.2 | 1.477 | 791
803 | 2022-12-22 13:24 | 13.2 | 20.8 | 39.3 | 38.1 | 1.43 | 797
804 | 2022-12-22 13:25 | 13.4 | 20.8 | 39.3 | 37.8 | 1.082 | 790
805 | 2022-12-22 13:26 | 13.7 | 20.7 | 39.2 | 37.8 | 1.08 | 791
806 | 2022-12-22 13:27 | 14.2 | 20.7 | 39.1 | 37.7 | 1.081 | 799
807 | 2022-12-22 13:28 | 13.9 | 20.6 | 39.1 | 37.6 | 1.079 | 791
808 | 2022-12-22 13:29 | 13.6 | 20.6 | 39 | 37.6 | 1.079 | 793
809 | 2022-12-22 13:30 | 14.2 | 20.5 | 38.9 | 37.5 | 1.075 | 795
810 | 2022-12-22 13:31 | 14.4 | 20.5 | 38.8 | 37.4 | 1.08 | 779
811 | 2022-12-22 13:32 | 13.9 | 20.6 | 38.8 | 37.3 | 1.083 | 779
812 | 2022-12-22 13:33 | 13.9 | 20.6 | 38.7 | 36.8 | 1.478 | 780
813 | 2022-12-22 13:34 | 13.8 | 20.4 | 38.7 | 36.8 | 1.484 | 776
814 | 2022-12-22 13:35 | 13.8 | 20.4 | 39 | 37 | 1.474 | 771
815 | 2022-12-22 13:36 | 13.7 | 20.5 | 39.4 | 37.3 | 1.477 | 769
816 | 2022-12-22 13:37 | 13.4 | 20.5 | 39.8 | 37.7 | 1.479 | 767
817 | 2022-12-22 13:38 | 13.4 | 20.4 | 40 | 37.9 | 1.48 | 760
818 | 2022-12-22 13:39 | 13.8 | 20.4 | 40.4 | 38.1 | 1.484 | 768
819 | 2022-12-22 13:40 | 13.6 | 20.5 | 40.8 | 38.6 | 1.479 | 761
820 | 2022-12-22 13:41 | 13.8 | 20.4 | 41.2 | 38.9 | 1.485 | 762
821 | 2022-12-22 13:42 | 13.5 | 20.5 | 41.6 | 39.3 | 1.474 | 764
822 | 2022-12-22 13:43 | 13.8 | 20.6 | 41.9 | 38.9 | 1.65 | 757
823 | 2022-12-22 13:44 | 13.7 | 20.6 | 41.8 | 38.7 | 1.784 | 752
824 | 2022-12-22 13:45 | 13.8 | 20.8 | 41.5 | 38.8 | 1.786 | 748
825 | 2022-12-22 13:46 | 13.8 | 21 | 41.3 | 38.5 | 1.787 | 744
826 | 2022-12-22 13:47 | 13.8 | 21.3 | 41.2 | 38.5 | 1.794 | 738
827 | 2022-12-22 13:48 | 13.6 | 21.5 | 41 | 38.3 | 1.786 | 742
828 | 2022-12-22 13:49 | 13.4 | 21.6 | 40.7 | 38.2 | 1.792 | 745
829 | 2022-12-22 13:50 | 13.4 | 21.8 | 40.5 | 38 | 1.791 | 748
830 | 2022-12-22 13:51 | 13.5 | 21.9 | 40.4 | 37.8 | 1.787 | 747
831 | 2022-12-22 13:52 | 13.8 | 21.9 | 40.1 | 37.7 | 1.788 | 752
832 | 2022-12-22 13:53 | 14.2 | 22 | 39.9 | 38 | 1.782 | 743
833 | 2022-12-22 13:54 | 14.2 | 21.9 | 39.8 | 37.8 | 1.78 | 740
834 | 2022-12-22 13:55 | 13.9 | 21.9 | 39.7 | 38.6 | 1.781 | 741
835 | 2022-12-22 13:56 | 14.1 | 21.6 | 39.6 | 38.6 | 1.777 | 738
836 | 2022-12-22 13:57 | 12.8 | 21.3 | 39.6 | 38.5 | 1.586 | 734
837 | 2022-12-22 13:58 | 12.7 | 21.2 | 39.6 | 38.4 | 1.551 | 735
838 | 2022-12-22 13:59 | 13.3 | 21.1 | 39.5 | 38.1 | 1.23 | 734
839 | 2022-12-22 14:00 | 13.8 | 21 | 39.5 | 38 | 1.081 | 727
840 | 2022-12-22 14:01 | 13.6 | 20.9 | 39.4 | 37.9 | 1.083 | 723
841 | 2022-12-22 14:02 | 13.8 | 21 | 39.3 | 37.9 | 1.076 | 726
842 | 2022-12-22 14:03 | 14.1 | 20.8 | 39.2 | 37.8 | 1.08 | 726
843 | 2022-12-22 14:04 | 13.9 | 20.8 | 39.1 | 37.7 | 1.078 | 726
844 | 2022-12-22 14:05 | 13.8 | 20.7 | 39.3 | 36.5 | 1.47 | 722
845 | 2022-12-22 14:06 | 14.2 | 20.7 | 39.7 | 37.5 | 1.481 | 720
846 | 2022-12-22 14:07 | 14.1 | 20.7 | 40 | 37.9 | 1.484 | 717
847 | 2022-12-22 14:08 | 14 | 20.6 | 40.2 | 38.2 | 1.483 | 714
848 | 2022-12-22 14:09 | 13.9 | 20.6 | 39.9 | 38.2 | 1.485 | 708
849 | 2022-12-22 14:10 | 13.9 | 20.5 | 39.9 | 38 | 1.481 | 710
850 | 2022-12-22 14:11 | 14 | 20.5 | 39.8 | 38 | 1.481 | 709
851 | 2022-12-22 14:12 | 13.7 | 20.6 | 39.7 | 37.9 | 1.481 | 709
852 | 2022-12-22 14:13 | 14 | 20.5 | 39.6 | 37.8 | 1.483 | 706
853 | 2022-12-22 14:14 | 14.1 | 20.5 | 39.5 | 37.7 | 1.481 | 706
854 | 2022-12-22 14:15 | 14.1 | 20.5 | 39.4 | 37.6 | 1.483 | 703
855 | 2022-12-22 14:16 | 13.9 | 20.5 | 39.3 | 37.5 | 1.479 | 702
856 | 2022-12-22 14:17 | 14.1 | 20.5 | 39.2 | 37.4 | 1.481 | 698
857 | 2022-12-22 14:18 | 14.5 | 20.5 | 39 | 37.3 | 1.482 | 690
858 | 2022-12-22 14:19 | 14.5 | 20.5 | 39 | 37.2 | 1.48 | 686
859 | 2022-12-22 14:20 | 14.6 | 20.5 | 38.8 | 37.1 | 1.477 | 682
860 | 2022-12-22 14:21 | 14.4 | 20.4 | 38.7 | 37 | 1.479 | 678
861 | 2022-12-22 14:22 | 14.1 | 20.5 | 38.6 | 36.9 | 1.48 | 680
862 | 2022-12-22 14:23 | 13.7 | 20.5 | 38.5 | 36.8 | 1.477 | 679
863 | 2022-12-22 14:24 | 14.1 | 20.5 | 38.3 | 36.7 | 1.483 | 678
864 | 2022-12-22 14:25 | 14 | 20.5 | 38.3 | 36.5 | 1.482 | 679
865 | 2022-12-22 14:26 | 14 | 20.4 | 38.2 | 37 | 1.478 | 674
866 | 2022-12-22 14:27 | 14.3 | 20.5 | 38 | 37 | 1.478 | 671
867 | 2022-12-22 14:28 | 14.5 | 20.6 | 38 | 36.9 | 1.482 | 670
868 | 2022-12-22 14:29 | 14.7 | 20.6 | 37.9 | 36.2 | 1.667 | 666
869 | 2022-12-22 14:30 | 14.5 | 20.8 | 37.8 | 35.7 | 1.674 | 665
870 | 2022-12-22 14:31 | 14.4 | 20.9 | 37.7 | 35.7 | 1.589 | 662
871 | 2022-12-22 14:32 | 14.5 | 21 | 37.4 | 35.6 | 1.588 | 658
872 | 2022-12-22 14:33 | 14.2 | 21.2 | 37.3 | 35.4 | 1.583 | 650
873 | 2022-12-22 14:34 | 14 | 21.4 | 37.3 | 35.3 | 1.585 | 650
874 | 2022-12-22 14:35 | 14.3 | 21.6 | 37.6 | 35.4 | 1.583 | 648
875 | 2022-12-22 14:36 | 14.3 | 21.6 | 37.9 | 35.7 | 1.585 | 644
876 | 2022-12-22 14:37 | 14.6 | 21.6 | 38.2 | 35.9 | 1.583 | 641
877 | 2022-12-22 14:38 | 14.4 | 21.8 | 38.6 | 36.2 | 1.582 | 638
878 | 2022-12-22 14:39 | 14.2 | 21.8 | 38.9 | 36.4 | 1.752 | 635
879 | 2022-12-22 14:40 | 13.8 | 21.8 | 39.2 | 36.4 | 1.785 | 633
880 | 2022-12-22 14:41 | 13.8 | 21.8 | 39.5 | 37.4 | 1.786 | 633
881 | 2022-12-22 14:42 | 13.7 | 21.7 | 39.9 | 37.9 | 1.79 | 629
882 | 2022-12-22 14:43 | 13.8 | 21.3 | 40.4 | 38.3 | 1.783 | 623
883 | 2022-12-22 14:44 | 13.5 | 21.2 | 40.7 | 38.7 | 1.78 | 618
884 | 2022-12-22 14:45 | 13.8 | 21.1 | 41.2 | 38.8 | 1.583 | 618
885 | 2022-12-22 14:46 | 13.6 | 21.1 | 41.5 | 39.3 | 1.478 | 613
886 | 2022-12-22 14:47 | 13.6 | 20.9 | 42 | 39.5 | 1.484 | 609
887 | 2022-12-22 14:48 | 13.5 | 20.9 | 41.7 | 39.9 | 1.484 | 606
888 | 2022-12-22 14:49 | 13.6 | 20.9 | 41.6 | 39.6 | 1.483 | 607
889 | 2022-12-22 14:50 | 13.4 | 20.8 | 41.6 | 39.5 | 1.482 | 604
890 | 2022-12-22 14:51 | 13.5 | 20.7 | 41.5 | 39.5 | 1.476 | 600
891 | 2022-12-22 14:52 | 13.4 | 20.7 | 41.4 | 39.4 | 1.487 | 596
892 | 2022-12-22 14:53 | 13.6 | 20.7 | 41.3 | 39.3 | 1.484 | 596
893 | 2022-12-22 14:54 | 13.7 | 20.7 | 41.2 | 39.9 | 1.483 | 596
894 | 2022-12-22 14:55 | 14.1 | 20.7 | 41 | 39.8 | 1.481 | 600
895 | 2022-12-22 14:56 | 14.4 | 20.7 | 41 | 39.7 | 1.487 | 597
896 | 2022-12-22 14:57 | 14.3 | 20.6 | 40.9 | 39.7 | 1.459 | 595
897 | 2022-12-22 14:58 | 14 | 20.6 | 40.8 | 39.4 | 1.081 | 592
898 | 2022-12-22 14:59 | 14.3 | 20.7 | 40.9 | 39.2 | 1.085 | 591
899 | 2022-12-22 15:00 | 14 | 20.6 | 40.8 | 39.2 | 1.081 | 585
900 | 2022-12-22 15:01 | 14 | 20.6 | 40.7 | 39.2 | 1.077 | 581
901 | 2022-12-22 15:02 | 13.5 | 20.6 | 40.5 | 39.1 | 1.079 | 580
902 | 2022-12-22 15:03 | 13.4 | 20.6 | 40.4 | 38.9 | 1.079 | 578
903 | 2022-12-22 15:04 | 13.4 | 20.6 | 40.5 | 38.8 | 1.077 | 576
904 | 2022-12-22 15:05 | 13.4 | 20.7 | 40.6 | 38.9 | 1.083 | 573
905 | 2022-12-22 15:06 | 13.4 | 20.6 | 41.1 | 39.1 | 1.08 | 570
906 | 2022-12-22 15:07 | 13 | 20.6 | 41.6 | 39.5 | 1.081 | 566
907 | 2022-12-22 15:08 | 13.2 | 20.5 | 41.8 | 38.1 | 1.476 | 565
908 | 2022-12-22 15:09 | 13.1 | 20.6 | 42.1 | 39.7 | 1.486 | 563
909 | 2022-12-22 15:10 | 13.7 | 20.5 | 42.5 | 40.1 | 1.482 | 557
910 | 2022-12-22 15:11 | 13.4 | 20.6 | 42.8 | 40.4 | 1.481 | 553
911 | 2022-12-22 15:12 | 13.5 | 20.6 | 43.2 | 40.8 | 1.489 | 547
912 | 2022-12-22 15:13 | 13.6 | 20.6 | 43.7 | 41.1 | 1.487 | 543
913 | 2022-12-22 15:14 | 13.2 | 20.5 | 44.1 | 41.5 | 1.49 | 539
914 | 2022-12-22 15:15 | 13.7 | 20.5 | 43.5 | 41.6 | 1.489 | 536
915 | 2022-12-22 15:16 | 13.7 | 20.6 | 43.5 | 41.3 | 1.487 | 534
916 | 2022-12-22 15:17 | 13.6 | 20.5 | 43.5 | 41.3 | 1.487 | 531
917 | 2022-12-22 15:18 | 13.2 | 20.5 | 43.3 | 41.2 | 1.491 | 528
918 | 2022-12-22 15:19 | 13 | 20.5 | 43.2 | 41.7 | 1.485 | 524
919 | 2022-12-22 15:20 | 13.2 | 20.5 | 43.1 | 41.8 | 1.485 | 521
920 | 2022-12-22 15:21 | 13.3 | 20.4 | 43.1 | 41.7 | 1.491 | 518
921 | 2022-12-22 15:22 | 13.7 | 20.5 | 43 | 41.6 | 0 | 515
922 | 2022-12-22 15:23 | 13.6 | 20.5 | 42.8 | 41.3 | 0 | 512
923 | 2022-12-22 15:24 | 13.4 | 20.5 | 42.5 | 40.9 | 0 | 509
924 | 2022-12-22 15:25 | 13.5 | 20.5 | 42.8 | 40.7 | 1.088 | 507
925 | 2022-12-22 15:26 | 13.7 | 20.5 | 42.7 | 42.3 | 1.076 | 502
926 | 2022-12-22 15:27 | 13.7 | 20.4 | 42.7 | 42.3 | 1.006 | 495
927 | 2022-12-22 15:28 | 13.8 | 20.5 | 42.7 | 39.4 | 1.394 | 488
928 | 2022-12-22 15:29 | 13.6 | 20.4 | 42.7 | 40.3 | 1.004 | 482
929 | 2022-12-22 15:30 | 13 | 20.6 | 42.6 | 40.1 | 0.95 | 478
930 | 2022-12-22 15:31 | 12.9 | 20.9 | 42.2 | 39.9 | 0.95 | 476
931 | 2022-12-22 15:32 | 12.7 | 21.1 | 42 | 39.6 | 0.95 | 472
932 | 2022-12-22 15:33 | 12.6 | 21.3 | 41.9 | 39.5 | 0.949 | 468
933 | 2022-12-22 15:34 | 12.8 | 21.5 | 42 | 39.4 | 0.95 | 466
934 | 2022-12-22 15:35 | 13.3 | 21.5 | 41.7 | 37.4 | 1.556 | 462
935 | 2022-12-22 15:36 | 12.6 | 21.6 | 41.4 | 39.1 | 1.605 | 461
936 | 2022-12-22 15:37 | 12.9 | 21.5 | 41.2 | 38.9 | 1.606 | 453
937 | 2022-12-22 15:38 | 13.2 | 21.7 | 41.1 | 38.7 | 1.603 | 445
938 | 2022-12-22 15:39 | 13.2 | 21.8 | 41 | 38.7 | 1.605 | 437
939 | 2022-12-22 15:40 | 12.3 | 21.8 | 40.9 | 38.6 | 1.61 | 429
940 | 2022-12-22 15:41 | 12.4 | 21.8 | 40.7 | 38.5 | 1.601 | 423
941 | 2022-12-22 15:42 | 12.7 | 21.9 | 40.6 | 38.3 | 1.606 | 416
942 | 2022-12-22 15:43 | 12.9 | 21.9 | 40.4 | 38.2 | 1.599 | 411
943 | 2022-12-22 15:44 | 12.9 | 21.9 | 40.3 | 38.9 | 1.608 | 407
944 | 2022-12-22 15:45 | 13.1 | 21.6 | 40.2 | 39.1 | 1.604 | 402
945 | 2022-12-22 15:46 | 12.5 | 21.4 | 40.1 | 39 | 1.608 | 397
946 | 2022-12-22 15:47 | 12.5 | 21.2 | 40.1 | 38.9 | 1.6 | 392
947 | 2022-12-22 15:48 | 12.4 | 21 | 40.1 | 38.8 | 1.444 | 387
948 | 2022-12-22 15:49 | 12.4 | 21 | 40 | 38.5 | 1.079 | 383
949 | 2022-12-22 15:50 | 12 | 20.9 | 39.9 | 38.4 | 1.084 | 378
950 | 2022-12-22 15:51 | 11.1 | 20.9 | 39.9 | 38.4 | 1.084 | 374
951 | 2022-12-22 15:52 | 11 | 20.8 | 39.8 | 38.3 | 1.084 | 370
952 | 2022-12-22 15:53 | 11 | 20.7 | 39.7 | 38.2 | 1.08 | 366
953 | 2022-12-22 15:54 | 11 | 20.7 | 39.6 | 38.1 | 1.085 | 361
954 | 2022-12-22 15:55 | 11.1 | 20.7 | 39.5 | 38 | 1.087 | 356
955 | 2022-12-22 15:56 | 11.1 | 20.6 | 39.4 | 37.9 | 1.082 | 351
956 | 2022-12-22 15:57 | 10.9 | 20.6 | 39.3 | 37.9 | 1.085 | 346
957 | 2022-12-22 15:58 | 11.1 | 20.6 | 39.2 | 37.8 | 1.086 | 342
958 | 2022-12-22 15:59 | 10.9 | 20.5 | 39.1 | 37.7 | 1.083 | 337
959 | 2022-12-22 16:00 | 11 | 20.5 | 39 | 34.9 | 1.594 | 332
960 | 2022-12-22 16:01 | 10.8 | 20.5 | 38.9 | 37.1 | 1.612 | 326
961 | 2022-12-22 16:02 | 11 | 20.5 | 38.4 | 37 | 1.614 | 320
962 | 2022-12-22 16:03 | 10.7 | 20.4 | 38.4 | 36.6 | 1.608 | 314
963 | 2022-12-22 16:04 | 10.8 | 20.4 | 38.5 | 36.7 | 1.609 | 309
964 | 2022-12-22 16:05 | 10 | 20.6 | 38.9 | 36.8 | 1.614 | 303
965 | 2022-12-22 16:06 | 9.6 | 20.5 | 39.2 | 37.2 | 1.612 | 299
966 | 2022-12-22 16:07 | 9.7 | 20.6 | 39.5 | 37.4 | 1.613 | 296
967 | 2022-12-22 16:08 | 9.4 | 20.6 | 39.8 | 37.7 | 1.615 | 292
968 | 2022-12-22 16:09 | 9.5 | 20.5 | 40.1 | 37.6 | 1.609 | 287
969 | 2022-12-22 16:10 | 9.4 | 20.5 | 40.5 | 37.9 | 1.612 | 281
970 | 2022-12-22 16:11 | 9.2 | 20.6 | 40.7 | 38.2 | 1.614 | 276
971 | 2022-12-22 16:12 | 8.9 | 20.6 | 41 | 38.7 | 1.612 | 270
972 | 2022-12-22 16:13 | 8.5 | 20.7 | 41.3 | 39.9 | 1.621 | 265
973 | 2022-12-22 16:14 | 8.6 | 20.7 | 41.8 | 40.2 | 1.62 | 260
974 | 2022-12-22 16:15 | 8.6 | 20.6 | 42.4 | 40.6 | 1.613 | 255
975 | 2022-12-22 16:16 | 8.4 | 20.5 | 42.8 | 40.9 | 1.425 | 251
976 | 2022-12-22 16:17 | 8.2 | 20.5 | 43 | 41 | 1.085 | 247
977 | 2022-12-22 16:18 | 8.3 | 20.5 | 42.9 | 41.2 | 1.086 | 240
978 | 2022-12-22 16:19 | 8.1 | 20.5 | 42.6 | 41.1 | 1.087 | 234
979 | 2022-12-22 16:20 | 8.2 | 20.4 | 42.6 | 38.5 | 1.578 | 229
980 | 2022-12-22 16:21 | 8.2 | 20.4 | 42.5 | 40.8 | 1.606 | 199
981 | 2022-12-22 16:22 | 8.1 | 20.7 | 42.2 | 40.8 | 1.613 | 190
982 | 2022-12-22 16:23 | 8 | 21 | 42.2 | 40.5 | 1.604 | 207
983 | 2022-12-22 16:24 | 8.1 | 21.2 | 42.2 | 40.6 | 1.583 | 196
984 | 2022-12-22 16:25 | 8.2 | 21.4 | 42.1 | 40.4 | 1.494 | 194
985 | 2022-12-22 16:26 | 8.1 | 21.6 | 42.1 | 40.1 | 1.22 | 193
986 | 2022-12-22 16:27 | 8 | 21.6 | 42 | 39.6 | 0.95 | 188
987 | 2022-12-22 16:28 | 8 | 21.6 | 41.9 | 39.5 | 0.948 | 183
988 | 2022-12-22 16:29 | 7.6 | 21.7 | 41.7 | 39.4 | 0.947 | 176
989 | 2022-12-22 16:30 | 7.5 | 21.8 | 41.6 | 39.3 | 0.949 | 170
990 | 2022-12-22 16:31 | 7.6 | 21.7 | 41.5 | 39.1 | 0.946 | 165
991 | 2022-12-22 16:32 | 7.5 | 21.7 | 41.3 | 39 | 0.946 | 157
992 | 2022-12-22 16:33 | 7.7 | 21.8 | 41.2 | 38.9 | 1.302 | 152
993 | 2022-12-22 16:34 | 7.4 | 21.8 | 40.9 | 35.3 | 1.788 | 147
994 | 2022-12-22 16:35 | 7.3 | 21.8 | 40.7 | 38 | 1.803 | 142
995 | 2022-12-22 16:36 | 7.3 | 21.9 | 40.3 | 37.9 | 1.794 | 135
996 | 2022-12-22 16:37 | 7.3 | 21.8 | 40.3 | 38.5 | 1.808 | 109
997 | 2022-12-22 16:38 | 7.3 | 21.4 | 40.2 | 38.6 | 1.808 | 66
998 | 2022-12-22 16:39 | 7.3 | 21.2 | 40.1 | 38.5 | 1.801 | 41
999 | 2022-12-22 16:40 | 7.1 | 21 | 40.1 | 38.4 | 1.785 | 31
1000 | 2022-12-22 16:41 | 7.1 | 20.9 | 39.9 | 38.1 | 1.552 | 20
1001 | 2022-12-22 16:42 | 7.1 | 20.7 | 39.8 | 38 | 1.49 | 18
1002 | 2022-12-22 16:43 | 7 | 20.6 | 39.7 | 37.9 | 1.492 | 17
1003 | 2022-12-22 16:44 | 7 | 20.6 | 39.5 | 37.7 | 1.491 | 16
1004 | 2022-12-22 16:45 | 7 | 20.5 | 39.4 | 37.6 | 1.491 | 15
1005 | 2022-12-22 16:46 | 6.9 | 20.4 | 39.3 | 37.5 | 1.485 | 14
1006 | 2022-12-22 16:47 | 7 | 20.4 | 39.2 | 37.3 | 1.575 | 13
1007 | 2022-12-22 16:48 | 6.9 | 20.4 | 39 | 36.5 | 1.801 | 12
1008 | 2022-12-22 16:49 | 6.8 | 20.4 | 38.8 | 36.4 | 1.805 | 11
1009 | 2022-12-22 16:50 | 6.9 | 20.4 | 38.5 | 36.2 | 1.806 | 11
1010 | 2022-12-22 16:51 | 6.6 | 20.4 | 38.3 | 36 | 1.806 | 10
1011 | 2022-12-22 16:52 | 6.6 | 20.4 | 38.2 | 35.9 | 1.799 | 9
1012 | 2022-12-22 16:53 | 6.7 | 20.5 | 38 | 35.8 | 1.794 | 9
1013 | 2022-12-22 16:54 | 6.5 | 20.5 | 37.9 | 35.6 | 1.803 | 9
1014 | 2022-12-22 16:55 | 6.5 | 20.7 | 37.7 | 35.5 | 1.805 | 8
1015 | 2022-12-22 16:56 | 6.4 | 20.8 | 37.5 | 33.8 | 1.95 | 7
1016 | 2022-12-22 16:57 | 6.6 | 20.9 | 37.4 | 34.6 | 1.962 | 6
1017 | 2022-12-22 16:58 | 6.4 | 21.1 | 37 | 34.9 | 1.953 | 5
1018 | 2022-12-22 16:59 | 6.5 | 21.3 | 36.8 | 34.9 | 1.958 | 5
1019 | 2022-12-22 17:00 | 6.4 | 21.5 | 36.7 | 34.7 | 1.954 | 4
1020 | 2022-12-22 17:01 | 6.4 | 21.6 | 36.6 | 34.7 | 1.949 | 3
1021 | 2022-12-22 17:02 | 6.3 | 21.6 | 36.8 | 34.3 | 1.812 | 3
1022 | 2022-12-22 17:03 | 6.3 | 21.6 | 37 | 34.6 | 1.793 | 2
1023 | 2022-12-22 17:04 | 6.4 | 21.7 | 37.3 | 34.8 | 1.794 | 1
1024 | 2022-12-22 17:05 | 6.2 | 21.7 | 37.7 | 35.1 | 1.79 | 1
1025 | 2022-12-22 17:06 | 6.2 | 21.7 | 38 | 35.4 | 1.799 | 0
1026 | 2022-12-22 17:07 | 5.9 | 21.8 | 38.3 | 35.6 | 1.797 | 0
1027 | 2022-12-22 17:08 | 6 | 21.6 | 38.6 | 36.8 | 1.795 | 0
1028 | 2022-12-22 17:09 | 6 | 21.3 | 39 | 37.2 | 1.794 | 0
1029 | 2022-12-22 17:10 | 5.9 | 21.1 | 39.1 | 37.4 | 1.793 | 0
1030 | 2022-12-22 17:11 | 5.9 | 20.9 | 39.1 | 37.4 | 1.742 | 0
1031 | 2022-12-22 17:12 | 5.8 | 20.8 | 39 | 37.2 | 1.48 | 0
1032 | 2022-12-22 17:13 | 5.7 | 20.6 | 39 | 37.2 | 1.49 | 0
1033 | 2022-12-22 17:14 | 5.7 | 20.5 | 38.9 | 37.1 | 1.485 | 0
1034 | 2022-12-22 17:15 | 5.8 | 20.5 | 38.7 | 37 | 1.488 | 0
1035 | 2022-12-22 17:16 | 5.8 | 20.5 | 38.6 | 36.9 | 1.488 | 0
1036 | 2022-12-22 17:17 | 5.7 | 20.5 | 38.5 | 36.8 | 1.482 | 0
1037 | 2022-12-22 17:18 | 5.6 | 20.4 | 38.4 | 36.7 | 1.482 | 0
1038 | 2022-12-22 17:19 | 5.7 | 20.3 | 38.3 | 36.6 | 1.491 | 0
1039 | 2022-12-22 17:20 | 5.5 | 20.3 | 38.2 | 36.5 | 1.482 | 0
1040 | 2022-12-22 17:21 | 5.6 | 20.3 | 38.1 | 33.8 | 1.779 | 0
1041 | 2022-12-22 17:22 | 5.7 | 20.5 | 37.9 | 34.4 | 1.933 | 0
1042 | 2022-12-22 17:23 | 5.6 | 20.5 | 37.5 | 35.3 | 1.959 | 0
1043 | 2022-12-22 17:24 | 5.5 | 20.7 | 37.3 | 35 | 1.956 | 0
1044 | 2022-12-22 17:25 | 5.7 | 20.9 | 37.2 | 34.9 | 1.953 | 0
1045 | 2022-12-22 17:26 | 5.5 | 21.1 | 37 | 34.6 | 1.906 | 0
1046 | 2022-12-22 17:27 | 5.4 | 21.4 | 36.8 | 34.5 | 1.858 | 0
1047 | 2022-12-22 17:28 | 5.3 | 21.5 | 36.7 | 34.3 | 1.844 | 0
1048 | 2022-12-22 17:29 | 5.3 | 21.6 | 36.5 | 34.2 | 1.845 | 0
1049 | 2022-12-22 17:30 | 5.4 | 21.7 | 36.4 | 34 | 1.851 | 0
1050 | 2022-12-22 17:31 | 5.2 | 21.7 | 36.7 | 34.1 | 1.846 | 0
1051 | 2022-12-22 17:32 | 5.4 | 21.8 | 37.1 | 35.1 | 1.849 | 0
1052 | 2022-12-22 17:33 | 5.1 | 21.8 | 37.4 | 35.4 | 1.847 | 0
1053 | 2022-12-22 17:34 | 5.3 | 21.6 | 37.8 | 36.4 | 1.851 | 0
1054 | 2022-12-22 17:35 | 5.1 | 21.3 | 38.2 | 36.7 | 1.849 | 0
1055 | 2022-12-22 17:36 | 5.1 | 21 | 38.6 | 36.6 | 1.791 | 0
1056 | 2022-12-22 17:37 | 5.2 | 20.9 | 39 | 37 | 1.754 | 0
1057 | 2022-12-22 17:38 | 5.1 | 20.8 | 39.2 | 37.1 | 1.486 | 0
1058 | 2022-12-22 17:39 | 5 | 20.7 | 39.6 | 37.5 | 1.482 | 0
1059 | 2022-12-22 17:40 | 5 | 20.6 | 39.7 | 37.7 | 1.487 | 0
1060 | 2022-12-22 17:41 | 5 | 20.5 | 39.7 | 37.8 | 1.486 | 0
1061 | 2022-12-22 17:42 | 5 | 20.5 | 39.6 | 37.8 | 1.49 | 0
1062 | 2022-12-22 17:43 | 5 | 20.4 | 39.5 | 37.7 | 1.485 | 0
1063 | 2022-12-22 17:44 | 5 | 20.4 | 39.5 | 37.6 | 1.488 | 0
1064 | 2022-12-22 17:45 | 4.9 | 20.4 | 39.3 | 37.5 | 1.481 | 0
1065 | 2022-12-22 17:46 | 4.9 | 20.4 | 39.2 | 37.4 | 1.49 | 0
1066 | 2022-12-22 17:47 | 5.1 | 20.4 | 39.1 | 37.3 | 1.486 | 0
1067 | 2022-12-22 17:48 | 4.8 | 20.4 | 39 | 37.1 | 1.646 | 0
1068 | 2022-12-22 17:49 | 5 | 20.5 | 38.7 | 36.2 | 1.791 | 0
1069 | 2022-12-22 17:50 | 4.9 | 20.6 | 38.5 | 36 | 1.869 | 0
1070 | 2022-12-22 17:51 | 4.9 | 20.8 | 38.2 | 35.3 | 1.959 | 0
1071 | 2022-12-22 17:52 | 5 | 21.1 | 38 | 35.1 | 1.95 | 0
1072 | 2022-12-22 17:53 | 4.9 | 21.3 | 37.7 | 34.9 | 1.952 | 0
1073 | 2022-12-22 17:54 | 5 | 21.4 | 37.5 | 34.7 | 1.96 | 0
1074 | 2022-12-22 17:55 | 4.7 | 21.5 | 37.3 | 34.6 | 1.958 | 0
1075 | 2022-12-22 17:56 | 5 | 21.6 | 37.1 | 34.4 | 1.954 | 0
1076 | 2022-12-22 17:57 | 5 | 21.7 | 36.9 | 34.3 | 1.956 | 0
1077 | 2022-12-22 17:58 | 4.8 | 21.8 | 36.7 | 34.1 | 1.957 | 0
1078 | 2022-12-22 17:59 | 5 | 21.9 | 36.5 | 33.9 | 1.951 | 0
1079 | 2022-12-22 18:00 | 4.9 | 21.8 | 36.5 | 34.3 | 1.949 | 0
1080 | 2022-12-22 18:01 | 4.9 | 21.6 | 36.8 | 35.1 | 1.956 | 0
1081 | 2022-12-22 18:02 | 4.9 | 21.3 | 36.9 | 35.5 | 1.958 | 0
1082 | 2022-12-22 18:03 | 4.7 | 21.2 | 36.9 | 35.5 | 1.953 | 0
1083 | 2022-12-22 18:04 | 4.7 | 21 | 36.9 | 35.3 | 1.745 | 0
1084 | 2022-12-22 18:05 | 4.7 | 20.9 | 37.2 | 35.3 | 1.482 | 0
1085 | 2022-12-22 18:06 | 4.8 | 20.7 | 37.6 | 35.6 | 1.487 | 0
1086 | 2022-12-22 18:07 | 4.7 | 20.7 | 38.1 | 36 | 1.483 | 0
1087 | 2022-12-22 18:08 | 4.6 | 20.5 | 38.4 | 36.3 | 1.485 | 0
1088 | 2022-12-22 18:09 | 4.6 | 20.5 | 38.6 | 36.7 | 1.484 | 0
1089 | 2022-12-22 18:10 | 4.6 | 20.5 | 39 | 36.9 | 1.487 | 0
1090 | 2022-12-22 18:11 | 4.6 | 20.4 | 39.4 | 37.2 | 1.485 | 0
1091 | 2022-12-22 18:12 | 4.6 | 20.4 | 39.8 | 37.6 | 1.485 | 0
1092 | 2022-12-22 18:13 | 4.7 | 20.4 | 39.8 | 38.5 | 1.495 | 0
1093 | 2022-12-22 18:14 | 4.6 | 20.4 | 39.7 | 38.6 | 1.487 | 0
1094 | 2022-12-22 18:15 | 4.7 | 20.4 | 39.7 | 38.4 | 1.491 | 0
1095 | 2022-12-22 18:16 | 4.5 | 20.4 | 39.7 | 38.1 | 1.574 | 0
1096 | 2022-12-22 18:17 | 4.5 | 20.5 | 39.6 | 37.1 | 1.619 | 0
1097 | 2022-12-22 18:18 | 4.5 | 20.6 | 39.5 | 35.3 | 1.84 | 0
1098 | 2022-12-22 18:19 | 4.6 | 20.8 | 39 | 36.4 | 1.847 | 0
1099 | 2022-12-22 18:20 | 4.5 | 21.2 | 38.6 | 36.1 | 1.852 | 0
1100 | 2022-12-22 18:21 | 4.4 | 21.3 | 38.5 | 35.8 | 1.851 | 0
1101 | 2022-12-22 18:22 | 4.5 | 21.5 | 38.3 | 35.7 | 1.85 | 0
1102 | 2022-12-22 18:23 | 4.4 | 21.7 | 38.1 | 35.6 | 1.848 | 0
1103 | 2022-12-22 18:24 | 4.5 | 21.7 | 37.9 | 35.4 | 1.851 | 0
1104 | 2022-12-22 18:25 | 4.4 | 21.9 | 37.8 | 35.2 | 1.856 | 0
1105 | 2022-12-22 18:26 | 4.4 | 21.8 | 37.6 | 35.1 | 1.848 | 0
1106 | 2022-12-22 18:27 | 4.3 | 21.9 | 37.4 | 35.6 | 1.854 | 0
1107 | 2022-12-22 18:28 | 4.4 | 21.8 | 37.2 | 35.4 | 1.954 | 0
1108 | 2022-12-22 18:29 | 4.6 | 21.4 | 37.1 | 35.8 | 1.961 | 0
1109 | 2022-12-22 18:30 | 4.5 | 21.2 | 37 | 35.7 | 1.948 | 0
1110 | 2022-12-22 18:31 | 4.4 | 21 | 37 | 35.5 | 1.773 | 0
1111 | 2022-12-22 18:32 | 4.3 | 20.9 | 36.9 | 35.2 | 1.483 | 0
1112 | 2022-12-22 18:33 | 4.3 | 20.8 | 36.9 | 35.2 | 1.482 | 0
1113 | 2022-12-22 18:34 | 4.3 | 20.7 | 37.1 | 35.3 | 1.488 | 0
1114 | 2022-12-22 18:35 | 4.4 | 20.6 | 37.5 | 35.5 | 1.477 | 0
1115 | 2022-12-22 18:36 | 4.2 | 20.5 | 37.8 | 35.8 | 1.482 | 0
1116 | 2022-12-22 18:37 | 4.5 | 20.6 | 38.1 | 36.1 | 1.483 | 0
1117 | 2022-12-22 18:38 | 4.3 | 20.5 | 38.5 | 36.4 | 1.482 | 0
1118 | 2022-12-22 18:39 | 4.4 | 20.4 | 38.9 | 36.7 | 1.484 | 0
1119 | 2022-12-22 18:40 | 4.2 | 20.4 | 39.2 | 37.1 | 1.483 | 0
1120 | 2022-12-22 18:41 | 4.5 | 20.3 | 39.6 | 37.4 | 1.482 | 0
1121 | 2022-12-22 18:42 | 4.3 | 20.4 | 40 | 37.7 | 1.491 | 0
1122 | 2022-12-22 18:43 | 4.5 | 20.4 | 40.4 | 38.1 | 1.488 | 0
1123 | 2022-12-22 18:44 | 4.4 | 20.5 | 40.8 | 37 | 1.788 | 0
1124 | 2022-12-22 18:45 | 4.5 | 20.6 | 41 | 37.9 | 1.862 | 0
1125 | 2022-12-22 18:46 | 4.4 | 20.8 | 41.1 | 37.1 | 1.955 | 0
1126 | 2022-12-22 18:47 | 4.4 | 21 | 41.3 | 37.6 | 1.963 | 0
1127 | 2022-12-22 18:48 | 4.3 | 21.4 | 41.5 | 37.7 | 1.96 | 0
1128 | 2022-12-22 18:49 | 4.5 | 21.6 | 41.7 | 38 | 1.965 | 0
1129 | 2022-12-22 18:50 | 4.3 | 21.8 | 41.5 | 38 | 1.965 | 0
1130 | 2022-12-22 18:51 | 4.3 | 21.8 | 41.3 | 38 | 1.967 | 0
1131 | 2022-12-22 18:52 | 4.3 | 22 | 41.1 | 37.8 | 1.956 | 0
1132 | 2022-12-22 18:53 | 4.3 | 22.1 | 40.8 | 39.5 | 1.964 | 0
1133 | 2022-12-22 18:54 | 4.4 | 22.1 | 40.7 | 39.4 | 0 | 0
1134 | 2022-12-22 18:55 | 4.4 | 21.6 | 40.4 | 38.8 | 0 | 0
1135 | 2022-12-22 18:56 | 4.4 | 21.4 | 40.1 | 38.1 | 0 | 0
1136 | 2022-12-22 18:57 | 4.3 | 21.1 | 39.8 | 37.5 | 0 | 0
1137 | 2022-12-22 18:58 | 4.3 | 20.9 | 39.6 | 36.9 | 0 | 0
1138 | 2022-12-22 18:59 | 4.4 | 20.8 | 39.3 | 36.4 | 0 | 0
1139 | 2022-12-22 19:00 | 4.2 | 20.6 | 39 | 35.9 | 0 | 0
1140 | 2022-12-22 19:01 | 4.4 | 20.5 | 38.7 | 35.3 | 0 | 0
1141 | 2022-12-22 19:02 | 4.3 | 20.3 | 38.4 | 34.9 | 0 | 0
1142 | 2022-12-22 19:03 | 4.2 | 20.4 | 38.1 | 34.4 | 0 | 0
1143 | 2022-12-22 19:04 | 4.2 | 20.2 | 37.8 | 36.9 | 0.015 | 0
1144 | 2022-12-22 19:05 | 4.4 | 20.2 | 40.2 | 35.6 | 0.982 | 0
1145 | 2022-12-22 19:06 | 4.2 | 20.1 | 40 | 38.4 | 1.087 | 0
1146 | 2022-12-22 19:07 | 4.3 | 20.3 | 39.9 | 37.7 | 1.342 | 0
1147 | 2022-12-22 19:08 | 4.3 | 20.4 | 39.8 | 36.7 | 1.806 | 0
1148 | 2022-12-22 19:09 | 4.2 | 20.4 | 39.8 | 37.1 | 1.808 | 0
1149 | 2022-12-22 19:10 | 4.1 | 20.6 | 39.6 | 35.2 | 1.967 | 0
1150 | 2022-12-22 19:11 | 4.1 | 21 | 39.5 | 36.2 | 1.976 | 0
1151 | 2022-12-22 19:12 | 4.2 | 21.2 | 39.1 | 36.2 | 1.974 | 0
1152 | 2022-12-22 19:13 | 4.3 | 21.4 | 38.8 | 35.9 | 1.976 | 0
1153 | 2022-12-22 19:14 | 4.2 | 21.6 | 38.6 | 35.7 | 1.973 | 0
1154 | 2022-12-22 19:15 | 4.1 | 21.7 | 38.4 | 35.5 | 1.969 | 0
1155 | 2022-12-22 19:16 | 4 | 21.8 | 38.2 | 35.3 | 1.966 | 0
1156 | 2022-12-22 19:17 | 4.3 | 21.8 | 38 | 35.1 | 1.968 | 0
1157 | 2022-12-22 19:18 | 4.3 | 21.8 | 37.7 | 35 | 1.966 | 0
1158 | 2022-12-22 19:19 | 4.2 | 21.9 | 37.5 | 35.1 | 1.969 | 0
1159 | 2022-12-22 19:20 | 4.2 | 21.8 | 37.3 | 36 | 1.974 | 0
1160 | 2022-12-22 19:21 | 4.3 | 21.5 | 37.2 | 35.9 | 1.968 | 0
1161 | 2022-12-22 19:22 | 4.4 | 21.3 | 37.2 | 35.8 | 1.961 | 0
1162 | 2022-12-22 19:23 | 4.1 | 21 | 37.1 | 35.7 | 1.861 | 0
1163 | 2022-12-22 19:24 | 4.1 | 21 | 37 | 35.4 | 1.542 | 0
1164 | 2022-12-22 19:25 | 4.1 | 20.9 | 36.9 | 35.3 | 1.49 | 0
1165 | 2022-12-22 19:26 | 4 | 20.6 | 36.9 | 35.2 | 1.488 | 0
1166 | 2022-12-22 19:27 | 4.1 | 20.7 | 37.1 | 35.3 | 1.49 | 0
1167 | 2022-12-22 19:28 | 4.2 | 20.6 | 37.3 | 35.4 | 1.487 | 0
1168 | 2022-12-22 19:29 | 4.2 | 20.5 | 37.2 | 35.6 | 1.492 | 0
1169 | 2022-12-22 19:30 | 4.2 | 20.5 | 37.1 | 35.5 | 1.485 | 0
1170 | 2022-12-22 19:31 | 4.3 | 20.4 | 37 | 35.4 | 1.482 | 0
1171 | 2022-12-22 19:32 | 4.2 | 20.3 | 36.9 | 35.3 | 1.488 | 0
1172 | 2022-12-22 19:33 | 4 | 20.2 | 36.8 | 35.2 | 1.486 | 0
1173 | 2022-12-22 19:34 | 4 | 20.3 | 36.9 | 35.1 | 1.487 | 0
1174 | 2022-12-22 19:35 | 4.1 | 20.3 | 37.4 | 35.4 | 1.489 | 0
1175 | 2022-12-22 19:36 | 4.3 | 20.5 | 37.9 | 33.4 | 1.774 | 0
1176 | 2022-12-22 19:37 | 4 | 20.5 | 38.2 | 35 | 1.926 | 0
1177 | 2022-12-22 19:38 | 4.2 | 20.6 | 38.2 | 35 | 1.969 | 0
1178 | 2022-12-22 19:39 | 4 | 20.8 | 38.5 | 35.1 | 1.964 | 0
1179 | 2022-12-22 19:40 | 4.1 | 21 | 38.8 | 35.4 | 1.974 | 0
1180 | 2022-12-22 19:41 | 4.1 | 21.2 | 38.8 | 35.7 | 1.968 | 0
1181 | 2022-12-22 19:42 | 4.2 | 21.4 | 38.7 | 35.7 | 1.973 | 0
1182 | 2022-12-22 19:43 | 4 | 21.6 | 38.5 | 35.6 | 1.969 | 0
1183 | 2022-12-22 19:44 | 4.2 | 21.7 | 38.2 | 35.4 | 1.967 | 0
1184 | 2022-12-22 19:45 | 4.2 | 21.7 | 38 | 35.2 | 1.967 | 0
1185 | 2022-12-22 19:46 | 4.2 | 21.9 | 37.8 | 35 | 1.967 | 0
1186 | 2022-12-22 19:47 | 4.2 | 21.9 | 37.6 | 35 | 1.963 | 0
1187 | 2022-12-22 19:48 | 4.3 | 21.8 | 37.4 | 36.1 | 1.968 | 0
1188 | 2022-12-22 19:49 | 4.3 | 21.5 | 37.3 | 36.4 | 1.963 | 0
1189 | 2022-12-22 19:50 | 4.2 | 21.3 | 37.3 | 36.3 | 1.963 | 0
1190 | 2022-12-22 19:51 | 4.2 | 21 | 37.3 | 36.3 | 1.895 | 0
1191 | 2022-12-22 19:52 | 4.1 | 20.9 | 37.3 | 36.2 | 1.489 | 0
1192 | 2022-12-22 19:53 | 4 | 20.8 | 37.2 | 35.8 | 1.085 | 0
1193 | 2022-12-22 19:54 | 4 | 20.7 | 37.1 | 35.8 | 1.077 | 0
1194 | 2022-12-22 19:55 | 4 | 20.5 | 37.2 | 35.7 | 1.082 | 0
1195 | 2022-12-22 19:56 | 4.2 | 20.5 | 37.4 | 35.8 | 1.079 | 0
1196 | 2022-12-22 19:57 | 4.1 | 20.4 | 37.7 | 36 | 1.085 | 0
1197 | 2022-12-22 19:58 | 4.2 | 20.4 | 37.4 | 36.2 | 1.085 | 0
1198 | 2022-12-22 19:59 | 4.2 | 20.3 | 37.3 | 35.9 | 1.083 | 0
1199 | 2022-12-22 20:00 | 4.2 | 20.3 | 37.2 | 34.9 | 1.449 | 0
1200 | 2022-12-22 20:01 | 4.1 | 20.3 | 37.1 | 35.4 | 1.49 | 0
1201 | 2022-12-22 20:02 | 4.2 | 20.2 | 37.1 | 35.4 | 1.488 | 0
1202 | 2022-12-22 20:03 | 4 | 20.3 | 36.9 | 35.3 | 1.507 | 0
1203 | 2022-12-22 20:04 | 4.1 | 20.4 | 37 | 34.2 | 1.8 | 0
1204 | 2022-12-22 20:05 | 3.9 | 20.5 | 37.3 | 33.8 | 1.966 | 0
1205 | 2022-12-22 20:06 | 4.2 | 20.7 | 37.4 | 34.4 | 1.967 | 0
1206 | 2022-12-22 20:07 | 4 | 20.9 | 37.7 | 34.5 | 1.968 | 0
1207 | 2022-12-22 20:08 | 4.1 | 21.2 | 38 | 34.7 | 1.97 | 0
1208 | 2022-12-22 20:09 | 3.9 | 21.2 | 38.2 | 35 | 1.97 | 0
1209 | 2022-12-22 20:10 | 4 | 21.4 | 38.6 | 35.1 | 1.965 | 0
1210 | 2022-12-22 20:11 | 4.1 | 21.6 | 38.7 | 35.5 | 1.971 | 0
1211 | 2022-12-22 20:12 | 4.1 | 21.6 | 38.9 | 35.6 | 1.966 | 0
1212 | 2022-12-22 20:13 | 4.1 | 21.7 | 38.7 | 35.7 | 1.967 | 0
1213 | 2022-12-22 20:14 | 4.2 | 21.7 | 38.4 | 35.5 | 1.963 | 0
1214 | 2022-12-22 20:15 | 4.1 | 21.8 | 38.3 | 36 | 1.966 | 0
1215 | 2022-12-22 20:16 | 4 | 21.9 | 38.1 | 36 | 1.968 | 0
1216 | 2022-12-22 20:17 | 4.2 | 21.8 | 38.1 | 36.4 | 1.967 | 0
1217 | 2022-12-22 20:18 | 4.1 | 21.6 | 37.9 | 36.5 | 1.963 | 0
1218 | 2022-12-22 20:19 | 4.2 | 21.3 | 37.9 | 36.2 | 1.797 | 0
1219 | 2022-12-22 20:20 | 4.1 | 21.1 | 37.8 | 36.3 | 1.795 | 0
1220 | 2022-12-22 20:21 | 4.1 | 20.9 | 37.6 | 36.1 | 1.677 | 0
1221 | 2022-12-22 20:22 | 3.9 | 20.8 | 37.5 | 35.9 | 1.49 | 0
1222 | 2022-12-22 20:23 | 4 | 20.7 | 37.5 | 35.8 | 1.491 | 0
1223 | 2022-12-22 20:24 | 4.1 | 20.7 | 37.4 | 35.7 | 1.493 | 0
1224 | 2022-12-22 20:25 | 4 | 20.6 | 37.3 | 35.6 | 1.49 | 0
1225 | 2022-12-22 20:26 | 4.2 | 20.5 | 37.2 | 35.5 | 1.488 | 0
1226 | 2022-12-22 20:27 | 4 | 20.4 | 37.1 | 35.4 | 1.488 | 0
1227 | 2022-12-22 20:28 | 3.9 | 20.3 | 36.9 | 35.4 | 1.49 | 0
1228 | 2022-12-22 20:29 | 3.9 | 20.3 | 36.9 | 35.2 | 1.488 | 0
1229 | 2022-12-22 20:30 | 4.1 | 20.3 | 37.1 | 35.3 | 1.487 | 0
1230 | 2022-12-22 20:31 | 4 | 20.3 | 37.4 | 35.5 | 1.49 | 0
1231 | 2022-12-22 20:32 | 4.2 | 20.4 | 37.4 | 35.7 | 1.523 | 0
1232 | 2022-12-22 20:33 | 4.2 | 20.6 | 37.2 | 34.7 | 1.8 | 0
1233 | 2022-12-22 20:34 | 4.1 | 20.6 | 37.2 | 34.8 | 1.832 | 0
1234 | 2022-12-22 20:35 | 4 | 20.8 | 37.4 | 34.1 | 1.964 | 0
1235 | 2022-12-22 20:36 | 4.3 | 21 | 37.7 | 34.4 | 1.967 | 0
1236 | 2022-12-22 20:37 | 4.4 | 21.3 | 37.9 | 34.7 | 1.964 | 0
1237 | 2022-12-22 20:38 | 4.5 | 21.3 | 38.1 | 34.9 | 1.965 | 0
1238 | 2022-12-22 20:39 | 4.3 | 21.4 | 38.4 | 35.1 | 1.967 | 0
1239 | 2022-12-22 20:40 | 4.5 | 21.4 | 38.6 | 35.3 | 1.965 | 0
1240 | 2022-12-22 20:41 | 4.7 | 21.6 | 38.9 | 35.5 | 1.966 | 0
1241 | 2022-12-22 20:42 | 4.7 | 21.7 | 39.1 | 35.7 | 1.968 | 0
1242 | 2022-12-22 20:43 | 4.7 | 21.8 | 39.4 | 35.9 | 1.966 | 0
1243 | 2022-12-22 20:44 | 4.8 | 21.8 | 39.6 | 36.7 | 1.969 | 0
1244 | 2022-12-22 20:45 | 4.8 | 21.9 | 39.7 | 37.1 | 1.97 | 0
1245 | 2022-12-22 20:46 | 4.9 | 21.9 | 39.7 | 37.3 | 1.967 | 0
1246 | 2022-12-22 20:47 | 4.9 | 21.7 | 39.5 | 38 | 1.964 | 0
1247 | 2022-12-22 20:48 | 5.1 | 21.4 | 39.4 | 37.7 | 1.82 | 0
1248 | 2022-12-22 20:49 | 5.1 | 21.2 | 39.4 | 37.8 | 1.801 | 0
1249 | 2022-12-22 20:50 | 5 | 21.1 | 39.3 | 37.6 | 1.746 | 0
1250 | 2022-12-22 20:51 | 5.3 | 20.8 | 39.1 | 37.3 | 1.487 | 0
1251 | 2022-12-22 20:52 | 5 | 20.8 | 39 | 37.2 | 1.489 | 0
1252 | 2022-12-22 20:53 | 5.1 | 20.7 | 38.9 | 37.1 | 1.489 | 0
1253 | 2022-12-22 20:54 | 5.2 | 20.6 | 38.8 | 37 | 1.484 | 0
1254 | 2022-12-22 20:55 | 5.2 | 20.6 | 38.7 | 36.9 | 1.486 | 0
1255 | 2022-12-22 20:56 | 5.2 | 20.5 | 38.6 | 36.8 | 1.487 | 0
1256 | 2022-12-22 20:57 | 5.1 | 20.4 | 38.5 | 36.7 | 1.491 | 0
1257 | 2022-12-22 20:58 | 5.1 | 20.4 | 38.3 | 36.6 | 1.488 | 0
1258 | 2022-12-22 20:59 | 5.3 | 20.3 | 38.2 | 36.5 | 1.489 | 0
1259 | 2022-12-22 21:00 | 5.1 | 20.3 | 38.1 | 36.4 | 1.485 | 0
1260 | 2022-12-22 21:01 | 5.2 | 20.3 | 38.1 | 36.3 | 0 | 0
1261 | 2022-12-22 21:02 | 5.2 | 20.2 | 37.8 | 35.8 | 0 | 0
1262 | 2022-12-22 21:03 | 5.1 | 20.1 | 37.6 | 35.3 | 0 | 0
1263 | 2022-12-22 21:04 | 5.2 | 20.1 | 37.3 | 34.8 | 0 | 0
1264 | 2022-12-22 21:05 | 5.2 | 20.1 | 37.1 | 34.3 | 0 | 0
1265 | 2022-12-22 21:06 | 5.2 | 20.1 | 36.8 | 33.8 | 0 | 0
1266 | 2022-12-22 21:07 | 5.2 | 20 | 36.6 | 33.4 | 0 | 0
1267 | 2022-12-22 21:08 | 5.1 | 20 | 36.3 | 33 | 0 | 0
1268 | 2022-12-22 21:09 | 5.2 | 20 | 36 | 32.5 | 0 | 0
1269 | 2022-12-22 21:10 | 5.2 | 19.9 | 35.8 | 32.2 | 0 | 0
1270 | 2022-12-22 21:11 | 5.1 | 19.9 | 35.5 | 31.8 | 0 | 0
1271 | 2022-12-22 21:12 | 5 | 19.9 | 35.3 | 31.4 | 0 | 0
1272 | 2022-12-22 21:13 | 5.2 | 19.7 | 35 | 31.1 | 0 | 0
1273 | 2022-12-22 21:14 | 5 | 19.8 | 34.8 | 30.8 | 0 | 0
1274 | 2022-12-22 21:15 | 5.1 | 19.7 | 34.6 | 30.4 | 0 | 0
1275 | 2022-12-22 21:16 | 5 | 19.8 | 34.3 | 30.1 | 0 | 0
1276 | 2022-12-22 21:17 | 5.1 | 19.7 | 34.1 | 29.8 | 0 | 0
1277 | 2022-12-22 21:18 | 5 | 19.8 | 33.9 | 29.5 | 0 | 0
1278 | 2022-12-22 21:19 | 5 | 19.7 | 33.6 | 29.2 | 0 | 0
1279 | 2022-12-22 21:20 | 5.1 | 19.8 | 33.4 | 28.9 | 0 | 0
1280 | 2022-12-22 21:21 | 5.2 | 19.6 | 33.2 | 28.7 | 0 | 0
1281 | 2022-12-22 21:22 | 5 | 19.6 | 33 | 28.4 | 0 | 0
1282 | 2022-12-22 21:23 | 5.1 | 19.6 | 32.8 | 28.1 | 0 | 0
1283 | 2022-12-22 21:24 | 5.1 | 19.6 | 32.5 | 27.9 | 0 | 0
1284 | 2022-12-22 21:25 | 5 | 19.6 | 32.3 | 27.6 | 0 | 0
1285 | 2022-12-22 21:26 | 4.8 | 19.6 | 32.1 | 27.4 | 0 | 0
1286 | 2022-12-22 21:27 | 4.7 | 19.6 | 31.9 | 27.1 | 0 | 0
1287 | 2022-12-22 21:28 | 4.9 | 19.6 | 31.7 | 26.9 | 0 | 0
1288 | 2022-12-22 21:29 | 4.8 | 19.6 | 31.5 | 26.7 | 0 | 0
1289 | 2022-12-22 21:30 | 4.8 | 19.6 | 31.2 | 26.4 | 0 | 0
1290 | 2022-12-22 21:31 | 4.7 | 19.5 | 31 | 26.2 | 0 | 0
1291 | 2022-12-22 21:32 | 5 | 19.5 | 30.8 | 26 | 0 | 0
1292 | 2022-12-22 21:33 | 5 | 19.5 | 30.6 | 25.7 | 0 | 0
1293 | 2022-12-22 21:34 | 4.8 | 19.5 | 30.4 | 25.5 | 0 | 0
1294 | 2022-12-22 21:35 | 4.9 | 19.5 | 30.2 | 25.3 | 0 | 0
1295 | 2022-12-22 21:36 | 4.9 | 19.5 | 30 | 25.1 | 0 | 0
1296 | 2022-12-22 21:37 | 5.1 | 19.5 | 29.8 | 24.9 | 0 | 0
1297 | 2022-12-22 21:38 | 5.1 | 19.5 | 29.6 | 24.7 | 0 | 0
1298 | 2022-12-22 21:39 | 5.1 | 19.5 | 29.4 | 24.5 | 0 | 0
1299 | 2022-12-22 21:40 | 5.1 | 19.5 | 29.2 | 24.3 | 0 | 0
1300 | 2022-12-22 21:41 | 5.2 | 19.4 | 29.1 | 24.1 | 0 | 1
1301 | 2022-12-22 21:42 | 5.2 | 19.5 | 28.9 | 23.9 | 0 | 1
1302 | 2022-12-22 21:43 | 5.5 | 19.5 | 28.7 | 23.7 | 0 | 1
1303 | 2022-12-22 21:44 | 5.5 | 19.4 | 28.5 | 23.5 | 0 | 1
1304 | 2022-12-22 21:45 | 5.6 | 19.4 | 28.4 | 23.3 | 0 | 1
1305 | 2022-12-22 21:46 | 5.5 | 19.4 | 28.2 | 23.2 | 0 | 1
1306 | 2022-12-22 21:47 | 5.5 | 19.5 | 28 | 23 | 0 | 1
1307 | 2022-12-22 21:48 | 5.7 | 19.5 | 27.8 | 22.8 | 0 | 1
1308 | 2022-12-22 21:49 | 5.6 | 19.4 | 27.7 | 22.6 | 0 | 1
1309 | 2022-12-22 21:50 | 5.7 | 19.4 | 27.5 | 22.5 | 0 | 1
1310 | 2022-12-22 21:51 | 5.8 | 19.4 | 27.3 | 22.3 | 0 | 1
1311 | 2022-12-22 21:52 | 5.8 | 19.3 | 27.2 | 22.2 | 0 | 1
1312 | 2022-12-22 21:53 | 5.7 | 19.3 | 27 | 22 | 0 | 1
1313 | 2022-12-22 21:54 | 6 | 19.4 | 26.8 | 21.9 | 0 | 1
1314 | 2022-12-22 21:55 | 5.9 | 19.3 | 26.7 | 21.7 | 0 | 1
1315 | 2022-12-22 21:56 | 5.8 | 19.3 | 26.5 | 21.6 | 0 | 1
1316 | 2022-12-22 21:57 | 5.8 | 19.3 | 26.4 | 21.4 | 0 | 1
1317 | 2022-12-22 21:58 | 6 | 19.3 | 26.2 | 21.3 | 0 | 1
1318 | 2022-12-22 21:59 | 6.1 | 19.3 | 26.1 | 21.1 | 0 | 1
1319 | 2022-12-22 22:00 | 6 | 19.3 | 25.9 | 21 | 0 | 1
1320 | 2022-12-22 22:01 | 6.2 | 19.3 | 25.8 | 20.9 | 0 | 1
1321 | 2022-12-22 22:02 | 6.1 | 19.3 | 25.6 | 20.8 | 0 | 1
1322 | 2022-12-22 22:03 | 6.2 | 19.3 | 25.5 | 20.6 | 0 | 1
1323 | 2022-12-22 22:04 | 6.1 | 19.3 | 25.3 | 20.5 | 0 | 1
1324 | 2022-12-22 22:05 | 6.2 | 19.2 | 25.2 | 20.4 | 0 | 1
1325 | 2022-12-22 22:06 | 6.2 | 19.3 | 25 | 20.3 | 0 | 1
1326 | 2022-12-22 22:07 | 6.4 | 19.2 | 24.9 | 20.1 | 0 | 1
1327 | 2022-12-22 22:08 | 6.3 | 19.2 | 24.7 | 20 | 0 | 0
1328 | 2022-12-22 22:09 | 6.5 | 19.2 | 24.6 | 19.9 | 0 | 0
1329 | 2022-12-22 22:10 | 6.4 | 19.2 | 24.5 | 19.8 | 0 | 1
1330 | 2022-12-22 22:11 | 6.6 | 19.2 | 24.4 | 19.7 | 0 | 1
1331 | 2022-12-22 22:12 | 6.6 | 19.2 | 24.2 | 19.6 | 0 | 1
1332 | 2022-12-22 22:13 | 6.7 | 19.2 | 24.1 | 19.4 | 0 | 1
1333 | 2022-12-22 22:14 | 6.6 | 19.3 | 24 | 19.3 | 0 | 1
1334 | 2022-12-22 22:15 | 6.5 | 19.2 | 23.8 | 19.2 | 0 | 0
1335 | 2022-12-22 22:16 | 6.6 | 19.2 | 23.7 | 19.1 | 0 | 0
1336 | 2022-12-22 22:17 | 6.6 | 19.2 | 23.6 | 19 | 0 | 0
1337 | 2022-12-22 22:18 | 6.8 | 19.3 | 23.5 | 18.9 | 0 | 0
1338 | 2022-12-22 22:19 | 6.8 | 19.3 | 23.4 | 18.8 | 0 | 0
1339 | 2022-12-22 22:20 | 6.8 | 19.2 | 23.3 | 18.7 | 0 | 1
1340 | 2022-12-22 22:21 | 6.7 | 19.1 | 23.1 | 18.6 | 0 | 1
1341 | 2022-12-22 22:22 | 6.8 | 19.2 | 23 | 18.5 | 0 | 1
1342 | 2022-12-22 22:23 | 6.9 | 19.2 | 22.9 | 18.4 | 0 | 0
1343 | 2022-12-22 22:24 | 6.9 | 19.1 | 22.8 | 18.3 | 0 | 0
1344 | 2022-12-22 22:25 | 6.9 | 19.1 | 22.7 | 18.2 | 0 | 0
1345 | 2022-12-22 22:26 | 6.9 | 19.1 | 22.6 | 18.1 | 0 | 0
1346 | 2022-12-22 22:27 | 6.9 | 19.1 | 22.5 | 18.1 | 0 | 0
1347 | 2022-12-22 22:28 | 6.8 | 19.1 | 22.4 | 18 | 0 | 0
1348 | 2022-12-22 22:29 | 6.9 | 19.1 | 22.4 | 18 | 0 | 0
1349 | 2022-12-22 22:30 | 6.9 | 19.1 | 22.3 | 17.9 | 0 | 0
1350 | 2022-12-22 22:31 | 7.1 | 19.1 | 22.2 | 17.9 | 0 | 0
1351 | 2022-12-22 22:32 | 6.8 | 19.1 | 22.1 | 17.8 | 0 | 0
1352 | 2022-12-22 22:33 | 7 | 19.1 | 22 | 17.8 | 0 | 0
1353 | 2022-12-22 22:34 | 6.9 | 19.2 | 21.9 | 17.7 | 0 | 0
1354 | 2022-12-22 22:35 | 6.8 | 19 | 21.8 | 17.7 | 0 | 0
1355 | 2022-12-22 22:36 | 7.1 | 19.1 | 21.7 | 17.6 | 0 | 0
1356 | 2022-12-22 22:37 | 7.1 | 19.1 | 21.6 | 17.5 | 0 | 0
1357 | 2022-12-22 22:38 | 7 | 19.1 | 21.5 | 17.5 | 0 | 0
1358 | 2022-12-22 22:39 | 7 | 19.1 | 21.4 | 17.4 | 0 | 0
1359 | 2022-12-22 22:40 | 7.1 | 19.1 | 21.4 | 17.4 | 0 | 0
1360 | 2022-12-22 22:41 | 7 | 19.1 | 21.3 | 17.4 | 0 | 0
1361 | 2022-12-22 22:42 | 7 | 19 | 21.2 | 17.3 | 0 | 0
1362 | 2022-12-22 22:43 | 7.1 | 19 | 21.1 | 17.3 | 0 | 0
1363 | 2022-12-22 22:44 | 7 | 19 | 21 | 17.2 | 0 | 0
1364 | 2022-12-22 22:45 | 7.1 | 19 | 20.9 | 17.2 | 0 | 0
1365 | 2022-12-22 22:46 | 7 | 19 | 20.8 | 17.1 | 0 | 0
1366 | 2022-12-22 22:47 | 7 | 19 | 20.8 | 17.1 | 0 | 0
1367 | 2022-12-22 22:48 | 7 | 19 | 20.7 | 17 | 0 | 0
1368 | 2022-12-22 22:49 | 7.2 | 19 | 20.6 | 17 | 0 | 0
1369 | 2022-12-22 22:50 | 7 | 19 | 20.5 | 16.9 | 0 | 0
1370 | 2022-12-22 22:51 | 7 | 19 | 20.5 | 16.9 | 0 | 0
1371 | 2022-12-22 22:52 | 7 | 19 | 20.4 | 16.8 | 0 | 0
1372 | 2022-12-22 22:53 | 7.1 | 19 | 20.3 | 16.8 | 0 | 0
1373 | 2022-12-22 22:54 | 7.1 | 19 | 20.3 | 16.7 | 0 | 0
1374 | 2022-12-22 22:55 | 7.2 | 19 | 20.2 | 16.7 | 0 | 0
1375 | 2022-12-22 22:56 | 7.3 | 19 | 20.2 | 16.6 | 0 | 0
1376 | 2022-12-22 22:57 | 7.1 | 19 | 20.2 | 16.6 | 0 | 0
1377 | 2022-12-22 22:58 | 7.2 | 19 | 20.1 | 16.5 | 0 | 0
1378 | 2022-12-22 22:59 | 7.2 | 19 | 20 | 16.5 | 0 | 0
1379 | 2022-12-22 23:00 | 7.2 | 18.9 | 20 | 16.4 | 0 | 0
1380 | 2022-12-22 23:01 | 7.2 | 18.9 | 19.9 | 16.4 | 0 | 0
1381 | 2022-12-22 23:02 | 7.2 | 18.9 | 19.8 | 16.3 | 0 | 0
1382 | 2022-12-22 23:03 | 7.2 | 18.8 | 19.7 | 16.3 | 0 | 0
1383 | 2022-12-22 23:04 | 7.2 | 18.9 | 19.7 | 16.2 | 0 | 0
1384 | 2022-12-22 23:05 | 7.4 | 18.8 | 19.6 | 16.2 | 0 | 0
1385 | 2022-12-22 23:06 | 7.4 | 18.9 | 19.6 | 16.2 | 0 | 0
1386 | 2022-12-22 23:07 | 7.2 | 18.9 | 19.5 | 16.1 | 0 | 0
1387 | 2022-12-22 23:08 | 7.4 | 19 | 19.4 | 16.1 | 0 | 0
1388 | 2022-12-22 23:09 | 7.2 | 18.9 | 19.4 | 16 | 0 | 0
1389 | 2022-12-22 23:10 | 7.2 | 18.9 | 19.3 | 16 | 0 | 0
1390 | 2022-12-22 23:11 | 7.4 | 18.9 | 19.3 | 15.9 | 0 | 0
1391 | 2022-12-22 23:12 | 7.2 | 18.9 | 19.2 | 15.9 | 0 | 0
1392 | 2022-12-22 23:13 | 7.4 | 18.9 | 19.1 | 15.9 | 0 | 0
1393 | 2022-12-22 23:14 | 7.1 | 18.9 | 19.1 | 15.8 | 0 | 0
1394 | 2022-12-22 23:15 | 7.1 | 18.8 | 19 | 15.8 | 0 | 0
1395 | 2022-12-22 23:16 | 7.2 | 18.8 | 19 | 15.7 | 0 | 0
1396 | 2022-12-22 23:17 | 7.1 | 18.9 | 18.9 | 15.7 | 0 | 0
1397 | 2022-12-22 23:18 | 7 | 18.9 | 18.9 | 15.7 | 0 | 0
1398 | 2022-12-22 23:19 | 7.1 | 18.9 | 18.8 | 15.6 | 0 | 0
1399 | 2022-12-22 23:20 | 7.1 | 18.9 | 18.8 | 15.6 | 0 | 0
1400 | 2022-12-22 23:21 | 7.1 | 18.9 | 18.7 | 15.5 | 0 | 0
1401 | 2022-12-22 23:22 | 7.2 | 18.8 | 18.6 | 15.5 | 0 | 0
1402 | 2022-12-22 23:23 | 7.2 | 18.8 | 18.6 | 15.4 | 0 | 0
1403 | 2022-12-22 23:24 | 6.9 | 18.9 | 18.5 | 15.4 | 0 | 0
1404 | 2022-12-22 23:25 | 7 | 18.9 | 18.5 | 15.4 | 0 | 0
1405 | 2022-12-22 23:26 | 6.9 | 18.8 | 18.4 | 15.3 | 0 | 0
1406 | 2022-12-22 23:27 | 6.9 | 18.8 | 18.4 | 15.3 | 0 | 0
1407 | 2022-12-22 23:28 | 6.9 | 18.8 | 18.3 | 15.2 | 0 | 0
1408 | 2022-12-22 23:29 | 6.8 | 18.9 | 18.3 | 15.2 | 0 | 0
1409 | 2022-12-22 23:30 | 7 | 18.8 | 18.2 | 15.1 | 0 | 0
1410 | 2022-12-22 23:31 | 6.8 | 18.8 | 18.2 | 15.1 | 0 | 0
1411 | 2022-12-22 23:32 | 6.8 | 18.8 | 18.1 | 15.1 | 0 | 0
1412 | 2022-12-22 23:33 | 6.8 | 18.8 | 18.1 | 15 | 0 | 0
1413 | 2022-12-22 23:34 | 6.9 | 18.8 | 18 | 15 | 0 | 0
1414 | 2022-12-22 23:35 | 7 | 18.8 | 18 | 14.9 | 0 | 0
1415 | 2022-12-22 23:36 | 6.7 | 18.8 | 17.9 | 14.9 | 0 | 0
1416 | 2022-12-22 23:37 | 6.7 | 18.8 | 17.9 | 14.9 | 0 | 0
1417 | 2022-12-22 23:38 | 6.7 | 18.8 | 17.8 | 14.8 | 0 | 0
1418 | 2022-12-22 23:39 | 6.6 | 18.8 | 17.8 | 14.8 | 0 | 0
1419 | 2022-12-22 23:40 | 6.6 | 18.8 | 17.7 | 14.7 | 0 | 0
1420 | 2022-12-22 23:41 | 6.7 | 18.8 | 17.7 | 14.7 | 0 | 0
1421 | 2022-12-22 23:42 | 6.5 | 18.8 | 17.6 | 14.7 | 0 | 0
1422 | 2022-12-22 23:43 | 6.5 | 18.7 | 17.6 | 14.6 | 0 | 0
1423 | 2022-12-22 23:44 | 6.7 | 18.7 | 17.5 | 14.6 | 0 | 0
1424 | 2022-12-22 23:45 | 6.7 | 18.7 | 17.5 | 14.5 | 0 | 0
1425 | 2022-12-22 23:46 | 6.7 | 18.7 | 17.4 | 14.5 | 0 | 0
1426 | 2022-12-22 23:47 | 6.6 | 18.7 | 17.4 | 14.5 | 0 | 0
1427 | 2022-12-22 23:48 | 6.6 | 18.7 | 17.4 | 14.4 | 0 | 0
1428 | 2022-12-22 23:49 | 6.6 | 18.7 | 17.3 | 14.4 | 0 | 0
1429 | 2022-12-22 23:50 | 6.5 | 18.7 | 17.3 | 14.3 | 0 | 0
1430 | 2022-12-22 23:51 | 6.6 | 18.7 | 17.2 | 14.3 | 0 | 0
1431 | 2022-12-22 23:52 | 6.6 | 18.7 | 17.2 | 14.3 | 0 | 0
1432 | 2022-12-22 23:53 | 6.4 | 18.7 | 17.1 | 14.2 | 0 | 0
1433 | 2022-12-22 23:54 | 6.6 | 18.7 | 17.1 | 14.2 | 0 | 0
1434 | 2022-12-22 23:55 | 6.5 | 18.6 | 17.1 | 14.2 | 0 | 0
1435 | 2022-12-22 23:56 | 6.5 | 18.7 | 17 | 14.1 | 0 | 0
1436 | 2022-12-22 23:57 | 6.5 | 18.7 | 17 | 14.1 | 0 | 0
1437 | 2022-12-22 23:58 | 6.5 | 18.7 | 16.9 | 14.1 | 0 | 0
1438 | 2022-12-22 23:59 | 6.5 | 18.6 | 16.9 | 14 | 0 | 0
1439 | 2022-12-23 | 6.6 | 18.6 | 16.8 | 15.2 | 0.051 | 0

## 23-12-2022_WITH HEAT
| Date&time_x | OUTDOOR_TEMP | INDOOR_TEMP | SH_INLET | SH_RETURN | FLOW_FAN_COILS_INDOOR | PYRANOMETER
0 | 2022-12-23 00:01 | 6.5 | 18.6 | 16.8 | 15.3 | 0 | 0
1 | 2022-12-23 00:02 | 6.6 | 18.6 | 17 | 15.4 | 0 | 0
2 | 2022-12-23 00:03 | 6.5 | 18.7 | 39.9 | 18.4 | 0.878 | 0
3 | 2022-12-23 00:04 | 6.6 | 18.6 | 40.3 | 36.6 | 0.929 | 0
4 | 2022-12-23 00:05 | 6.6 | 18.6 | 39.7 | 37 | 0.936 | 0
5 | 2022-12-23 00:06 | 6.6 | 18.6 | 39.9 | 37.1 | 0.932 | 0
6 | 2022-12-23 00:07 | 6.5 | 18.7 | 39.9 | 37.4 | 0.977 | 0
7 | 2022-12-23 00:08 | 6.7 | 18.7 | 40.3 | 37.6 | 0.974 | 0
8 | 2022-12-23 00:09 | 6.5 | 18.8 | 40.3 | 37.8 | 0 | 0
9 | 2022-12-23 00:10 | 6.7 | 18.8 | 40 | 37.4 | 0 | 0
10 | 2022-12-23 00:11 | 6.7 | 18.8 | 39.6 | 36.6 | 0 | 0
11 | 2022-12-23 00:12 | 6.7 | 18.8 | 39.2 | 35.9 | 0 | 0
12 | 2022-12-23 00:13 | 6.7 | 18.9 | 38.9 | 35.2 | 0 | 0
13 | 2022-12-23 00:14 | 6.7 | 18.8 | 38.6 | 34.6 | 0 | 0
14 | 2022-12-23 00:15 | 6.8 | 18.8 | 38.2 | 34 | 0 | 0
15 | 2022-12-23 00:16 | 6.7 | 18.8 | 37.9 | 33.4 | 0 | 0
16 | 2022-12-23 00:17 | 6.8 | 18.7 | 37.6 | 32.9 | 0 | 0
17 | 2022-12-23 00:18 | 6.7 | 18.7 | 37.4 | 32.5 | 0 | 0
18 | 2022-12-23 00:19 | 6.7 | 18.7 | 37.1 | 32 | 0 | 0
19 | 2022-12-23 00:20 | 6.7 | 18.7 | 36.8 | 31.6 | 0 | 0
20 | 2022-12-23 00:21 | 6.9 | 18.7 | 36.6 | 31.2 | 0 | 0
21 | 2022-12-23 00:22 | 7 | 18.8 | 36.3 | 30.8 | 0 | 0
22 | 2022-12-23 00:23 | 7 | 18.7 | 36.1 | 30.4 | 0 | 0
23 | 2022-12-23 00:24 | 6.8 | 18.7 | 35.9 | 30.1 | 0 | 0
24 | 2022-12-23 00:25 | 6.8 | 18.6 | 35.6 | 29.7 | 0 | 0
25 | 2022-12-23 00:26 | 6.8 | 18.6 | 35.4 | 29.4 | 0 | 0
26 | 2022-12-23 00:27 | 6.9 | 18.6 | 35.2 | 29.1 | 0 | 0
27 | 2022-12-23 00:28 | 7 | 18.7 | 35 | 28.8 | 0 | 0
28 | 2022-12-23 00:29 | 7 | 18.7 | 34.7 | 28.5 | 0 | 0
29 | 2022-12-23 00:30 | 6.9 | 18.6 | 34.5 | 28.2 | 0 | 0
30 | 2022-12-23 00:31 | 7.1 | 18.6 | 34.3 | 27.9 | 0 | 0
31 | 2022-12-23 00:32 | 6.8 | 18.6 | 34.1 | 27.7 | 0 | 0
32 | 2022-12-23 00:33 | 6.8 | 18.5 | 33.9 | 27.4 | 0 | 0
33 | 2022-12-23 00:34 | 7.1 | 18.6 | 33.7 | 27.2 | 0 | 0
34 | 2022-12-23 00:35 | 7 | 18.6 | 33.5 | 26.9 | 0 | 0
35 | 2022-12-23 00:36 | 7.1 | 18.6 | 33.3 | 26.7 | 0 | 0
36 | 2022-12-23 00:37 | 7.1 | 18.6 | 33.1 | 26.5 | 0 | 0
37 | 2022-12-23 00:38 | 7 | 18.6 | 32.9 | 26.2 | 0 | 0
38 | 2022-12-23 00:39 | 7 | 18.6 | 32.7 | 26 | 0 | 0
39 | 2022-12-23 00:40 | 7.1 | 18.6 | 32.5 | 25.8 | 0 | 0
40 | 2022-12-23 00:41 | 6.9 | 18.6 | 32.3 | 25.6 | 0 | 0
41 | 2022-12-23 00:42 | 7 | 18.6 | 32.1 | 25.4 | 0 | 0
42 | 2022-12-23 00:43 | 6.9 | 18.6 | 31.9 | 25.2 | 0 | 0
43 | 2022-12-23 00:44 | 6.9 | 18.5 | 31.7 | 25 | 0 | 0
44 | 2022-12-23 00:45 | 6.9 | 18.6 | 31.6 | 24.8 | 0 | 0
45 | 2022-12-23 00:46 | 7 | 18.6 | 31.4 | 24.6 | 0 | 0
46 | 2022-12-23 00:47 | 7.2 | 18.6 | 31.2 | 24.4 | 0 | 0
47 | 2022-12-23 00:48 | 6.9 | 18.6 | 31 | 24.3 | 0 | 0
48 | 2022-12-23 00:49 | 7.1 | 18.5 | 30.8 | 24.1 | 0 | 0
49 | 2022-12-23 00:50 | 7 | 18.5 | 30.6 | 27.8 | 0.068 | 0
50 | 2022-12-23 00:51 | 7 | 18.6 | 30.5 | 27.9 | 0 | 0
51 | 2022-12-23 00:52 | 7 | 18.5 | 30.9 | 29.1 | 0 | 0
52 | 2022-12-23 00:53 | 7.1 | 18.5 | 40.2 | 33 | 0.923 | 0
53 | 2022-12-23 00:54 | 7.1 | 18.5 | 39.9 | 37.5 | 0.977 | 0
54 | 2022-12-23 00:55 | 7.1 | 18.5 | 39.9 | 37.2 | 0.977 | 0
55 | 2022-12-23 00:56 | 7.1 | 18.5 | 40.2 | 37.6 | 0.976 | 0
56 | 2022-12-23 00:57 | 7.2 | 18.5 | 40.4 | 37.8 | 0.975 | 0
57 | 2022-12-23 00:58 | 7.2 | 18.6 | 40.5 | 38 | 0.975 | 0
58 | 2022-12-23 00:59 | 7.1 | 18.7 | 40.4 | 38.1 | 0 | 0
59 | 2022-12-23 01:00 | 7.1 | 18.7 | 40.2 | 37.6 | 0 | 0
60 | 2022-12-23 01:01 | 7.2 | 18.8 | 39.9 | 36.9 | 0 | 0
61 | 2022-12-23 01:02 | 7.2 | 18.8 | 39.6 | 36.3 | 0 | 0
62 | 2022-12-23 01:03 | 7.2 | 18.6 | 39.3 | 35.7 | 0 | 0
63 | 2022-12-23 01:04 | 7.1 | 18.6 | 39 | 35.2 | 0 | 0
64 | 2022-12-23 01:05 | 7.2 | 18.6 | 38.7 | 34.6 | 0 | 0
65 | 2022-12-23 01:06 | 7.1 | 18.6 | 38.4 | 34.1 | 0 | 0
66 | 2022-12-23 01:07 | 7.1 | 18.6 | 38.2 | 33.6 | 0 | 0
67 | 2022-12-23 01:08 | 7.1 | 18.6 | 37.9 | 33.2 | 0 | 0
68 | 2022-12-23 01:09 | 7.1 | 18.6 | 37.7 | 32.8 | 0 | 0
69 | 2022-12-23 01:10 | 7.3 | 18.6 | 37.4 | 32.3 | 0 | 0
70 | 2022-12-23 01:11 | 7.1 | 18.5 | 37.2 | 32 | 0 | 0
71 | 2022-12-23 01:12 | 7.1 | 18.5 | 36.9 | 31.6 | 0 | 0
72 | 2022-12-23 01:13 | 7.3 | 18.6 | 36.7 | 31.2 | 0 | 0
73 | 2022-12-23 01:14 | 7.1 | 18.5 | 36.5 | 30.9 | 0 | 0
74 | 2022-12-23 01:15 | 7.1 | 18.6 | 36.2 | 30.5 | 0 | 0
75 | 2022-12-23 01:16 | 7.2 | 18.5 | 36 | 30.2 | 0 | 0
76 | 2022-12-23 01:17 | 7.3 | 18.5 | 35.8 | 29.9 | 0 | 0
77 | 2022-12-23 01:18 | 7.3 | 18.4 | 35.5 | 29.6 | 0 | 0
78 | 2022-12-23 01:19 | 7.2 | 18.5 | 35.3 | 29.3 | 0 | 0
79 | 2022-12-23 01:20 | 7.1 | 18.4 | 35.1 | 29 | 0 | 0
80 | 2022-12-23 01:21 | 7.2 | 18.5 | 34.9 | 28.7 | 0 | 0
81 | 2022-12-23 01:22 | 7.1 | 18.5 | 34.7 | 28.5 | 0 | 0
82 | 2022-12-23 01:23 | 7.1 | 18.5 | 34.5 | 28.2 | 0 | 0
83 | 2022-12-23 01:24 | 7.1 | 18.5 | 34.3 | 27.9 | 0 | 0
84 | 2022-12-23 01:25 | 7.2 | 18.5 | 34.1 | 27.7 | 0 | 0
85 | 2022-12-23 01:26 | 7.1 | 18.4 | 33.8 | 27.4 | 0 | 0
86 | 2022-12-23 01:27 | 7.1 | 18.4 | 33.6 | 27.2 | 0 | 0
87 | 2022-12-23 01:28 | 7.1 | 18.4 | 33.4 | 27 | 0 | 0
88 | 2022-12-23 01:29 | 7.2 | 18.4 | 33.2 | 26.7 | 0 | 0
89 | 2022-12-23 01:30 | 7.2 | 18.5 | 33 | 26.5 | 0 | 0
90 | 2022-12-23 01:31 | 7.1 | 18.4 | 32.8 | 26.3 | 0 | 0
91 | 2022-12-23 01:32 | 7.1 | 18.4 | 32.6 | 26.1 | 0 | 0
92 | 2022-12-23 01:33 | 7.2 | 18.5 | 32.4 | 30.1 | 0.022 | 0
93 | 2022-12-23 01:34 | 7.1 | 18.4 | 32.2 | 30 | 0 | 0
94 | 2022-12-23 01:35 | 7.1 | 18.5 | 38 | 30.4 | 0.183 | 0
95 | 2022-12-23 01:36 | 7.1 | 18.5 | 40 | 33.6 | 0.475 | 0
96 | 2022-12-23 01:37 | 7.2 | 18.5 | 39.9 | 37 | 0.932 | 0
97 | 2022-12-23 01:38 | 7.1 | 18.4 | 40.1 | 37.2 | 0.942 | 0
98 | 2022-12-23 01:39 | 7.1 | 18.5 | 40 | 37.6 | 0.941 | 0
99 | 2022-12-23 01:40 | 7 | 18.5 | 40.1 | 37.7 | 0.977 | 0
100 | 2022-12-23 01:41 | 7.2 | 18.6 | 40.5 | 37.8 | 0.977 | 0
101 | 2022-12-23 01:42 | 7.2 | 18.6 | 40.5 | 37.6 | 0 | 0
102 | 2022-12-23 01:43 | 7.1 | 18.6 | 40.1 | 37 | 0 | 0
103 | 2022-12-23 01:44 | 7.1 | 18.6 | 39.8 | 36.3 | 0 | 0
104 | 2022-12-23 01:45 | 7.1 | 18.5 | 39.5 | 35.8 | 0 | 0
105 | 2022-12-23 01:46 | 7.2 | 18.5 | 39.2 | 35.2 | 0 | 0
106 | 2022-12-23 01:47 | 7.3 | 18.5 | 38.9 | 34.7 | 0 | 0
107 | 2022-12-23 01:48 | 7.2 | 18.5 | 38.6 | 34.2 | 0 | 0
108 | 2022-12-23 01:49 | 7.2 | 18.5 | 38.4 | 33.7 | 0 | 0
109 | 2022-12-23 01:50 | 7.1 | 18.5 | 38.1 | 33.3 | 0 | 0
110 | 2022-12-23 01:51 | 7.2 | 18.5 | 37.9 | 32.8 | 0 | 0
111 | 2022-12-23 01:52 | 7.3 | 18.5 | 37.6 | 32.4 | 0 | 0
112 | 2022-12-23 01:53 | 7.1 | 18.5 | 37.3 | 32 | 0 | 0
113 | 2022-12-23 01:54 | 7.3 | 18.4 | 37.1 | 31.6 | 0 | 0
114 | 2022-12-23 01:55 | 7.1 | 18.4 | 36.9 | 31.3 | 0 | 0
115 | 2022-12-23 01:56 | 7.2 | 18.4 | 36.6 | 30.9 | 0 | 0
116 | 2022-12-23 01:57 | 7.1 | 18.4 | 36.4 | 30.6 | 0 | 0
117 | 2022-12-23 01:58 | 7.2 | 18.4 | 36.2 | 30.3 | 0 | 0
118 | 2022-12-23 01:59 | 7.2 | 18.4 | 36 | 30 | 0 | 0
119 | 2022-12-23 02:00 | 7.3 | 18.4 | 35.7 | 29.7 | 0 | 0
120 | 2022-12-23 02:01 | 7.3 | 18.4 | 35.5 | 29.4 | 0 | 0
121 | 2022-12-23 02:02 | 7.2 | 18.4 | 35.3 | 29.1 | 0 | 0
122 | 2022-12-23 02:03 | 7.3 | 18.4 | 35.1 | 28.8 | 0 | 0
123 | 2022-12-23 02:04 | 7.3 | 18.4 | 34.9 | 28.5 | 0 | 0
124 | 2022-12-23 02:05 | 7.4 | 18.4 | 34.6 | 28.3 | 0 | 0
125 | 2022-12-23 02:06 | 7.3 | 18.4 | 34.4 | 28 | 0 | 0
126 | 2022-12-23 02:07 | 7.3 | 18.4 | 34.2 | 27.8 | 0 | 0
127 | 2022-12-23 02:08 | 7.2 | 18.4 | 34 | 27.5 | 0 | 0
128 | 2022-12-23 02:09 | 7.4 | 18.4 | 33.8 | 30 | 0 | 0
129 | 2022-12-23 02:10 | 7.3 | 18.4 | 33.6 | 31.1 | 0 | 0
130 | 2022-12-23 02:11 | 7.3 | 18.4 | 33.6 | 31.7 | 0 | 0
131 | 2022-12-23 02:12 | 7.5 | 18.4 | 39.3 | 33.2 | 0.926 | 0
132 | 2022-12-23 02:13 | 7.3 | 18.4 | 38.9 | 36.7 | 0.979 | 0
133 | 2022-12-23 02:14 | 7.5 | 18.3 | 38.8 | 36.4 | 0.976 | 0
134 | 2022-12-23 02:15 | 7.3 | 18.4 | 38.9 | 36.5 | 0.979 | 0
135 | 2022-12-23 02:16 | 7.3 | 18.4 | 38.9 | 36.6 | 0.976 | 0
136 | 2022-12-23 02:17 | 7.3 | 18.5 | 38.8 | 36.6 | 0.976 | 0
137 | 2022-12-23 02:18 | 7.4 | 18.5 | 38.7 | 36.5 | 0.975 | 0
138 | 2022-12-23 02:19 | 7.5 | 18.5 | 38.6 | 36.3 | 0 | 0
139 | 2022-12-23 02:20 | 7.3 | 18.6 | 38.3 | 35.8 | 0 | 0
140 | 2022-12-23 02:21 | 7.5 | 18.5 | 38 | 35.2 | 0 | 0
141 | 2022-12-23 02:22 | 7.3 | 18.6 | 37.8 | 34.7 | 0 | 0
142 | 2022-12-23 02:23 | 7.3 | 18.5 | 37.5 | 34.2 | 0 | 0
143 | 2022-12-23 02:24 | 7.5 | 18.5 | 37.3 | 33.7 | 0 | 0
144 | 2022-12-23 02:25 | 7.3 | 18.4 | 37.1 | 33.2 | 0 | 0
145 | 2022-12-23 02:26 | 7.3 | 18.4 | 36.8 | 32.8 | 0 | 0
146 | 2022-12-23 02:27 | 7.4 | 18.5 | 36.6 | 32.4 | 0 | 0
147 | 2022-12-23 02:28 | 7.2 | 18.4 | 36.3 | 32 | 0 | 0
148 | 2022-12-23 02:29 | 7.5 | 18.4 | 36.1 | 31.6 | 0 | 0
149 | 2022-12-23 02:30 | 7.3 | 18.4 | 35.9 | 31.2 | 0 | 0
150 | 2022-12-23 02:31 | 7.4 | 18.4 | 35.6 | 30.9 | 0 | 0
151 | 2022-12-23 02:32 | 7.3 | 18.4 | 35.4 | 30.6 | 0 | 0
152 | 2022-12-23 02:33 | 7.4 | 18.3 | 35.2 | 30.2 | 0 | 0
153 | 2022-12-23 02:34 | 7.3 | 18.4 | 35 | 29.9 | 0 | 0
154 | 2022-12-23 02:35 | 7.2 | 18.4 | 34.8 | 29.6 | 0 | 0
155 | 2022-12-23 02:36 | 7.4 | 18.4 | 34.6 | 29.3 | 0 | 0
156 | 2022-12-23 02:37 | 7.3 | 18.4 | 34.4 | 29 | 0 | 0
157 | 2022-12-23 02:38 | 7.3 | 18.3 | 34.1 | 28.7 | 0 | 0
158 | 2022-12-23 02:39 | 7.2 | 18.4 | 33.9 | 28.5 | 0 | 0
159 | 2022-12-23 02:40 | 7.2 | 18.4 | 33.7 | 28.2 | 0 | 0
160 | 2022-12-23 02:41 | 7.3 | 18.3 | 33.5 | 27.9 | 0 | 0
161 | 2022-12-23 02:42 | 7.4 | 18.4 | 33.3 | 30.8 | 0.086 | 0
162 | 2022-12-23 02:43 | 7.3 | 18.3 | 33.1 | 31 | 0 | 0
163 | 2022-12-23 02:44 | 7.3 | 18.3 | 32.9 | 30.8 | 0 | 0
164 | 2022-12-23 02:45 | 7.4 | 18.3 | 37.6 | 23.4 | 0.561 | 0
165 | 2022-12-23 02:46 | 7.4 | 18.4 | 37 | 33.8 | 1.606 | 0
166 | 2022-12-23 02:47 | 7.4 | 18.3 | 36.9 | 34.6 | 1.625 | 0
167 | 2022-12-23 02:48 | 7.4 | 18.3 | 36.2 | 34.4 | 1.622 | 0
168 | 2022-12-23 02:49 | 7.4 | 18.3 | 37 | 34.2 | 1.631 | 0
169 | 2022-12-23 02:50 | 7.2 | 18.4 | 37.5 | 35.1 | 1.624 | 0
170 | 2022-12-23 02:51 | 7.2 | 18.4 | 37.5 | 35.4 | 1.63 | 0
171 | 2022-12-23 02:52 | 7.3 | 18.5 | 37.4 | 35.3 | 1.621 | 0
172 | 2022-12-23 02:53 | 7.4 | 18.5 | 37.4 | 36.1 | 1.623 | 0
173 | 2022-12-23 02:54 | 7.2 | 18.6 | 37.3 | 36.2 | 1.622 | 0
174 | 2022-12-23 02:55 | 7.3 | 18.6 | 37.2 | 36.1 | 1.624 | 0
175 | 2022-12-23 02:56 | 7.4 | 18.6 | 37.2 | 36 | 1.582 | 0
176 | 2022-12-23 02:57 | 7.3 | 18.6 | 37.2 | 35.7 | 1.103 | 0
177 | 2022-12-23 02:58 | 7.3 | 18.5 | 37.1 | 35.7 | 1.09 | 0
178 | 2022-12-23 02:59 | 7.3 | 18.5 | 37 | 35.6 | 1.086 | 0
179 | 2022-12-23 03:00 | 7.5 | 18.5 | 37.1 | 35.5 | 1.091 | 0
180 | 2022-12-23 03:01 | 7.5 | 18.5 | 37.5 | 35.6 | 1.086 | 0
181 | 2022-12-23 03:02 | 7.2 | 18.4 | 37.6 | 36.1 | 1.085 | 0
182 | 2022-12-23 03:03 | 7.2 | 18.4 | 37.2 | 35.9 | 1.087 | 0
183 | 2022-12-23 03:04 | 7.2 | 18.4 | 37.3 | 35.7 | 1.089 | 0
184 | 2022-12-23 03:05 | 7.2 | 18.4 | 37.6 | 35.8 | 1.087 | 0
185 | 2022-12-23 03:06 | 7.5 | 18.5 | 38.2 | 36.2 | 1.084 | 0
186 | 2022-12-23 03:07 | 7.3 | 18.4 | 38.6 | 36.7 | 1.086 | 0
187 | 2022-12-23 03:08 | 7.3 | 18.5 | 38.9 | 37 | 1.088 | 0
188 | 2022-12-23 03:09 | 7.3 | 18.4 | 39.4 | 37.3 | 1.087 | 0
189 | 2022-12-23 03:10 | 7.2 | 18.4 | 39.8 | 37.7 | 1.088 | 0
190 | 2022-12-23 03:11 | 7.5 | 18.4 | 40.3 | 38.1 | 1.087 | 0
191 | 2022-12-23 03:12 | 7.3 | 18.5 | 40.6 | 38.6 | 1.088 | 0
192 | 2022-12-23 03:13 | 7.5 | 18.5 | 41 | 38.9 | 1.092 | 0
193 | 2022-12-23 03:14 | 7.3 | 18.4 | 41.5 | 39.3 | 1.091 | 0
194 | 2022-12-23 03:15 | 7.4 | 18.5 | 41 | 39.6 | 1.093 | 0
195 | 2022-12-23 03:16 | 7.3 | 18.4 | 41.1 | 39.2 | 1.087 | 0
196 | 2022-12-23 03:17 | 7.4 | 18.4 | 40.8 | 39.3 | 1.092 | 0
197 | 2022-12-23 03:18 | 7.3 | 18.5 | 40.6 | 39.2 | 0 | 0
198 | 2022-12-23 03:19 | 7.4 | 18.5 | 40.4 | 38.7 | 0 | 0
199 | 2022-12-23 03:20 | 7.4 | 18.4 | 40.7 | 38.3 | 1.091 | 0
200 | 2022-12-23 03:21 | 7.4 | 18.4 | 40.4 | 40.2 | 1.089 | 0
201 | 2022-12-23 03:22 | 7.4 | 18.4 | 40.4 | 37.4 | 1.306 | 0
202 | 2022-12-23 03:23 | 7.3 | 18.4 | 40.5 | 38.5 | 1.512 | 0
203 | 2022-12-23 03:24 | 7.4 | 18.4 | 40.6 | 33.6 | 1.598 | 0
204 | 2022-12-23 03:25 | 7.3 | 18.4 | 40.2 | 37.9 | 1.568 | 0
205 | 2022-12-23 03:26 | 7.5 | 18.5 | 40 | 37.8 | 1.568 | 0
206 | 2022-12-23 03:27 | 7.4 | 18.5 | 39.8 | 37.6 | 1.567 | 0
207 | 2022-12-23 03:28 | 7.5 | 18.6 | 39.8 | 38.2 | 1.567 | 0
208 | 2022-12-23 03:29 | 7.5 | 18.6 | 39.7 | 38.6 | 1.568 | 0
209 | 2022-12-23 03:30 | 7.3 | 18.6 | 39.7 | 38.6 | 1.57 | 0
210 | 2022-12-23 03:31 | 7.6 | 18.6 | 39.7 | 38.5 | 1.537 | 0
211 | 2022-12-23 03:32 | 7.6 | 18.5 | 39.7 | 38.1 | 0.991 | 0
212 | 2022-12-23 03:33 | 7.6 | 18.5 | 39.6 | 38.1 | 0.975 | 0
213 | 2022-12-23 03:34 | 7.7 | 18.5 | 39.6 | 38 | 0.974 | 0
214 | 2022-12-23 03:35 | 7.7 | 18.4 | 39.5 | 38 | 0.974 | 0
215 | 2022-12-23 03:36 | 7.5 | 18.5 | 39.4 | 38 | 0.974 | 0
216 | 2022-12-23 03:37 | 7.6 | 18.4 | 39.3 | 37.8 | 0.973 | 0
217 | 2022-12-23 03:38 | 7.7 | 18.4 | 39.2 | 37.7 | 0.972 | 0
218 | 2022-12-23 03:39 | 7.6 | 18.4 | 39.1 | 37.6 | 0.975 | 0
219 | 2022-12-23 03:40 | 7.5 | 18.4 | 39 | 37.6 | 0.974 | 0
220 | 2022-12-23 03:41 | 7.5 | 18.3 | 38.9 | 37.5 | 0.971 | 0
221 | 2022-12-23 03:42 | 7.6 | 18.3 | 38.8 | 37.4 | 0.97 | 0
222 | 2022-12-23 03:43 | 7.7 | 18.3 | 38.7 | 37.3 | 0.974 | 0
223 | 2022-12-23 03:44 | 7.8 | 18.3 | 38.6 | 37.2 | 0.97 | 0
224 | 2022-12-23 03:45 | 7.6 | 18.3 | 38.6 | 37.1 | 0 | 0
225 | 2022-12-23 03:46 | 7.6 | 18.2 | 38.4 | 36.9 | 0 | 0
226 | 2022-12-23 03:47 | 7.7 | 18.2 | 38.2 | 36.4 | 0 | 0
227 | 2022-12-23 03:48 | 7.8 | 18.3 | 38 | 35.9 | 0 | 0
228 | 2022-12-23 03:49 | 7.6 | 18.4 | 37.7 | 35.4 | 0 | 0
229 | 2022-12-23 03:50 | 7.5 | 18.3 | 37.5 | 34.9 | 0 | 0
230 | 2022-12-23 03:51 | 7.5 | 18.2 | 37.3 | 34.5 | 0 | 0
231 | 2022-12-23 03:52 | 7.7 | 18.2 | 37.1 | 36 | 0.015 | 0
232 | 2022-12-23 03:53 | 7.7 | 18.2 | 36.9 | 36 | 0 | 0
233 | 2022-12-23 03:54 | 7.6 | 18.2 | 38.2 | 30.1 | 0.825 | 0
234 | 2022-12-23 03:55 | 7.6 | 18.2 | 38 | 35.8 | 0.97 | 0
235 | 2022-12-23 03:56 | 7.6 | 18.3 | 37.7 | 35.7 | 0.975 | 0
236 | 2022-12-23 03:57 | 7.8 | 18.3 | 37.8 | 35.7 | 0.972 | 0
237 | 2022-12-23 03:58 | 7.8 | 18.4 | 37.6 | 35.6 | 0.974 | 0
238 | 2022-12-23 03:59 | 7.6 | 18.4 | 37.5 | 35.5 | 0.971 | 0
239 | 2022-12-23 04:00 | 7.6 | 18.4 | 37.4 | 35.5 | 0.972 | 0
240 | 2022-12-23 04:01 | 7.6 | 18.5 | 37.4 | 35.3 | 0 | 0
241 | 2022-12-23 04:02 | 7.8 | 18.5 | 37.2 | 35 | 0 | 0
242 | 2022-12-23 04:03 | 7.7 | 18.5 | 36.9 | 34.5 | 0 | 0
243 | 2022-12-23 04:04 | 7.9 | 18.4 | 36.7 | 34 | 0 | 0
244 | 2022-12-23 04:05 | 7.8 | 18.4 | 36.5 | 33.6 | 0 | 0
245 | 2022-12-23 04:06 | 7.8 | 18.3 | 36.3 | 33.2 | 0 | 0
246 | 2022-12-23 04:07 | 7.7 | 18.3 | 36.1 | 32.8 | 0 | 0
247 | 2022-12-23 04:08 | 7.8 | 18.3 | 35.8 | 32.4 | 0 | 0
248 | 2022-12-23 04:09 | 7.8 | 18.3 | 35.6 | 32 | 0 | 0
249 | 2022-12-23 04:10 | 8 | 18.3 | 35.4 | 31.6 | 0 | 0
250 | 2022-12-23 04:11 | 7.8 | 18.3 | 35.2 | 31.3 | 0 | 0
251 | 2022-12-23 04:12 | 7.8 | 18.2 | 35 | 31 | 0 | 0
252 | 2022-12-23 04:13 | 7.8 | 18.2 | 34.8 | 30.6 | 0 | 0
253 | 2022-12-23 04:14 | 7.8 | 18.3 | 34.6 | 30.3 | 0 | 0
254 | 2022-12-23 04:15 | 7.9 | 18.2 | 34.4 | 30 | 0 | 0
255 | 2022-12-23 04:16 | 7.9 | 18.3 | 34.2 | 29.8 | 0 | 0
256 | 2022-12-23 04:17 | 7.9 | 18.2 | 34 | 29.5 | 0 | 0
257 | 2022-12-23 04:18 | 7.8 | 18.2 | 33.8 | 29.2 | 0 | 0
258 | 2022-12-23 04:19 | 7.9 | 18.3 | 33.6 | 29 | 0 | 0
259 | 2022-12-23 04:20 | 7.9 | 18.2 | 33.4 | 28.7 | 0 | 0
260 | 2022-12-23 04:21 | 7.8 | 18.2 | 33.2 | 28.5 | 0 | 0
261 | 2022-12-23 04:22 | 7.9 | 18.2 | 33 | 30.7 | 0.089 | 0
262 | 2022-12-23 04:23 | 7.8 | 18.2 | 32.8 | 30.8 | 0 | 0
263 | 2022-12-23 04:24 | 8 | 18.2 | 38.5 | 31 | 0.117 | 0
264 | 2022-12-23 04:25 | 7.8 | 18.2 | 40.9 | 37.3 | 0.971 | 0
265 | 2022-12-23 04:26 | 7.8 | 18.2 | 40.2 | 38.1 | 0.978 | 0
266 | 2022-12-23 04:27 | 7.8 | 18.2 | 40.5 | 37.8 | 0.977 | 0
267 | 2022-12-23 04:28 | 7.7 | 18.3 | 40.6 | 38.1 | 0.977 | 0
268 | 2022-12-23 04:29 | 7.7 | 18.3 | 40.7 | 38.2 | 0.976 | 0
269 | 2022-12-23 04:30 | 7.6 | 18.4 | 40.7 | 38.2 | 0 | 0
270 | 2022-12-23 04:31 | 7.5 | 18.4 | 40.5 | 37.9 | 0 | 0
271 | 2022-12-23 04:32 | 7.7 | 18.4 | 40.2 | 37.3 | 0 | 0
272 | 2022-12-23 04:33 | 7.7 | 18.5 | 39.9 | 36.7 | 0 | 0
273 | 2022-12-23 04:34 | 7.6 | 18.3 | 39.6 | 36.1 | 0 | 0
274 | 2022-12-23 04:35 | 7.6 | 18.3 | 39.3 | 35.6 | 0 | 0
275 | 2022-12-23 04:36 | 7.5 | 18.3 | 39 | 36.7 | 0.016 | 0
276 | 2022-12-23 04:37 | 7.4 | 18.3 | 38.7 | 37.1 | 0.011 | 0
277 | 2022-12-23 04:38 | 7.4 | 18.2 | 38.6 | 37.8 | 0 | 0
278 | 2022-12-23 04:39 | 7.5 | 18.3 | 40.1 | 28.5 | 1.001 | 0
279 | 2022-12-23 04:40 | 7.3 | 18.2 | 39.7 | 37.9 | 1.092 | 0
280 | 2022-12-23 04:41 | 7.2 | 18.3 | 39.6 | 37.9 | 1.091 | 0
281 | 2022-12-23 04:42 | 7.2 | 18.2 | 39.1 | 37.9 | 1.093 | 0
282 | 2022-12-23 04:43 | 7.4 | 18.3 | 39 | 37.4 | 1.091 | 0
283 | 2022-12-23 04:44 | 7.2 | 18.2 | 39 | 37.3 | 1.086 | 0
284 | 2022-12-23 04:45 | 7.2 | 18.2 | 39 | 37.3 | 1.097 | 0
285 | 2022-12-23 04:46 | 7.3 | 18.2 | 38.9 | 37.3 | 1.093 | 0
286 | 2022-12-23 04:47 | 7.2 | 18.2 | 38.8 | 37.3 | 1.084 | 0
287 | 2022-12-23 04:48 | 7.4 | 18.3 | 38.7 | 37.2 | 1.095 | 0
288 | 2022-12-23 04:49 | 7.4 | 18.2 | 38.7 | 37.1 | 1.087 | 0
289 | 2022-12-23 04:50 | 7.3 | 18.3 | 38.6 | 37.1 | 1.088 | 0
290 | 2022-12-23 04:51 | 7.1 | 18.2 | 38.5 | 37 | 1.092 | 0
291 | 2022-12-23 04:52 | 7.3 | 18.3 | 38.5 | 36.9 | 1.087 | 0
292 | 2022-12-23 04:53 | 7.2 | 18.2 | 38.4 | 36.9 | 1.089 | 0
293 | 2022-12-23 04:54 | 7.1 | 18.3 | 38.4 | 35.4 | 1.615 | 0
294 | 2022-12-23 04:55 | 7.1 | 18.3 | 38.4 | 36.1 | 1.625 | 0
295 | 2022-12-23 04:56 | 7.2 | 18.3 | 38.2 | 36.1 | 1.628 | 0
296 | 2022-12-23 04:57 | 7.2 | 18.3 | 38.3 | 36 | 1.627 | 0
297 | 2022-12-23 04:58 | 7.1 | 18.4 | 38.3 | 36.1 | 1.626 | 0
298 | 2022-12-23 04:59 | 7 | 18.4 | 38.3 | 36.1 | 1.634 | 0
299 | 2022-12-23 05:00 | 6.9 | 18.6 | 38.2 | 36 | 1.617 | 0
300 | 2022-12-23 05:01 | 7.1 | 18.6 | 38.1 | 36.9 | 1.627 | 0
301 | 2022-12-23 05:02 | 7.1 | 18.6 | 38 | 36.9 | 1.629 | 0
302 | 2022-12-23 05:03 | 6.9 | 18.6 | 37.9 | 36.8 | 1.625 | 0
303 | 2022-12-23 05:04 | 6.8 | 18.6 | 38 | 36.7 | 1.541 | 0
304 | 2022-12-23 05:05 | 6.9 | 18.6 | 38.2 | 36.4 | 1.092 | 0
305 | 2022-12-23 05:06 | 6.9 | 18.5 | 38.4 | 36.7 | 1.088 | 0
306 | 2022-12-23 05:07 | 6.7 | 18.5 | 39 | 36.9 | 1.09 | 0
307 | 2022-12-23 05:08 | 6.8 | 18.5 | 39.3 | 37.4 | 1.087 | 0
308 | 2022-12-23 05:09 | 6.9 | 18.4 | 39.5 | 37.7 | 1.087 | 0
309 | 2022-12-23 05:10 | 6.7 | 18.4 | 39.9 | 37.9 | 1.089 | 0
310 | 2022-12-23 05:11 | 6.8 | 18.3 | 40.3 | 38.8 | 1.086 | 0
311 | 2022-12-23 05:12 | 6.6 | 18.4 | 40.8 | 39.9 | 1.09 | 0
312 | 2022-12-23 05:13 | 6.7 | 18.4 | 41.2 | 40.3 | 1.088 | 0
313 | 2022-12-23 05:14 | 6.8 | 18.3 | 41.7 | 37.1 | 1.488 | 0
314 | 2022-12-23 05:15 | 6.6 | 18.3 | 41.8 | 40.5 | 1.497 | 0
315 | 2022-12-23 05:16 | 6.5 | 18.4 | 41.6 | 40.4 | 1.452 | 0
316 | 2022-12-23 05:17 | 6.6 | 18.4 | 41.5 | 40.1 | 1.258 | 0
317 | 2022-12-23 05:18 | 6.7 | 18.3 | 41.5 | 39.8 | 0.978 | 0
318 | 2022-12-23 05:19 | 6.5 | 18.3 | 41.5 | 39.8 | 0.974 | 0
319 | 2022-12-23 05:20 | 6.5 | 18.3 | 41.4 | 39.7 | 0.977 | 0
320 | 2022-12-23 05:21 | 6.3 | 18.3 | 41.2 | 39.7 | 0.974 | 0
321 | 2022-12-23 05:22 | 6.5 | 18.2 | 41.1 | 39.5 | 0.974 | 0
322 | 2022-12-23 05:23 | 6.4 | 18.3 | 41 | 39.4 | 0.971 | 0
323 | 2022-12-23 05:24 | 6.2 | 18.3 | 40.9 | 39.3 | 0.977 | 0
324 | 2022-12-23 05:25 | 6.4 | 18.2 | 40.8 | 38.1 | 1.14 | 0
325 | 2022-12-23 05:26 | 6.2 | 18.2 | 40.7 | 38.1 | 1.559 | 0
326 | 2022-12-23 05:27 | 6.1 | 18.2 | 40.5 | 38.2 | 1.559 | 0
327 | 2022-12-23 05:28 | 6.1 | 18.2 | 40.2 | 38 | 1.568 | 0
328 | 2022-12-23 05:29 | 6.1 | 18.3 | 40.2 | 37.9 | 1.571 | 0
329 | 2022-12-23 05:30 | 6 | 18.3 | 40.1 | 37.8 | 1.567 | 0
330 | 2022-12-23 05:31 | 6 | 18.4 | 40 | 38 | 1.571 | 0
331 | 2022-12-23 05:32 | 5.9 | 18.4 | 39.9 | 38.8 | 1.573 | 0
332 | 2022-12-23 05:33 | 6 | 18.4 | 39.8 | 38.7 | 1.568 | 0
333 | 2022-12-23 05:34 | 6 | 18.4 | 39.7 | 38.5 | 0 | 0
334 | 2022-12-23 05:35 | 6 | 18.4 | 39.4 | 38 | 0 | 0
335 | 2022-12-23 05:36 | 5.8 | 18.4 | 39.1 | 37.4 | 0 | 0
336 | 2022-12-23 05:37 | 5.7 | 18.3 | 38.9 | 36.8 | 0 | 0
337 | 2022-12-23 05:38 | 5.8 | 18.2 | 38.6 | 36.3 | 0 | 0
338 | 2022-12-23 05:39 | 5.8 | 18.3 | 38.3 | 35.8 | 0 | 0
339 | 2022-12-23 05:40 | 5.6 | 18.3 | 38.1 | 35.3 | 0 | 0
340 | 2022-12-23 05:41 | 5.8 | 18.2 | 37.8 | 34.8 | 0 | 0
341 | 2022-12-23 05:42 | 5.6 | 18.2 | 37.5 | 34.3 | 0 | 0
342 | 2022-12-23 05:43 | 5.5 | 18.2 | 37.3 | 33.9 | 0 | 0
343 | 2022-12-23 05:44 | 5.5 | 18.2 | 37 | 33.5 | 0 | 0
344 | 2022-12-23 05:45 | 5.5 | 18.2 | 36.8 | 33.1 | 0 | 0
345 | 2022-12-23 05:46 | 5.5 | 18.1 | 36.5 | 32.7 | 0 | 0
346 | 2022-12-23 05:47 | 5.4 | 18.1 | 36.2 | 32.3 | 0 | 0
347 | 2022-12-23 05:48 | 5.6 | 18.1 | 36 | 31.9 | 0 | 0
348 | 2022-12-23 05:49 | 5.4 | 18.1 | 35.7 | 31.6 | 0 | 0
349 | 2022-12-23 05:50 | 5.4 | 18.1 | 35.5 | 31.2 | 0 | 0
350 | 2022-12-23 05:51 | 5.4 | 18.1 | 35.2 | 30.9 | 0 | 0
351 | 2022-12-23 05:52 | 5.3 | 18 | 35 | 33.8 | 0.072 | 0
352 | 2022-12-23 05:53 | 5.3 | 18 | 34.7 | 33.9 | 0 | 0
353 | 2022-12-23 05:54 | 5.3 | 18.1 | 38.1 | 33.6 | 0.056 | 0
354 | 2022-12-23 05:55 | 5.5 | 18.1 | 38.9 | 35.9 | 0.927 | 0
355 | 2022-12-23 05:56 | 5.6 | 18.1 | 38.4 | 36.3 | 0.93 | 0
356 | 2022-12-23 05:57 | 5.4 | 18.2 | 38.6 | 36.1 | 0.936 | 0
357 | 2022-12-23 05:58 | 5.5 | 18.1 | 38.6 | 36.3 | 0.961 | 0
358 | 2022-12-23 05:59 | 5.5 | 18.2 | 38.5 | 36.2 | 0.97 | 0
359 | 2022-12-23 06:00 | 5.6 | 18.3 | 38.4 | 36.2 | 0.971 | 0
360 | 2022-12-23 06:01 | 5.6 | 18.4 | 38.2 | 36 | 0 | 0
361 | 2022-12-23 06:02 | 5.5 | 18.4 | 38 | 35.5 | 0 | 0
362 | 2022-12-23 06:03 | 5.8 | 18.3 | 37.7 | 34.9 | 0 | 0
363 | 2022-12-23 06:04 | 5.9 | 18.4 | 37.4 | 34.4 | 0 | 0
364 | 2022-12-23 06:05 | 5.6 | 18.2 | 37.1 | 33.9 | 0 | 0
365 | 2022-12-23 06:06 | 6 | 18.1 | 36.9 | 33.4 | 0 | 0
366 | 2022-12-23 06:07 | 5.8 | 18.2 | 36.6 | 33 | 0 | 0
367 | 2022-12-23 06:08 | 5.7 | 18.1 | 36.4 | 32.5 | 0 | 0
368 | 2022-12-23 06:09 | 5.7 | 18.1 | 36.1 | 32.1 | 0 | 0
369 | 2022-12-23 06:10 | 5.8 | 18.2 | 35.9 | 31.8 | 0 | 0
370 | 2022-12-23 06:11 | 5.7 | 18.2 | 35.6 | 31.4 | 0 | 0
371 | 2022-12-23 06:12 | 5.8 | 18.1 | 35.4 | 31 | 0 | 0
372 | 2022-12-23 06:13 | 5.8 | 18.1 | 35.2 | 30.7 | 0 | 0
373 | 2022-12-23 06:14 | 5.8 | 18.1 | 34.9 | 30.4 | 0 | 0
374 | 2022-12-23 06:15 | 5.9 | 18.1 | 34.7 | 32 | 0 | 0
375 | 2022-12-23 06:16 | 6.1 | 18.1 | 34.5 | 32.7 | 0 | 0
376 | 2022-12-23 06:17 | 6.2 | 18.1 | 34.2 | 32.4 | 0 | 0
377 | 2022-12-23 06:18 | 6 | 18 | 40.8 | 29.2 | 0.839 | 0
378 | 2022-12-23 06:19 | 6 | 18 | 40.6 | 38.1 | 1.083 | 0
379 | 2022-12-23 06:20 | 6.3 | 18 | 40.3 | 38.5 | 1.091 | 0
380 | 2022-12-23 06:21 | 6.3 | 18.1 | 40.5 | 37.9 | 1.132 | 0
381 | 2022-12-23 06:22 | 6.2 | 18 | 40.1 | 37.6 | 1.625 | 0
382 | 2022-12-23 06:23 | 6.4 | 18.1 | 40.2 | 37.7 | 1.631 | 0
383 | 2022-12-23 06:24 | 6.4 | 18.1 | 40.1 | 37.7 | 1.633 | 0
384 | 2022-12-23 06:25 | 6.5 | 18.2 | 40.1 | 37.7 | 1.632 | 0
385 | 2022-12-23 06:26 | 6.3 | 18.2 | 40.1 | 37.7 | 1.634 | 0
386 | 2022-12-23 06:27 | 6.4 | 18.4 | 40 | 37.6 | 1.632 | 0
387 | 2022-12-23 06:28 | 6.4 | 18.5 | 39.9 | 38.6 | 1.64 | 0
388 | 2022-12-23 06:29 | 6.4 | 18.5 | 39.8 | 38.6 | 1.631 | 0
389 | 2022-12-23 06:30 | 6.4 | 18.5 | 39.8 | 38.5 | 1.635 | 0
390 | 2022-12-23 06:31 | 6.5 | 18.5 | 39.7 | 38.5 | 1.566 | 0
391 | 2022-12-23 06:32 | 6.6 | 18.5 | 39.7 | 38.1 | 1.094 | 0
392 | 2022-12-23 06:33 | 6.5 | 18.5 | 39.6 | 38 | 1.086 | 0
393 | 2022-12-23 06:34 | 6.4 | 18.4 | 39.6 | 38 | 1.086 | 0
394 | 2022-12-23 06:35 | 6.4 | 18.4 | 39.5 | 37.9 | 1.087 | 0
395 | 2022-12-23 06:36 | 6.5 | 18.4 | 39.3 | 37.8 | 1.087 | 0
396 | 2022-12-23 06:37 | 6.5 | 18.3 | 39.2 | 37.7 | 1.089 | 0
397 | 2022-12-23 06:38 | 6.7 | 18.3 | 39.1 | 37.6 | 1.086 | 0
398 | 2022-12-23 06:39 | 6.7 | 18.3 | 39 | 37.5 | 1.091 | 0
399 | 2022-12-23 06:40 | 6.6 | 18.2 | 38.9 | 37.4 | 1.087 | 0
400 | 2022-12-23 06:41 | 6.8 | 18.3 | 38.8 | 37.3 | 1.081 | 0
401 | 2022-12-23 06:42 | 6.7 | 18.2 | 38.7 | 37.2 | 1.084 | 0
402 | 2022-12-23 06:43 | 6.7 | 18.2 | 38.7 | 36.3 | 1.497 | 0
403 | 2022-12-23 06:44 | 6.8 | 18.2 | 38.5 | 36.6 | 1.505 | 0
404 | 2022-12-23 06:45 | 6.8 | 18.3 | 38.2 | 36.5 | 1.503 | 0
405 | 2022-12-23 06:46 | 6.8 | 18.2 | 38.2 | 36.3 | 1.502 | 0
406 | 2022-12-23 06:47 | 6.8 | 18.2 | 38.1 | 36.3 | 1.5 | 0
407 | 2022-12-23 06:48 | 6.8 | 18.3 | 38 | 36.2 | 1.502 | 0
408 | 2022-12-23 06:49 | 6.8 | 18.3 | 37.9 | 36.1 | 1.502 | 0
409 | 2022-12-23 06:50 | 6.8 | 18.2 | 37.8 | 35.7 | 1.592 | 0
410 | 2022-12-23 06:51 | 6.7 | 18.3 | 37.6 | 35.8 | 1.823 | 0
411 | 2022-12-23 06:52 | 6.9 | 18.3 | 37.4 | 35.7 | 1.823 | 0
412 | 2022-12-23 06:53 | 6.6 | 18.2 | 37.3 | 35.5 | 1.824 | 0
413 | 2022-12-23 06:54 | 6.7 | 18.3 | 37.2 | 35.4 | 1.824 | 0
414 | 2022-12-23 06:55 | 6.6 | 18.3 | 37 | 35.3 | 1.805 | 0
415 | 2022-12-23 06:56 | 6.6 | 18.4 | 36.9 | 35.1 | 1.719 | 0
416 | 2022-12-23 06:57 | 6.6 | 18.4 | 36.8 | 34.9 | 1.565 | 0
417 | 2022-12-23 06:58 | 6.5 | 18.4 | 36.7 | 35.8 | 1.56 | 0
418 | 2022-12-23 06:59 | 6.4 | 18.4 | 37 | 35.8 | 1.56 | 0
419 | 2022-12-23 07:00 | 6.3 | 18.4 | 37.3 | 36 | 1.564 | 0
420 | 2022-12-23 07:01 | 6.3 | 18.3 | 37.3 | 36.2 | 1.457 | 0
421 | 2022-12-23 07:02 | 6.2 | 18.3 | 37.3 | 36 | 0.975 | 0
422 | 2022-12-23 07:03 | 6.1 | 18.3 | 37.2 | 35.9 | 0.971 | 0
423 | 2022-12-23 07:04 | 6.2 | 18.2 | 37.3 | 35.8 | 0.972 | 0
424 | 2022-12-23 07:05 | 6 | 18.2 | 37.5 | 35.9 | 0.968 | 0
425 | 2022-12-23 07:06 | 5.9 | 18.2 | 38 | 36.1 | 0.97 | 0
426 | 2022-12-23 07:07 | 5.8 | 18.2 | 38.4 | 36.6 | 0.973 | 0
427 | 2022-12-23 07:08 | 6 | 18.1 | 38.8 | 37 | 0.974 | 0
428 | 2022-12-23 07:09 | 5.9 | 18.1 | 39.1 | 37.1 | 0.018 | 0
429 | 2022-12-23 07:10 | 5.9 | 18 | 38.9 | 36.9 | 0 | 0
430 | 2022-12-23 07:11 | 5.9 | 18.1 | 38.6 | 36.4 | 0 | 0
431 | 2022-12-23 07:12 | 5.8 | 18.1 | 38.3 | 35.8 | 0 | 0
432 | 2022-12-23 07:13 | 5.8 | 18.1 | 38 | 35.3 | 0 | 0
433 | 2022-12-23 07:14 | 5.6 | 18 | 37.7 | 34.9 | 0 | 0
434 | 2022-12-23 07:15 | 5.5 | 18.1 | 37.5 | 34.4 | 0 | 0
435 | 2022-12-23 07:16 | 5.6 | 18.1 | 37.2 | 34 | 0 | 0
436 | 2022-12-23 07:17 | 5.6 | 18.1 | 36.9 | 35.5 | 0.009 | 0
437 | 2022-12-23 07:18 | 5.4 | 18 | 36.6 | 35.9 | 0.01 | 0
438 | 2022-12-23 07:19 | 5.6 | 18 | 40.1 | 30.1 | 0.7 | 0
439 | 2022-12-23 07:20 | 5.3 | 18.1 | 40 | 37.4 | 0.977 | 0
440 | 2022-12-23 07:21 | 5.3 | 18.1 | 39.5 | 37.3 | 0.975 | 0
441 | 2022-12-23 07:22 | 5.3 | 18.1 | 39.7 | 37.2 | 0.981 | 0
442 | 2022-12-23 07:23 | 5.3 | 18.1 | 39.6 | 37.3 | 0.984 | 0
443 | 2022-12-23 07:24 | 5.4 | 18.3 | 39.5 | 37.3 | 0.977 | 0
444 | 2022-12-23 07:25 | 5.3 | 18.3 | 39.4 | 37.2 | 0 | 0
445 | 2022-12-23 07:26 | 5.2 | 18.4 | 39.2 | 36.9 | 0 | 0
446 | 2022-12-23 07:27 | 5.2 | 18.4 | 38.9 | 36.4 | 0 | 0
447 | 2022-12-23 07:28 | 5.1 | 18.3 | 38.6 | 35.9 | 0 | 0
448 | 2022-12-23 07:29 | 5.1 | 18.3 | 38.4 | 35.3 | 0 | 0
449 | 2022-12-23 07:30 | 5.2 | 18.2 | 38.1 | 34.8 | 0 | 0
450 | 2022-12-23 07:31 | 5.2 | 18.1 | 37.8 | 34.3 | 0 | 0
451 | 2022-12-23 07:32 | 5 | 18.1 | 37.5 | 33.9 | 0 | 0
452 | 2022-12-23 07:33 | 5 | 18.1 | 37.2 | 33.4 | 0 | 0
453 | 2022-12-23 07:34 | 5.1 | 18 | 37 | 33 | 0 | 1
454 | 2022-12-23 07:35 | 5 | 18 | 36.7 | 32.6 | 0 | 1
455 | 2022-12-23 07:36 | 5.2 | 18 | 36.4 | 32.2 | 0 | 2
456 | 2022-12-23 07:37 | 5 | 18 | 36.2 | 31.8 | 0 | 2
457 | 2022-12-23 07:38 | 5.1 | 18 | 35.9 | 31.4 | 0 | 3
458 | 2022-12-23 07:39 | 4.9 | 18 | 35.7 | 31 | 0 | 4
459 | 2022-12-23 07:40 | 4.9 | 18 | 35.4 | 30.7 | 0 | 4
460 | 2022-12-23 07:41 | 4.9 | 18 | 35.2 | 30.3 | 0 | 5
461 | 2022-12-23 07:42 | 5.1 | 18 | 34.9 | 30 | 0 | 6
462 | 2022-12-23 07:43 | 5 | 18 | 34.7 | 32.5 | 0.113 | 6
463 | 2022-12-23 07:44 | 4.8 | 18 | 34.4 | 32.6 | 0 | 7
464 | 2022-12-23 07:45 | 5 | 18 | 38 | 32.4 | 0.503 | 8
465 | 2022-12-23 07:46 | 4.9 | 18 | 38.6 | 35.6 | 0.923 | 8
466 | 2022-12-23 07:47 | 4.8 | 18 | 38 | 36 | 0.955 | 9
467 | 2022-12-23 07:48 | 4.9 | 18 | 37.8 | 32.2 | 1.587 | 10
468 | 2022-12-23 07:49 | 4.8 | 18 | 37.8 | 35.5 | 1.627 | 11
469 | 2022-12-23 07:50 | 5 | 18.1 | 37.7 | 35.6 | 1.632 | 11
470 | 2022-12-23 07:51 | 4.9 | 18.2 | 37.8 | 35.5 | 1.635 | 12
471 | 2022-12-23 07:52 | 5 | 18.3 | 37.9 | 35.6 | 1.625 | 13
472 | 2022-12-23 07:53 | 5 | 18.4 | 37.9 | 36.6 | 1.627 | 13
473 | 2022-12-23 07:54 | 4.9 | 18.4 | 37.9 | 36.7 | 1.629 | 14
474 | 2022-12-23 07:55 | 5 | 18.3 | 38.1 | 36.8 | 1.615 | 15
475 | 2022-12-23 07:56 | 5 | 18.3 | 38 | 36.7 | 1.408 | 15
476 | 2022-12-23 07:57 | 4.9 | 18.3 | 37.9 | 36.5 | 1.088 | 16
477 | 2022-12-23 07:58 | 4.9 | 18.3 | 37.9 | 36.4 | 1.085 | 17
478 | 2022-12-23 07:59 | 5.1 | 18.2 | 37.9 | 36.4 | 1.082 | 17
479 | 2022-12-23 08:00 | 5.1 | 18.2 | 37.7 | 36.3 | 1.087 | 18
480 | 2022-12-23 08:01 | 5.1 | 18.2 | 37.7 | 36.2 | 1.089 | 18
481 | 2022-12-23 08:02 | 5 | 18.2 | 37.6 | 35.3 | 1.616 | 19
482 | 2022-12-23 08:03 | 5 | 18.1 | 37.3 | 35.3 | 1.631 | 19
483 | 2022-12-23 08:04 | 5.1 | 18.2 | 37.2 | 30.8 | 1.959 | 19
484 | 2022-12-23 08:05 | 4.9 | 18.3 | 37.1 | 33.9 | 1.982 | 19
485 | 2022-12-23 08:06 | 4.9 | 18.8 | 37 | 33.9 | 1.983 | 19
486 | 2022-12-23 08:07 | 4.9 | 19.1 | 37.7 | 34 | 1.993 | 19
487 | 2022-12-23 08:08 | 4.9 | 19.4 | 37.8 | 34.5 | 1.987 | 20
488 | 2022-12-23 08:09 | 4.9 | 19.7 | 37.9 | 34.6 | 1.991 | 21
489 | 2022-12-23 08:10 | 5.1 | 19.8 | 38.2 | 34.8 | 1.993 | 21
490 | 2022-12-23 08:11 | 5.1 | 20 | 38.4 | 35 | 1.987 | 22
491 | 2022-12-23 08:12 | 4.9 | 20.1 | 38.7 | 35.2 | 1.987 | 22
492 | 2022-12-23 08:13 | 4.9 | 20.1 | 38.9 | 35.4 | 1.986 | 23
493 | 2022-12-23 08:14 | 5.1 | 20.2 | 39.1 | 35.6 | 1.982 | 24
494 | 2022-12-23 08:15 | 4.9 | 20.4 | 39.3 | 35.7 | 1.985 | 25
495 | 2022-12-23 08:16 | 5 | 20.5 | 39.5 | 36 | 1.991 | 26
496 | 2022-12-23 08:17 | 5 | 20.6 | 39.7 | 36.1 | 1.99 | 26
497 | 2022-12-23 08:18 | 5.2 | 20.6 | 39.9 | 36.3 | 1.989 | 27
498 | 2022-12-23 08:19 | 5.1 | 20.6 | 40.1 | 36.5 | 1.984 | 27
499 | 2022-12-23 08:20 | 5.1 | 20.6 | 40 | 36.6 | 1.992 | 28
500 | 2022-12-23 08:21 | 4.9 | 20.8 | 39.7 | 36.5 | 1.989 | 28
501 | 2022-12-23 08:22 | 5.2 | 20.6 | 39.5 | 36.3 | 1.988 | 28
502 | 2022-12-23 08:23 | 5 | 20.8 | 39.6 | 36.1 | 1.987 | 29
503 | 2022-12-23 08:24 | 4.9 | 20.9 | 39.8 | 36.2 | 1.979 | 30
504 | 2022-12-23 08:25 | 5.1 | 20.8 | 40.3 | 36.4 | 1.985 | 31
505 | 2022-12-23 08:26 | 5 | 21 | 40.3 | 36.8 | 1.986 | 31
506 | 2022-12-23 08:27 | 5.1 | 21 | 40.6 | 36.8 | 1.99 | 31
507 | 2022-12-23 08:28 | 5.1 | 21 | 40.8 | 37 | 1.992 | 32
508 | 2022-12-23 08:29 | 5.1 | 21 | 41 | 37.2 | 1.994 | 32
509 | 2022-12-23 08:30 | 5 | 21 | 41.2 | 37.4 | 1.99 | 32
510 | 2022-12-23 08:31 | 5.2 | 21.1 | 41.3 | 37.6 | 1.99 | 32
511 | 2022-12-23 08:32 | 5.1 | 21.1 | 41.5 | 37.7 | 1.987 | 33
512 | 2022-12-23 08:33 | 5 | 21.1 | 41.7 | 38.1 | 1.991 | 33
513 | 2022-12-23 08:34 | 5 | 21.2 | 41.9 | 38.9 | 1.988 | 33
514 | 2022-12-23 08:35 | 5.2 | 21.2 | 42.2 | 39.1 | 1.995 | 33
515 | 2022-12-23 08:36 | 5.1 | 21.1 | 42.5 | 39.4 | 1.99 | 34
516 | 2022-12-23 08:37 | 5.3 | 21.1 | 42.8 | 39.5 | 1.982 | 35
517 | 2022-12-23 08:38 | 5.2 | 21 | 42.9 | 39.6 | 1.819 | 36
518 | 2022-12-23 08:39 | 5.2 | 20.9 | 43.1 | 39.8 | 1.822 | 38
519 | 2022-12-23 08:40 | 5.2 | 21 | 43.2 | 40 | 1.824 | 39
520 | 2022-12-23 08:41 | 5.3 | 21 | 43.5 | 40.1 | 1.827 | 40
521 | 2022-12-23 08:42 | 5.2 | 20.9 | 43.7 | 40.3 | 1.832 | 41
522 | 2022-12-23 08:43 | 5.4 | 21 | 43.9 | 40.5 | 1.822 | 42
523 | 2022-12-23 08:44 | 5.3 | 21 | 44 | 40.7 | 1.826 | 43
524 | 2022-12-23 08:45 | 5.4 | 21 | 44.3 | 39.7 | 1.962 | 44
525 | 2022-12-23 08:46 | 5.3 | 21.1 | 44.4 | 40.2 | 1.99 | 45
526 | 2022-12-23 08:47 | 5.4 | 21.1 | 44.4 | 40.3 | 1.991 | 45
527 | 2022-12-23 08:48 | 5.3 | 21.1 | 44.7 | 40.3 | 1.995 | 47
528 | 2022-12-23 08:49 | 5.5 | 21.3 | 44.6 | 40.5 | 1.991 | 48
529 | 2022-12-23 08:50 | 5.3 | 21.3 | 44.7 | 40.4 | 1.989 | 49
530 | 2022-12-23 08:51 | 5.5 | 21.4 | 44.6 | 40.5 | 1.995 | 49
531 | 2022-12-23 08:52 | 5.4 | 21.6 | 44.5 | 40.5 | 1.993 | 50
532 | 2022-12-23 08:53 | 5.6 | 21.6 | 44.2 | 40.4 | 1.992 | 50
533 | 2022-12-23 08:54 | 5.4 | 21.7 | 44.3 | 41.1 | 1.995 | 51
534 | 2022-12-23 08:55 | 5.5 | 21.7 | 44.6 | 41.3 | 1.997 | 52
535 | 2022-12-23 08:56 | 5.7 | 21.7 | 45 | 41.6 | 1.991 | 53
536 | 2022-12-23 08:57 | 5.7 | 21.6 | 45.1 | 41.8 | 1.989 | 53
537 | 2022-12-23 08:58 | 5.7 | 21.5 | 45.2 | 41.5 | 1.839 | 54
538 | 2022-12-23 08:59 | 5.7 | 21.5 | 45.4 | 41.9 | 1.829 | 54
539 | 2022-12-23 09:00 | 5.5 | 21.4 | 45.5 | 42 | 1.819 | 55
540 | 2022-12-23 09:01 | 5.6 | 21.5 | 45.7 | 42.2 | 1.829 | 55
541 | 2022-12-23 09:02 | 5.7 | 21.4 | 45.9 | 42.3 | 1.825 | 56
542 | 2022-12-23 09:03 | 5.5 | 21.3 | 46.1 | 42.5 | 1.822 | 56
543 | 2022-12-23 09:04 | 5.6 | 21.5 | 46.3 | 42.6 | 1.831 | 57
544 | 2022-12-23 09:05 | 5.8 | 21.4 | 46.3 | 42.7 | 1.826 | 57
545 | 2022-12-23 09:06 | 5.7 | 21.4 | 46.5 | 42.8 | 1.827 | 57
546 | 2022-12-23 09:07 | 5.8 | 21.5 | 46.4 | 43 | 1.829 | 57
547 | 2022-12-23 09:08 | 5.9 | 21.6 | 46.3 | 42.9 | 1.826 | 57
548 | 2022-12-23 09:09 | 6 | 21.5 | 46 | 41.3 | 1.986 | 57
549 | 2022-12-23 09:10 | 6 | 21.6 | 45.7 | 41.6 | 1.997 | 57
550 | 2022-12-23 09:11 | 6 | 21.6 | 45.1 | 41.4 | 1.994 | 58
551 | 2022-12-23 09:12 | 6 | 21.8 | 44.9 | 40.9 | 1.994 | 58
552 | 2022-12-23 09:13 | 5.8 | 21.9 | 44.6 | 40.7 | 1.991 | 59
553 | 2022-12-23 09:14 | 5.9 | 21.9 | 44.2 | 40.5 | 1.99 | 60
554 | 2022-12-23 09:15 | 5.8 | 21.9 | 43.9 | 40.3 | 1.992 | 60
555 | 2022-12-23 09:16 | 5.8 | 21.9 | 43.6 | 40.9 | 1.984 | 61
556 | 2022-12-23 09:17 | 6 | 22 | 43.4 | 40.6 | 1.996 | 62
557 | 2022-12-23 09:18 | 6 | 22 | 43.1 | 40.5 | 1.992 | 63
558 | 2022-12-23 09:19 | 5.9 | 21.9 | 42.9 | 40.1 | 1.955 | 64
559 | 2022-12-23 09:20 | 6 | 21.8 | 42.7 | 39.8 | 1.825 | 65
560 | 2022-12-23 09:21 | 5.9 | 21.7 | 42.5 | 39.7 | 1.817 | 65
561 | 2022-12-23 09:22 | 6 | 21.7 | 42.3 | 39.4 | 1.825 | 66
562 | 2022-12-23 09:23 | 6.1 | 21.6 | 42.1 | 39.3 | 1.822 | 66
563 | 2022-12-23 09:24 | 6 | 21.7 | 41.9 | 39.1 | 1.821 | 66
564 | 2022-12-23 09:25 | 6.2 | 21.7 | 41.7 | 38.9 | 1.824 | 67
565 | 2022-12-23 09:26 | 6.2 | 21.6 | 41.5 | 38.7 | 1.822 | 69
566 | 2022-12-23 09:27 | 6 | 21.6 | 41.2 | 38.5 | 1.819 | 72
567 | 2022-12-23 09:28 | 6 | 21.6 | 41 | 38.2 | 1.817 | 75
568 | 2022-12-23 09:29 | 6.1 | 21.6 | 40.8 | 38.1 | 1.82 | 84
569 | 2022-12-23 09:30 | 6.3 | 21.6 | 40.6 | 38 | 1.819 | 162
570 | 2022-12-23 09:31 | 6.4 | 21.6 | 40.3 | 37.8 | 1.811 | 308
571 | 2022-12-23 09:32 | 6.4 | 21.5 | 40.2 | 37.6 | 1.82 | 405
572 | 2022-12-23 09:33 | 6.6 | 21.5 | 40.1 | 37.3 | 1.913 | 439
573 | 2022-12-23 09:34 | 6.8 | 21.6 | 39.9 | 36.6 | 1.978 | 487
574 | 2022-12-23 09:35 | 7.2 | 21.6 | 40 | 36.5 | 1.986 | 497
575 | 2022-12-23 09:36 | 7.3 | 21.5 | 40.3 | 36.7 | 1.984 | 494
576 | 2022-12-23 09:37 | 7.6 | 21.6 | 40.4 | 36.9 | 1.987 | 528
577 | 2022-12-23 09:38 | 7.9 | 21.6 | 40.6 | 37 | 1.984 | 545
578 | 2022-12-23 09:39 | 7.9 | 21.7 | 40.8 | 37.2 | 1.986 | 550
579 | 2022-12-23 09:40 | 7.8 | 21.8 | 41.1 | 37.4 | 1.989 | 554
580 | 2022-12-23 09:41 | 8 | 21.8 | 41.2 | 37.6 | 1.991 | 558
581 | 2022-12-23 09:42 | 8.2 | 21.8 | 41.5 | 37.7 | 1.982 | 567
582 | 2022-12-23 09:43 | 8.6 | 21.9 | 41.7 | 38.8 | 1.984 | 531
583 | 2022-12-23 09:44 | 8.7 | 21.9 | 41.9 | 39 | 1.989 | 480
584 | 2022-12-23 09:45 | 8.2 | 21.7 | 42.3 | 40.1 | 1.992 | 499
585 | 2022-12-23 09:46 | 8.1 | 21.3 | 42.6 | 40.5 | 1.981 | 480
586 | 2022-12-23 09:47 | 8 | 21 | 43 | 40.6 | 1.821 | 466
587 | 2022-12-23 09:48 | 8.3 | 20.6 | 43.4 | 41.1 | 1.793 | 379
588 | 2022-12-23 09:49 | 8.6 | 20.4 | 43.6 | 41.1 | 1.579 | 426
589 | 2022-12-23 09:50 | 8.6 | 20.4 | 43.8 | 41.3 | 1.505 | 488
590 | 2022-12-23 09:51 | 8.9 | 20.3 | 43.6 | 41.4 | 1.505 | 520
591 | 2022-12-23 09:52 | 9.3 | 20.2 | 43.5 | 41.3 | 1.501 | 516
592 | 2022-12-23 09:53 | 9.3 | 20.2 | 43.8 | 39.3 | 1.815 | 589
593 | 2022-12-23 09:54 | 9.4 | 20.4 | 43.9 | 40.7 | 1.829 | 540
594 | 2022-12-23 09:55 | 9.3 | 20.6 | 44.1 | 40.8 | 1.826 | 496
595 | 2022-12-23 09:56 | 9.4 | 21 | 44.2 | 40.7 | 1.92 | 567
596 | 2022-12-23 09:57 | 9.3 | 21.2 | 44.5 | 40.1 | 1.997 | 585
597 | 2022-12-23 09:58 | 9.7 | 21.4 | 44.5 | 40.5 | 1.993 | 607
598 | 2022-12-23 09:59 | 9.9 | 21.5 | 44.6 | 40.5 | 1.985 | 604
599 | 2022-12-23 10:00 | 9.7 | 21.7 | 44.8 | 40.6 | 1.991 | 425
600 | 2022-12-23 10:01 | 9.5 | 21.9 | 45 | 40.7 | 1.99 | 425
601 | 2022-12-23 10:02 | 9.8 | 22 | 45 | 40.9 | 1.994 | 453
602 | 2022-12-23 10:03 | 9.8 | 22 | 45.2 | 41.9 | 1.996 | 400
603 | 2022-12-23 10:04 | 10 | 22.3 | 45.5 | 42.1 | 1.991 | 531
604 | 2022-12-23 10:05 | 9.8 | 22.2 | 45.8 | 43 | 1.993 | 559
605 | 2022-12-23 10:06 | 10.1 | 21.9 | 46 | 43.7 | 1.989 | 601
606 | 2022-12-23 10:07 | 10 | 21.4 | 46.4 | 43.8 | 1.832 | 553
607 | 2022-12-23 10:08 | 10.6 | 21 | 46.6 | 44.2 | 1.833 | 481
608 | 2022-12-23 10:09 | 10.7 | 20.9 | 46.9 | 44.4 | 1.784 | 448
609 | 2022-12-23 10:10 | 10.9 | 20.7 | 47 | 44.3 | 1.506 | 473
610 | 2022-12-23 10:11 | 11 | 20.5 | 47.3 | 44.5 | 1.512 | 554
611 | 2022-12-23 10:12 | 11.3 | 20.4 | 47.5 | 44.7 | 1.51 | 532
612 | 2022-12-23 10:13 | 11.2 | 20.4 | 47.8 | 45 | 1.511 | 532
613 | 2022-12-23 10:14 | 11.4 | 20.4 | 48.4 | 45.2 | 1.513 | 483
614 | 2022-12-23 10:15 | 11.6 | 20.3 | 47.9 | 45.7 | 1.513 | 514
615 | 2022-12-23 10:16 | 11.9 | 20.4 | 47.7 | 42.1 | 1.786 | 540
616 | 2022-12-23 10:17 | 11.7 | 20.6 | 47.7 | 44.1 | 1.832 | 516
617 | 2022-12-23 10:18 | 11.7 | 20.9 | 47.6 | 44.1 | 1.834 | 452
618 | 2022-12-23 10:19 | 12 | 21.2 | 47.8 | 42.4 | 1.965 | 481
619 | 2022-12-23 10:20 | 12.1 | 21.4 | 48 | 43.2 | 2.001 | 536
620 | 2022-12-23 10:21 | 11.8 | 21.6 | 47.8 | 43.7 | 2.001 | 588
621 | 2022-12-23 10:22 | 11.8 | 21.8 | 47.7 | 43.9 | 1.998 | 647
622 | 2022-12-23 10:23 | 12 | 22.1 | 47.6 | 44 | 1.995 | 633
623 | 2022-12-23 10:24 | 12.1 | 22.4 | 47.3 | 44.2 | 2.001 | 513
624 | 2022-12-23 10:25 | 11.8 | 22.4 | 47.2 | 45.4 | 1.99 | 432
625 | 2022-12-23 10:26 | 12 | 22.2 | 47.4 | 45.7 | 1.89 | 517
626 | 2022-12-23 10:27 | 12.6 | 21.8 | 47.8 | 46 | 1.895 | 535
627 | 2022-12-23 10:28 | 13.1 | 21.4 | 47.7 | 46.1 | 1.779 | 547
628 | 2022-12-23 10:29 | 12.6 | 21.2 | 47.6 | 46 | 1.557 | 591
629 | 2022-12-23 10:30 | 12.9 | 21 | 47.5 | 45.5 | 1.184 | 462
630 | 2022-12-23 10:31 | 13.2 | 20.8 | 47.5 | 44.8 | 1.506 | 467
631 | 2022-12-23 10:32 | 12.8 | 20.6 | 47.4 | 44.9 | 1.51 | 415
632 | 2022-12-23 10:33 | 12.6 | 20.6 | 47 | 44.7 | 1.51 | 490
633 | 2022-12-23 10:34 | 12.8 | 20.5 | 46.8 | 44.4 | 1.51 | 568
634 | 2022-12-23 10:35 | 12.9 | 20.4 | 46.7 | 44.3 | 1.51 | 566
635 | 2022-12-23 10:36 | 12.8 | 20.3 | 46.5 | 44.2 | 1.508 | 508
636 | 2022-12-23 10:37 | 12.9 | 20.3 | 46.4 | 44 | 1.513 | 498
637 | 2022-12-23 10:38 | 13.2 | 20.4 | 46.1 | 43.8 | 1.509 | 447
638 | 2022-12-23 10:39 | 13 | 20.5 | 46 | 41.2 | 1.817 | 444
639 | 2022-12-23 10:40 | 13 | 20.6 | 45.8 | 42.6 | 1.829 | 473
640 | 2022-12-23 10:41 | 12.9 | 20.9 | 45.5 | 42.4 | 1.828 | 499
641 | 2022-12-23 10:42 | 13 | 21.3 | 45.3 | 42.1 | 1.831 | 436
642 | 2022-12-23 10:43 | 13 | 21.4 | 45 | 42 | 1.825 | 503
643 | 2022-12-23 10:44 | 13.1 | 21.7 | 44.8 | 41.7 | 1.829 | 498
644 | 2022-12-23 10:45 | 13.2 | 21.8 | 44.5 | 41.5 | 1.824 | 573
645 | 2022-12-23 10:46 | 13.4 | 21.9 | 44.3 | 41.3 | 1.825 | 667
646 | 2022-12-23 10:47 | 13.9 | 22 | 44.1 | 41.1 | 1.826 | 628
647 | 2022-12-23 10:48 | 14 | 22 | 43.8 | 40.9 | 1.829 | 685
648 | 2022-12-23 10:49 | 14.5 | 22.1 | 43.6 | 40.7 | 1.821 | 684
649 | 2022-12-23 10:50 | 14.1 | 22.1 | 43.3 | 40.5 | 1.829 | 681
650 | 2022-12-23 10:51 | 13.9 | 22.2 | 43.1 | 41.1 | 1.828 | 686
651 | 2022-12-23 10:52 | 14.5 | 21.8 | 42.9 | 41.1 | 1.826 | 686
652 | 2022-12-23 10:53 | 14.4 | 21.4 | 42.8 | 40.9 | 1.824 | 706
653 | 2022-12-23 10:54 | 14.3 | 21.1 | 42.7 | 40.9 | 1.822 | 723
654 | 2022-12-23 10:55 | 14.4 | 20.9 | 42.5 | 40.7 | 1.773 | 721
655 | 2022-12-23 10:56 | 13.8 | 20.7 | 42.5 | 40.4 | 1.501 | 705
656 | 2022-12-23 10:57 | 14 | 20.6 | 42.3 | 40.3 | 1.506 | 705
657 | 2022-12-23 10:58 | 14.2 | 20.5 | 42.2 | 40.1 | 1.516 | 696
658 | 2022-12-23 10:59 | 13.5 | 20.5 | 42 | 39.1 | 1.823 | 761
659 | 2022-12-23 11:00 | 13.8 | 20.4 | 41.9 | 39.1 | 1.828 | 761
660 | 2022-12-23 11:01 | 13.7 | 20.4 | 41.4 | 39 | 1.821 | 756
661 | 2022-12-23 11:02 | 14.1 | 20.5 | 41.2 | 38.6 | 1.832 | 752
662 | 2022-12-23 11:03 | 14 | 20.6 | 41.1 | 38.5 | 1.826 | 749
663 | 2022-12-23 11:04 | 14.3 | 20.8 | 40.8 | 38.3 | 1.833 | 734
664 | 2022-12-23 11:05 | 14.5 | 21 | 40.7 | 36.4 | 1.981 | 760
665 | 2022-12-23 11:06 | 14.4 | 21.1 | 40.5 | 37.3 | 1.982 | 758
666 | 2022-12-23 11:07 | 14.5 | 21.4 | 40.1 | 37.9 | 1.988 | 675
667 | 2022-12-23 11:08 | 14 | 21.5 | 39.9 | 37.6 | 1.989 | 158
668 | 2022-12-23 11:09 | 13.6 | 21.7 | 39.7 | 37.5 | 1.987 | 173
669 | 2022-12-23 11:10 | 13.1 | 21.8 | 39.6 | 37.2 | 1.952 | 177
670 | 2022-12-23 11:11 | 13.6 | 21.8 | 39.4 | 37 | 1.82 | 671
671 | 2022-12-23 11:12 | 13.8 | 21.8 | 39.3 | 36.9 | 1.816 | 237
672 | 2022-12-23 11:13 | 13.3 | 21.9 | 39 | 36.7 | 1.82 | 196
673 | 2022-12-23 11:14 | 13.9 | 21.9 | 38.8 | 36.5 | 1.818 | 820
674 | 2022-12-23 11:15 | 13.9 | 21.9 | 38.6 | 36.4 | 1.814 | 745
675 | 2022-12-23 11:16 | 13.9 | 21.8 | 38.4 | 37 | 1.82 | 553
676 | 2022-12-23 11:17 | 13.5 | 21.4 | 38.4 | 36.9 | 1.815 | 160
677 | 2022-12-23 11:18 | 13.7 | 21.1 | 38.3 | 36.9 | 1.816 | 513
678 | 2022-12-23 11:19 | 13.5 | 20.9 | 38.3 | 36.8 | 1.794 | 488
679 | 2022-12-23 11:20 | 13.8 | 20.7 | 38.2 | 36.4 | 1.525 | 719
680 | 2022-12-23 11:21 | 14.3 | 20.6 | 38 | 36.4 | 1.498 | 778
681 | 2022-12-23 11:22 | 13.8 | 20.5 | 38 | 36.3 | 1.5 | 640
682 | 2022-12-23 11:23 | 13.9 | 20.4 | 37.8 | 36.2 | 1.491 | 609
683 | 2022-12-23 11:24 | 13.9 | 20.4 | 37.7 | 36.1 | 1.497 | 566
684 | 2022-12-23 11:25 | 13.6 | 20.3 | 37.6 | 36 | 1.494 | 518
685 | 2022-12-23 11:26 | 13.6 | 20.3 | 37.5 | 35.9 | 1.5 | 382
686 | 2022-12-23 11:27 | 13.7 | 20.2 | 37.4 | 35.8 | 1.493 | 449
687 | 2022-12-23 11:28 | 13.2 | 20.4 | 37.3 | 35.4 | 1.73 | 508
688 | 2022-12-23 11:29 | 12.7 | 20.5 | 37.2 | 35 | 1.816 | 523
689 | 2022-12-23 11:30 | 12.7 | 20.6 | 37 | 34.9 | 1.81 | 773
690 | 2022-12-23 11:31 | 12.9 | 20.9 | 36.9 | 34.7 | 1.812 | 730
691 | 2022-12-23 11:32 | 13.5 | 21.1 | 37.1 | 34.7 | 1.809 | 767
692 | 2022-12-23 11:33 | 13.7 | 21.3 | 37.5 | 34.9 | 1.81 | 794
693 | 2022-12-23 11:34 | 13.9 | 21.3 | 37.9 | 35.3 | 1.814 | 743
694 | 2022-12-23 11:35 | 14.4 | 21.5 | 38.1 | 35.6 | 1.817 | 754
695 | 2022-12-23 11:36 | 14.3 | 21.5 | 38.4 | 35.8 | 1.815 | 733
696 | 2022-12-23 11:37 | 14.2 | 21.5 | 38.7 | 36.1 | 1.82 | 481
697 | 2022-12-23 11:38 | 14.1 | 21.7 | 39.1 | 36.3 | 1.818 | 798
698 | 2022-12-23 11:39 | 14.4 | 21.7 | 39.4 | 36.6 | 1.818 | 749
699 | 2022-12-23 11:40 | 14.6 | 21.8 | 39.7 | 36.9 | 1.818 | 704
700 | 2022-12-23 11:41 | 14.6 | 21.8 | 40 | 37.2 | 1.819 | 635
701 | 2022-12-23 11:42 | 14.6 | 21.9 | 40.3 | 37.4 | 1.82 | 632
702 | 2022-12-23 11:43 | 14.4 | 21.9 | 40.5 | 37.7 | 1.822 | 660
703 | 2022-12-23 11:44 | 14.4 | 21.9 | 40.9 | 38.1 | 1.824 | 660
704 | 2022-12-23 11:45 | 13.6 | 21.7 | 41.2 | 39.2 | 1.819 | 652
705 | 2022-12-23 11:46 | 13.7 | 21.3 | 41.5 | 39.5 | 1.826 | 621
706 | 2022-12-23 11:47 | 14 | 21.1 | 42 | 39.8 | 1.819 | 694
707 | 2022-12-23 11:48 | 13.9 | 20.9 | 42.4 | 40.2 | 1.773 | 652
708 | 2022-12-23 11:49 | 13.9 | 20.8 | 42.6 | 40.3 | 1.499 | 572
709 | 2022-12-23 11:50 | 13.9 | 20.6 | 43 | 40.6 | 1.503 | 545
710 | 2022-12-23 11:51 | 14.3 | 20.5 | 43.1 | 40.8 | 1.498 | 526
711 | 2022-12-23 11:52 | 14.2 | 20.5 | 43.1 | 40.9 | 1.505 | 602
712 | 2022-12-23 11:53 | 14.3 | 20.4 | 43 | 39.2 | 1.827 | 693
713 | 2022-12-23 11:54 | 14.3 | 20.4 | 42.7 | 40.5 | 1.831 | 773
714 | 2022-12-23 11:55 | 14.4 | 20.4 | 42.2 | 40.3 | 1.831 | 739
715 | 2022-12-23 11:56 | 14.4 | 20.5 | 42.2 | 40 | 1.831 | 782
716 | 2022-12-23 11:57 | 14.8 | 20.6 | 42.1 | 39.9 | 1.828 | 723
717 | 2022-12-23 11:58 | 15 | 20.8 | 41.9 | 39.7 | 1.677 | 670
718 | 2022-12-23 11:59 | 14.9 | 21.1 | 41.7 | 37.6 | 1.865 | 652
719 | 2022-12-23 12:00 | 14.6 | 21.2 | 41.5 | 39.4 | 1.877 | 642
720 | 2022-12-23 12:01 | 14.5 | 21.3 | 41.2 | 39.4 | 1.88 | 628
721 | 2022-12-23 12:02 | 14.4 | 21.6 | 41.1 | 39 | 1.879 | 648
722 | 2022-12-23 12:03 | 13.6 | 21.8 | 41 | 38.9 | 1.845 | 636
723 | 2022-12-23 12:04 | 13.6 | 21.9 | 40.8 | 38.6 | 1.614 | 609
724 | 2022-12-23 12:05 | 13.6 | 22 | 40.7 | 38.4 | 1.615 | 591
725 | 2022-12-23 12:06 | 13.7 | 22 | 40.5 | 37 | 1.808 | 534
726 | 2022-12-23 12:07 | 13.5 | 22 | 40.3 | 38.6 | 1.826 | 592
727 | 2022-12-23 12:08 | 13.7 | 21.7 | 40.1 | 38.6 | 1.815 | 612
728 | 2022-12-23 12:09 | 13.6 | 21.4 | 40 | 38.4 | 1.828 | 618
729 | 2022-12-23 12:10 | 14.1 | 21.1 | 40 | 38.4 | 1.814 | 605
730 | 2022-12-23 12:11 | 14.7 | 20.9 | 39.9 | 38.2 | 1.662 | 707
731 | 2022-12-23 12:12 | 14.6 | 20.8 | 39.8 | 38 | 1.499 | 329
732 | 2022-12-23 12:13 | 14.2 | 20.7 | 39.6 | 37.9 | 1.493 | 739
733 | 2022-12-23 12:14 | 14.2 | 20.6 | 39.5 | 37.8 | 1.498 | 459
734 | 2022-12-23 12:15 | 13.7 | 20.5 | 39.4 | 37.7 | 1.503 | 233
735 | 2022-12-23 12:16 | 13.6 | 20.5 | 39.3 | 37.6 | 1.493 | 777
736 | 2022-12-23 12:17 | 13.9 | 20.4 | 39.2 | 37.5 | 1.495 | 797
737 | 2022-12-23 12:18 | 14 | 20.4 | 39.1 | 37.4 | 1.494 | 681
738 | 2022-12-23 12:19 | 14 | 20.4 | 39 | 37.3 | 1.498 | 714
739 | 2022-12-23 12:20 | 14.2 | 20.4 | 38.9 | 37.2 | 1.502 | 202
740 | 2022-12-23 12:21 | 13.8 | 20.5 | 38.8 | 37.1 | 1.496 | 238
741 | 2022-12-23 12:22 | 13.6 | 20.6 | 38.6 | 35 | 1.798 | 255
742 | 2022-12-23 12:23 | 13.7 | 20.6 | 38.4 | 36.1 | 1.811 | 192
743 | 2022-12-23 12:24 | 13.5 | 20.7 | 38.1 | 36 | 1.811 | 211
744 | 2022-12-23 12:25 | 13.6 | 21 | 38 | 35.7 | 1.815 | 704
745 | 2022-12-23 12:26 | 13.9 | 21.2 | 37.8 | 35.6 | 1.812 | 682
746 | 2022-12-23 12:27 | 13.9 | 21.4 | 37.7 | 35.5 | 1.816 | 432
747 | 2022-12-23 12:28 | 14 | 21.5 | 37.6 | 35.4 | 1.81 | 548
748 | 2022-12-23 12:29 | 14.1 | 21.6 | 37.4 | 35.2 | 1.816 | 548
749 | 2022-12-23 12:30 | 13.9 | 21.6 | 37.2 | 35.5 | 1.809 | 695
750 | 2022-12-23 12:31 | 14.4 | 21.7 | 37.1 | 35.4 | 1.82 | 762
751 | 2022-12-23 12:32 | 14.3 | 21.7 | 37 | 35.3 | 1.809 | 776
752 | 2022-12-23 12:33 | 14.4 | 21.8 | 36.9 | 35.2 | 1.809 | 791
753 | 2022-12-23 12:34 | 14.8 | 21.9 | 37 | 35.1 | 1.714 | 793
754 | 2022-12-23 12:35 | 14.6 | 21.8 | 37.6 | 35.2 | 1.607 | 177
755 | 2022-12-23 12:36 | 14.8 | 21.8 | 37.9 | 36.4 | 1.607 | 849
756 | 2022-12-23 12:37 | 15 | 21.5 | 38.2 | 36.9 | 1.612 | 839
757 | 2022-12-23 12:38 | 15.1 | 21.2 | 38.6 | 37.2 | 1.616 | 838
758 | 2022-12-23 12:39 | 14.7 | 21 | 39.2 | 37.6 | 1.603 | 884
759 | 2022-12-23 12:40 | 14.8 | 20.8 | 39.5 | 37.9 | 1.443 | 837
760 | 2022-12-23 12:41 | 14.8 | 20.6 | 39.8 | 38 | 1.091 | 172
761 | 2022-12-23 12:42 | 14.5 | 20.5 | 40.2 | 37.4 | 1.484 | 161
762 | 2022-12-23 12:43 | 13.6 | 20.5 | 40.4 | 38.3 | 1.495 | 612
763 | 2022-12-23 12:44 | 13.7 | 20.4 | 40.5 | 38.5 | 1.5 | 817
764 | 2022-12-23 12:45 | 14 | 20.4 | 40.4 | 38.6 | 1.498 | 856
765 | 2022-12-23 12:46 | 14.1 | 20.4 | 40.3 | 38.5 | 1.506 | 811
766 | 2022-12-23 12:47 | 14.4 | 20.3 | 40.3 | 38.4 | 1.504 | 849
767 | 2022-12-23 12:48 | 14.9 | 20.4 | 40.2 | 35.1 | 1.769 | 830
768 | 2022-12-23 12:49 | 14.9 | 20.5 | 40 | 37.5 | 1.827 | 802
769 | 2022-12-23 12:50 | 14.8 | 20.6 | 39.6 | 35.4 | 1.981 | 788
770 | 2022-12-23 12:51 | 14.5 | 20.7 | 39.3 | 36.3 | 1.982 | 795
771 | 2022-12-23 12:52 | 14.3 | 21 | 39.1 | 36.2 | 1.987 | 844
772 | 2022-12-23 12:53 | 14.4 | 21.2 | 38.8 | 36 | 1.98 | 837
773 | 2022-12-23 12:54 | 14.9 | 21.4 | 38.6 | 35.8 | 1.975 | 865
774 | 2022-12-23 12:55 | 15.5 | 21.7 | 38.4 | 35.6 | 1.975 | 820
775 | 2022-12-23 12:56 | 15.7 | 21.8 | 38.2 | 36.2 | 1.986 | 798
776 | 2022-12-23 12:57 | 15.1 | 21.9 | 38 | 36 | 1.981 | 322
777 | 2022-12-23 12:58 | 15.2 | 22 | 37.9 | 35.9 | 1.983 | 758
778 | 2022-12-23 12:59 | 15.2 | 22 | 37.8 | 35.9 | 1.949 | 788
779 | 2022-12-23 13:00 | 15.5 | 21.8 | 37.6 | 36.3 | 1.818 | 797
780 | 2022-12-23 13:01 | 15.7 | 21.4 | 37.5 | 36.2 | 1.812 | 801
781 | 2022-12-23 13:02 | 15.2 | 21.1 | 37.5 | 36.1 | 1.807 | 807
782 | 2022-12-23 13:03 | 15.2 | 20.9 | 37.4 | 36 | 1.723 | 787
783 | 2022-12-23 13:04 | 15.3 | 20.8 | 37.4 | 35.8 | 1.494 | 759
784 | 2022-12-23 13:05 | 15.5 | 20.7 | 37.7 | 35.9 | 1.495 | 772
785 | 2022-12-23 13:06 | 15.5 | 20.6 | 38.1 | 36.1 | 1.493 | 767
786 | 2022-12-23 13:07 | 14.7 | 20.5 | 38.5 | 37.1 | 1.501 | 788
787 | 2022-12-23 13:08 | 14.5 | 20.5 | 38.6 | 37.4 | 1.497 | 788
788 | 2022-12-23 13:09 | 14.8 | 20.5 | 38.8 | 37.5 | 1.496 | 799
789 | 2022-12-23 13:10 | 14.9 | 20.4 | 38.8 | 37.7 | 1.46 | 276
790 | 2022-12-23 13:11 | 14.4 | 20.4 | 38.7 | 37.4 | 1.084 | 560
791 | 2022-12-23 13:12 | 14.5 | 20.4 | 38.7 | 37.3 | 1.087 | 473
792 | 2022-12-23 13:13 | 14.4 | 20.4 | 38.7 | 37.3 | 1.088 | 396
793 | 2022-12-23 13:14 | 14.4 | 20.5 | 38.6 | 37.2 | 1.081 | 699
794 | 2022-12-23 13:15 | 14.7 | 20.5 | 38.5 | 34.6 | 1.568 | 726
795 | 2022-12-23 13:16 | 14.4 | 20.6 | 38.4 | 36.4 | 1.612 | 149
796 | 2022-12-23 13:17 | 14.7 | 20.8 | 38.2 | 36.3 | 1.612 | 131
797 | 2022-12-23 13:18 | 14.3 | 21 | 38 | 36.1 | 1.61 | 125
798 | 2022-12-23 13:19 | 14.1 | 21.2 | 37.9 | 35.2 | 1.806 | 118
799 | 2022-12-23 13:20 | 13.8 | 21.3 | 37.8 | 35.5 | 1.809 | 144
800 | 2022-12-23 13:21 | 13.9 | 21.5 | 37.5 | 35.4 | 1.813 | 538
801 | 2022-12-23 13:22 | 14.3 | 21.6 | 37.4 | 35.2 | 1.813 | 770
802 | 2022-12-23 13:23 | 14.7 | 21.7 | 37.2 | 35.1 | 1.81 | 705
803 | 2022-12-23 13:24 | 14.8 | 21.7 | 37 | 35 | 1.811 | 737
804 | 2022-12-23 13:25 | 14.8 | 21.8 | 36.9 | 34.8 | 1.811 | 592
805 | 2022-12-23 13:26 | 15.1 | 21.8 | 36.8 | 34.7 | 1.81 | 781
806 | 2022-12-23 13:27 | 14.7 | 21.8 | 36.7 | 34.6 | 1.808 | 804
807 | 2022-12-23 13:28 | 14.7 | 21.8 | 37 | 34.8 | 1.811 | 808
808 | 2022-12-23 13:29 | 14.9 | 21.7 | 36.9 | 35.6 | 1.809 | 799
809 | 2022-12-23 13:30 | 15 | 21.4 | 36.9 | 35.5 | 1.814 | 798
810 | 2022-12-23 13:31 | 15.1 | 21.2 | 36.9 | 35.5 | 1.807 | 795
811 | 2022-12-23 13:32 | 15.1 | 20.9 | 36.8 | 35.5 | 1.752 | 769
812 | 2022-12-23 13:33 | 15.1 | 20.8 | 36.8 | 35.3 | 1.492 | 731
813 | 2022-12-23 13:34 | 15.3 | 20.7 | 36.8 | 35.2 | 1.493 | 750
814 | 2022-12-23 13:35 | 15.2 | 20.6 | 37.1 | 35.3 | 1.493 | 759
815 | 2022-12-23 13:36 | 15 | 20.6 | 37.6 | 35.6 | 1.494 | 145
816 | 2022-12-23 13:37 | 15 | 20.5 | 38.1 | 36 | 1.494 | 135
817 | 2022-12-23 13:38 | 14.4 | 20.4 | 38.6 | 36.5 | 1.494 | 158
818 | 2022-12-23 13:39 | 14.3 | 20.4 | 38.9 | 36.9 | 1.493 | 373
819 | 2022-12-23 13:40 | 14.5 | 20.4 | 39.3 | 37.3 | 1.496 | 645
820 | 2022-12-23 13:41 | 14.3 | 20.3 | 39.6 | 37.5 | 1.501 | 144
821 | 2022-12-23 13:42 | 14.3 | 20.4 | 40.2 | 37.9 | 1.5 | 202
822 | 2022-12-23 13:43 | 14.1 | 20.5 | 40.6 | 37.3 | 1.717 | 786
823 | 2022-12-23 13:44 | 14.6 | 20.6 | 40.8 | 37.8 | 1.819 | 762
824 | 2022-12-23 13:45 | 15 | 20.7 | 41.3 | 35.5 | 1.97 | 763
825 | 2022-12-23 13:46 | 15.2 | 20.8 | 41.6 | 38.3 | 1.993 | 772
826 | 2022-12-23 13:47 | 15.8 | 21.3 | 41.6 | 38.6 | 1.987 | 772
827 | 2022-12-23 13:48 | 16.1 | 21.5 | 42 | 38.6 | 1.982 | 755
828 | 2022-12-23 13:49 | 16.1 | 21.7 | 42.4 | 38.9 | 1.876 | 754
829 | 2022-12-23 13:50 | 16.2 | 22 | 42.6 | 39.2 | 1.877 | 748
830 | 2022-12-23 13:51 | 15.9 | 22.1 | 42.6 | 40.1 | 1.879 | 744
831 | 2022-12-23 13:52 | 16 | 22.2 | 42.4 | 41.2 | 1.884 | 744
832 | 2022-12-23 13:53 | 16.1 | 22.1 | 42.3 | 41.2 | 1.878 | 748
833 | 2022-12-23 13:54 | 16 | 21.7 | 42.4 | 41.1 | 1.859 | 732
834 | 2022-12-23 13:55 | 15.6 | 21.4 | 42.4 | 41 | 1.597 | 728
835 | 2022-12-23 13:56 | 15.8 | 21.2 | 42.3 | 40.8 | 1.292 | 734
836 | 2022-12-23 13:57 | 15.6 | 21.1 | 42.2 | 40.6 | 1.093 | 612
837 | 2022-12-23 13:58 | 15.8 | 20.9 | 42.1 | 40.5 | 1.092 | 555
838 | 2022-12-23 13:59 | 16 | 20.8 | 42.1 | 40.5 | 1.087 | 705
839 | 2022-12-23 14:00 | 16.1 | 20.8 | 42.1 | 40.5 | 1.088 | 749
840 | 2022-12-23 14:01 | 16.1 | 20.7 | 41.9 | 41.3 | 1.083 | 218
841 | 2022-12-23 14:02 | 15.7 | 20.6 | 41.8 | 41.4 | 1.343 | 141
842 | 2022-12-23 14:03 | 15.3 | 20.5 | 41.8 | 40.6 | 1.495 | 135
843 | 2022-12-23 14:04 | 15 | 20.5 | 41.8 | 40.6 | 1.504 | 132
844 | 2022-12-23 14:05 | 14.7 | 20.4 | 41.6 | 40.6 | 1.499 | 137
845 | 2022-12-23 14:06 | 14.4 | 20.4 | 41.6 | 40.5 | 1.446 | 138
846 | 2022-12-23 14:07 | 14.7 | 20.3 | 41.5 | 40.3 | 1.273 | 718
847 | 2022-12-23 14:08 | 15 | 20.3 | 41.4 | 40.1 | 0.976 | 723
848 | 2022-12-23 14:09 | 15 | 20.3 | 41.3 | 40 | 0.974 | 721
849 | 2022-12-23 14:10 | 15.3 | 20.4 | 41.3 | 36.3 | 1.472 | 719
850 | 2022-12-23 14:11 | 15.5 | 20.4 | 41.2 | 39 | 1.688 | 707
851 | 2022-12-23 14:12 | 15.8 | 20.7 | 40.9 | 38.3 | 1.82 | 713
852 | 2022-12-23 14:13 | 15.8 | 21 | 40.5 | 38 | 1.818 | 730
853 | 2022-12-23 14:14 | 15.6 | 21.4 | 40.3 | 37.9 | 1.813 | 721
854 | 2022-12-23 14:15 | 15.9 | 21.5 | 40.1 | 37.6 | 1.817 | 706
855 | 2022-12-23 14:16 | 15.9 | 21.6 | 40 | 37.6 | 1.819 | 715
856 | 2022-12-23 14:17 | 15.8 | 21.8 | 39.8 | 37.9 | 1.818 | 714
857 | 2022-12-23 14:18 | 15.6 | 21.9 | 39.7 | 37.8 | 1.815 | 719
858 | 2022-12-23 14:19 | 15.7 | 21.9 | 39.6 | 37.6 | 1.818 | 717
859 | 2022-12-23 14:20 | 15.8 | 22 | 39.5 | 37.5 | 1.767 | 699
860 | 2022-12-23 14:21 | 15.8 | 21.9 | 39.4 | 38.2 | 1.615 | 687
861 | 2022-12-23 14:22 | 15.7 | 21.6 | 39.2 | 38.2 | 1.617 | 677
862 | 2022-12-23 14:23 | 16.2 | 21.3 | 39.2 | 38.1 | 1.609 | 675
863 | 2022-12-23 14:24 | 16 | 21.1 | 39.2 | 38 | 1.594 | 664
864 | 2022-12-23 14:25 | 15.9 | 21 | 39.1 | 37.9 | 1.458 | 651
865 | 2022-12-23 14:26 | 15.7 | 20.8 | 39 | 37.6 | 1.088 | 649
866 | 2022-12-23 14:27 | 15.9 | 20.8 | 39 | 37.6 | 1.093 | 652
867 | 2022-12-23 14:28 | 15.8 | 20.7 | 38.9 | 37.5 | 1.087 | 663
868 | 2022-12-23 14:29 | 16.1 | 20.7 | 38.8 | 37.4 | 1.085 | 675
869 | 2022-12-23 14:30 | 15.6 | 20.6 | 38.7 | 37.3 | 1.086 | 674
870 | 2022-12-23 14:31 | 15.9 | 20.6 | 38.7 | 37.3 | 1.085 | 663
871 | 2022-12-23 14:32 | 15.9 | 20.5 | 38.5 | 37.1 | 1.418 | 280
872 | 2022-12-23 14:33 | 16.1 | 20.6 | 38.4 | 36.7 | 1.494 | 673
873 | 2022-12-23 14:34 | 15.6 | 20.5 | 38.5 | 36.7 | 1.5 | 662
874 | 2022-12-23 14:35 | 15.5 | 20.4 | 38.8 | 36.8 | 1.495 | 652
875 | 2022-12-23 14:36 | 15.2 | 20.4 | 39.3 | 37.2 | 1.494 | 640
876 | 2022-12-23 14:37 | 15.3 | 20.4 | 39.5 | 37.5 | 1.499 | 581
877 | 2022-12-23 14:38 | 15.6 | 20.5 | 39.8 | 37.8 | 1.493 | 513
878 | 2022-12-23 14:39 | 15.6 | 20.6 | 40.3 | 38.1 | 1.5 | 146
879 | 2022-12-23 14:40 | 15.3 | 20.6 | 40.6 | 37.1 | 1.814 | 141
880 | 2022-12-23 14:41 | 15 | 20.6 | 40.8 | 38 | 1.82 | 140
881 | 2022-12-23 14:42 | 14.9 | 20.9 | 40.5 | 38.1 | 1.819 | 416
882 | 2022-12-23 14:43 | 14.7 | 21.1 | 40.4 | 37.8 | 1.812 | 597
883 | 2022-12-23 14:44 | 14.7 | 21.4 | 40.2 | 37.7 | 1.814 | 602
884 | 2022-12-23 14:45 | 14.8 | 21.6 | 40.1 | 37.6 | 1.812 | 587
885 | 2022-12-23 14:46 | 14.8 | 21.7 | 39.8 | 37.4 | 1.82 | 591
886 | 2022-12-23 14:47 | 15.2 | 21.8 | 39.7 | 37.8 | 1.815 | 549
887 | 2022-12-23 14:48 | 15.1 | 22 | 39.6 | 37.7 | 1.817 | 316
888 | 2022-12-23 14:49 | 14.5 | 22 | 39.5 | 38.2 | 0.119 | 526
889 | 2022-12-23 14:50 | 14.7 | 21.9 | 39.4 | 38.1 | 0 | 399
890 | 2022-12-23 14:51 | 14.7 | 21.5 | 39.2 | 37.8 | 0 | 176
891 | 2022-12-23 14:52 | 14.4 | 21.2 | 39 | 37.5 | 0 | 188
892 | 2022-12-23 14:53 | 14.6 | 21 | 38.8 | 37.1 | 0 | 428
893 | 2022-12-23 14:54 | 15 | 20.8 | 38.6 | 36.8 | 0 | 572
894 | 2022-12-23 14:55 | 15.1 | 20.8 | 38.4 | 36.5 | 0 | 463
895 | 2022-12-23 14:56 | 15.5 | 20.7 | 38.3 | 36.2 | 0 | 341
896 | 2022-12-23 14:57 | 14.7 | 20.6 | 38.1 | 35.9 | 0 | 541
897 | 2022-12-23 14:58 | 14.7 | 20.5 | 37.9 | 35.6 | 0 | 557
898 | 2022-12-23 14:59 | 15 | 20.4 | 37.7 | 35.3 | 0 | 562
899 | 2022-12-23 15:00 | 15.1 | 20.4 | 37.5 | 36 | 0 | 581
900 | 2022-12-23 15:01 | 15.6 | 20.3 | 37.3 | 36.5 | 0 | 577
901 | 2022-12-23 15:02 | 15.5 | 20.3 | 39.1 | 34 | 1.04 | 573
902 | 2022-12-23 15:03 | 15.8 | 20.4 | 38.7 | 37.5 | 1.095 | 572
903 | 2022-12-23 15:04 | 15.7 | 20.5 | 38.8 | 35.2 | 1.82 | 567
904 | 2022-12-23 15:05 | 16.1 | 20.6 | 39.2 | 36.3 | 1.818 | 560
905 | 2022-12-23 15:06 | 16.1 | 20.8 | 39.4 | 33.8 | 1.978 | 558
906 | 2022-12-23 15:07 | 15.6 | 21 | 39.6 | 36.2 | 1.984 | 552
907 | 2022-12-23 15:08 | 15.7 | 21.3 | 39.8 | 36.4 | 1.99 | 548
908 | 2022-12-23 15:09 | 15.6 | 21.5 | 40.1 | 36.6 | 1.988 | 546
909 | 2022-12-23 15:10 | 14.8 | 21.7 | 40.4 | 36.9 | 1.99 | 540
910 | 2022-12-23 15:11 | 14.6 | 21.8 | 40.6 | 37.2 | 1.991 | 536
911 | 2022-12-23 15:12 | 14.8 | 22 | 40.6 | 37.3 | 1.991 | 525
912 | 2022-12-23 15:13 | 15.2 | 22.1 | 40.5 | 38.1 | 1.991 | 506
913 | 2022-12-23 15:14 | 15.6 | 22.1 | 40.2 | 38.9 | 1.992 | 495
914 | 2022-12-23 15:15 | 15.7 | 21.9 | 40.2 | 38.7 | 1.996 | 490
915 | 2022-12-23 15:16 | 15.8 | 21.5 | 40.2 | 39 | 1.909 | 491
916 | 2022-12-23 15:17 | 15.8 | 21.3 | 40.1 | 39.1 | 1.781 | 481
917 | 2022-12-23 15:18 | 15.6 | 21.1 | 40.1 | 38.9 | 1.501 | 471
918 | 2022-12-23 15:19 | 15.9 | 21 | 40.1 | 38.9 | 1.478 | 460
919 | 2022-12-23 15:20 | 16.2 | 20.9 | 40 | 38.6 | 1.09 | 460
920 | 2022-12-23 15:21 | 16.2 | 20.9 | 40 | 38.5 | 1.09 | 467
921 | 2022-12-23 15:22 | 16.3 | 20.8 | 39.9 | 38.4 | 1.09 | 458
922 | 2022-12-23 15:23 | 16.4 | 20.8 | 39.7 | 38.3 | 1.089 | 456
923 | 2022-12-23 15:24 | 16.6 | 20.6 | 39.7 | 38.3 | 0 | 456
924 | 2022-12-23 15:25 | 16.6 | 20.6 | 39.5 | 38 | 0 | 456
925 | 2022-12-23 15:26 | 16.3 | 20.6 | 39.3 | 37.6 | 0 | 457
926 | 2022-12-23 15:27 | 16.3 | 20.6 | 39.1 | 37.3 | 0 | 452
927 | 2022-12-23 15:28 | 16.1 | 20.5 | 38.9 | 37 | 0 | 449
928 | 2022-12-23 15:29 | 16 | 20.5 | 38.7 | 36.6 | 0 | 445
929 | 2022-12-23 15:30 | 16 | 20.5 | 38.5 | 36.3 | 0 | 118
930 | 2022-12-23 15:31 | 15.9 | 20.4 | 38.3 | 36 | 0 | 92
931 | 2022-12-23 15:32 | 15.4 | 20.4 | 38.1 | 36.1 | 0 | 88
932 | 2022-12-23 15:33 | 15.3 | 20.3 | 37.9 | 37.5 | 0.012 | 91
933 | 2022-12-23 15:34 | 14.8 | 20.4 | 37.7 | 38 | 0 | 89
934 | 2022-12-23 15:35 | 14.5 | 20.4 | 39.6 | 33.8 | 0.898 | 86
935 | 2022-12-23 15:36 | 14.4 | 20.5 | 39.9 | 36.8 | 1.494 | 251
936 | 2022-12-23 15:37 | 14.6 | 20.7 | 40.4 | 37.5 | 1.617 | 379
937 | 2022-12-23 15:38 | 14.9 | 20.9 | 40.6 | 38 | 1.619 | 363
938 | 2022-12-23 15:39 | 14.2 | 21.2 | 41 | 38.2 | 1.77 | 323
939 | 2022-12-23 15:40 | 14 | 21.4 | 41.5 | 38.2 | 1.825 | 247
940 | 2022-12-23 15:41 | 13.8 | 21.6 | 41.5 | 38.7 | 1.828 | 187
941 | 2022-12-23 15:42 | 13.9 | 21.7 | 41.3 | 38.7 | 1.829 | 336
942 | 2022-12-23 15:43 | 13.9 | 21.8 | 41.3 | 38.6 | 1.832 | 291
943 | 2022-12-23 15:44 | 13.8 | 21.9 | 41.1 | 38.6 | 1.831 | 335
944 | 2022-12-23 15:45 | 14 | 22 | 40.9 | 38.9 | 1.838 | 336
945 | 2022-12-23 15:46 | 13.7 | 21.9 | 40.7 | 38.7 | 1.831 | 331
946 | 2022-12-23 15:47 | 13.9 | 21.8 | 40.7 | 39.6 | 1.818 | 325
947 | 2022-12-23 15:48 | 13.8 | 21.6 | 40.6 | 39.5 | 1.619 | 323
948 | 2022-12-23 15:49 | 13.6 | 21.3 | 40.6 | 39.5 | 1.617 | 322
949 | 2022-12-23 15:50 | 13.4 | 21.1 | 40.5 | 39.4 | 1.579 | 315
950 | 2022-12-23 15:51 | 13.2 | 21 | 40.4 | 39.1 | 1.177 | 312
951 | 2022-12-23 15:52 | 13.1 | 20.9 | 40.3 | 38.8 | 1.088 | 311
952 | 2022-12-23 15:53 | 13.2 | 20.8 | 40.3 | 38.8 | 1.085 | 311
953 | 2022-12-23 15:54 | 13.1 | 20.7 | 40.3 | 38.7 | 0 | 303
954 | 2022-12-23 15:55 | 13.2 | 20.6 | 40.1 | 38.5 | 0 | 297
955 | 2022-12-23 15:56 | 13.2 | 20.6 | 39.9 | 38.1 | 0 | 293
956 | 2022-12-23 15:57 | 13.1 | 20.6 | 39.7 | 37.7 | 0 | 293
957 | 2022-12-23 15:58 | 13.2 | 20.6 | 39.4 | 37.4 | 0 | 294
958 | 2022-12-23 15:59 | 13.3 | 20.5 | 39.2 | 37 | 0 | 293
959 | 2022-12-23 16:00 | 13.3 | 20.5 | 39 | 36.7 | 0 | 292
960 | 2022-12-23 16:01 | 13.4 | 20.4 | 38.8 | 36.3 | 0 | 291
961 | 2022-12-23 16:02 | 13.4 | 20.4 | 38.6 | 36 | 0 | 288
962 | 2022-12-23 16:03 | 13 | 20.2 | 38.3 | 37.3 | 0.1 | 285
963 | 2022-12-23 16:04 | 13.2 | 20.3 | 38.1 | 37.8 | 0 | 283
964 | 2022-12-23 16:05 | 12.8 | 20.3 | 39.7 | 36.6 | 0.533 | 279
965 | 2022-12-23 16:06 | 13 | 20.4 | 40.4 | 34.9 | 1.512 | 276
966 | 2022-12-23 16:07 | 12.8 | 20.5 | 40.8 | 37.6 | 1.545 | 271
967 | 2022-12-23 16:08 | 12.6 | 20.8 | 40.7 | 37.5 | 1.799 | 266
968 | 2022-12-23 16:09 | 12.6 | 21.1 | 41.3 | 37.3 | 1.886 | 261
969 | 2022-12-23 16:10 | 12.4 | 21.4 | 41.6 | 38.3 | 1.891 | 256
970 | 2022-12-23 16:11 | 12.2 | 21.6 | 41.7 | 38.4 | 1.885 | 252
971 | 2022-12-23 16:12 | 12 | 21.8 | 42.2 | 38.7 | 1.886 | 246
972 | 2022-12-23 16:13 | 11.9 | 22 | 42.5 | 40 | 1.89 | 241
973 | 2022-12-23 16:14 | 11.8 | 22.1 | 42.9 | 40.3 | 1.886 | 236
974 | 2022-12-23 16:15 | 11.9 | 22.2 | 43 | 41.6 | 1.89 | 230
975 | 2022-12-23 16:16 | 11.6 | 21.8 | 43 | 41.6 | 1.653 | 225
976 | 2022-12-23 16:17 | 11.6 | 21.6 | 43 | 41.7 | 1.62 | 222
977 | 2022-12-23 16:18 | 11.3 | 21.2 | 43 | 41.7 | 1.606 | 219
978 | 2022-12-23 16:19 | 11.4 | 21.1 | 42.9 | 41.5 | 1.332 | 215
979 | 2022-12-23 16:20 | 11.2 | 21 | 42.9 | 41.2 | 1.094 | 210
980 | 2022-12-23 16:21 | 11.1 | 20.8 | 42.9 | 41.2 | 1.093 | 198
981 | 2022-12-23 16:22 | 11.1 | 20.8 | 42.9 | 41.1 | 0 | 181
982 | 2022-12-23 16:23 | 10.9 | 20.7 | 42.6 | 40.7 | 0 | 189
983 | 2022-12-23 16:24 | 10.9 | 20.6 | 42.4 | 40.2 | 0 | 189
984 | 2022-12-23 16:25 | 10.6 | 20.6 | 42.1 | 39.7 | 0 | 183
985 | 2022-12-23 16:26 | 10.6 | 20.5 | 41.8 | 39.3 | 0 | 186
986 | 2022-12-23 16:27 | 10.4 | 20.5 | 41.6 | 38.8 | 0 | 181
987 | 2022-12-23 16:28 | 10.5 | 20.5 | 41.3 | 38.4 | 0 | 176
988 | 2022-12-23 16:29 | 10.2 | 20.4 | 41.1 | 38 | 0 | 172
989 | 2022-12-23 16:30 | 10.3 | 20.3 | 40.8 | 37.6 | 0 | 167
990 | 2022-12-23 16:31 | 10.2 | 20.3 | 40.6 | 37.2 | 0 | 163
991 | 2022-12-23 16:32 | 10.3 | 20.3 | 40.3 | 37.9 | 0 | 159
992 | 2022-12-23 16:33 | 10.1 | 20.4 | 40.4 | 38.9 | 0 | 152
993 | 2022-12-23 16:34 | 10.1 | 20.4 | 42.1 | 37.6 | 1.598 | 147
994 | 2022-12-23 16:35 | 10.1 | 20.4 | 41.8 | 39.3 | 1.705 | 143
995 | 2022-12-23 16:36 | 10.1 | 20.8 | 41.4 | 38.6 | 1.834 | 138
996 | 2022-12-23 16:37 | 10 | 21 | 41.4 | 38.6 | 1.831 | 123
997 | 2022-12-23 16:38 | 9.8 | 21.3 | 41.2 | 38.6 | 1.825 | 88
998 | 2022-12-23 16:39 | 9.7 | 21.4 | 41.1 | 38.5 | 1.825 | 57
999 | 2022-12-23 16:40 | 9.7 | 21.6 | 40.9 | 38.3 | 1.825 | 44
1000 | 2022-12-23 16:41 | 9.5 | 21.8 | 40.7 | 38.2 | 1.823 | 30
1001 | 2022-12-23 16:42 | 9.6 | 21.8 | 40.5 | 38 | 1.833 | 26
1002 | 2022-12-23 16:43 | 9.8 | 21.9 | 40.3 | 37.8 | 1.83 | 25
1003 | 2022-12-23 16:44 | 9.6 | 22 | 40.1 | 37.7 | 1.831 | 23
1004 | 2022-12-23 16:45 | 9.7 | 22 | 40 | 37.5 | 1.829 | 20
1005 | 2022-12-23 16:46 | 9.5 | 21.9 | 39.8 | 38.3 | 1.822 | 18
1006 | 2022-12-23 16:47 | 9.6 | 21.5 | 39.7 | 38.2 | 1.826 | 17
1007 | 2022-12-23 16:48 | 9.5 | 21.3 | 39.7 | 38.1 | 1.819 | 15
1008 | 2022-12-23 16:49 | 9.4 | 21.1 | 39.6 | 38 | 1.798 | 14
1009 | 2022-12-23 16:50 | 9.3 | 21 | 39.4 | 37.7 | 1.527 | 13
1010 | 2022-12-23 16:51 | 9.2 | 20.8 | 39.3 | 37.6 | 1.503 | 12
1011 | 2022-12-23 16:52 | 9.1 | 20.8 | 39.2 | 37.5 | 1.508 | 11
1012 | 2022-12-23 16:53 | 9.1 | 20.7 | 39.1 | 37.4 | 1.504 | 10
1013 | 2022-12-23 16:54 | 9.1 | 20.6 | 38.9 | 37.3 | 1.502 | 9
1014 | 2022-12-23 16:55 | 9 | 20.6 | 38.8 | 37.1 | 1.502 | 8
1015 | 2022-12-23 16:56 | 8.9 | 20.5 | 38.7 | 37 | 1.5 | 7
1016 | 2022-12-23 16:57 | 8.8 | 20.5 | 38.6 | 36.9 | 1.499 | 6
1017 | 2022-12-23 16:58 | 8.7 | 20.5 | 38.5 | 35.6 | 1.818 | 5
1018 | 2022-12-23 16:59 | 8.8 | 20.4 | 38.3 | 36.5 | 1.828 | 5
1019 | 2022-12-23 17:00 | 8.7 | 20.5 | 38 | 36.4 | 1.83 | 4
1020 | 2022-12-23 17:01 | 8.8 | 20.5 | 38 | 36.2 | 1.825 | 3
1021 | 2022-12-23 17:02 | 8.6 | 20.5 | 37.9 | 35.9 | 1.63 | 1
1022 | 2022-12-23 17:03 | 8.7 | 20.5 | 37.7 | 35.8 | 1.619 | 0
1023 | 2022-12-23 17:04 | 8.4 | 20.6 | 37.7 | 35.7 | 1.628 | 0
1024 | 2022-12-23 17:05 | 8.4 | 20.6 | 37.8 | 35.7 | 1.63 | 0
1025 | 2022-12-23 17:06 | 8.3 | 20.6 | 38.1 | 35.8 | 1.624 | 0
1026 | 2022-12-23 17:07 | 8.2 | 20.6 | 38.5 | 37 | 1.631 | 0
1027 | 2022-12-23 17:08 | 8.2 | 20.6 | 38.9 | 37.5 | 1.63 | 0
1028 | 2022-12-23 17:09 | 8.2 | 20.6 | 39.3 | 37.9 | 1.628 | 0
1029 | 2022-12-23 17:10 | 8.1 | 20.6 | 39.8 | 39 | 1.622 | 0
1030 | 2022-12-23 17:11 | 8.1 | 20.7 | 40.1 | 39.2 | 1.305 | 0
1031 | 2022-12-23 17:12 | 8 | 20.6 | 40.6 | 38.3 | 1.615 | 0
1032 | 2022-12-23 17:13 | 8.1 | 20.7 | 40.5 | 39.1 | 1.618 | 0
1033 | 2022-12-23 17:14 | 8 | 20.9 | 40.2 | 37.5 | 1.794 | 0
1034 | 2022-12-23 17:15 | 7.9 | 21 | 40.2 | 38.2 | 1.785 | 0
1035 | 2022-12-23 17:16 | 7.8 | 21.1 | 40 | 38.1 | 1.649 | 0
1036 | 2022-12-23 17:17 | 7.8 | 21.2 | 39.9 | 37.8 | 1.559 | 0
1037 | 2022-12-23 17:18 | 8 | 21.3 | 39.8 | 37.7 | 1.554 | 0
1038 | 2022-12-23 17:19 | 7.7 | 21.3 | 39.7 | 37.6 | 1.556 | 0
1039 | 2022-12-23 17:20 | 7.7 | 21.5 | 39.5 | 37.5 | 1.558 | 0
1040 | 2022-12-23 17:21 | 7.8 | 21.5 | 39.3 | 37.3 | 1.559 | 0
1041 | 2022-12-23 17:22 | 7.6 | 21.5 | 39.3 | 37.2 | 1.558 | 0
1042 | 2022-12-23 17:23 | 7.6 | 21.5 | 39.1 | 37.1 | 1.556 | 0
1043 | 2022-12-23 17:24 | 7.6 | 21.6 | 38.9 | 37 | 1.652 | 0
1044 | 2022-12-23 17:25 | 7.7 | 21.5 | 38.7 | 36.3 | 1.824 | 0
1045 | 2022-12-23 17:26 | 7.7 | 21.6 | 38.6 | 36.3 | 1.822 | 0
1046 | 2022-12-23 17:27 | 7.6 | 21.7 | 38.3 | 36.1 | 1.826 | 0
1047 | 2022-12-23 17:28 | 7.7 | 21.7 | 38.2 | 35.9 | 1.826 | 0
1048 | 2022-12-23 17:29 | 7.4 | 21.7 | 38.1 | 35.8 | 1.821 | 0
1049 | 2022-12-23 17:30 | 7.5 | 21.8 | 37.9 | 35.6 | 1.819 | 0
1050 | 2022-12-23 17:31 | 7.5 | 21.8 | 37.7 | 36.6 | 1.82 | 0
1051 | 2022-12-23 17:32 | 7.7 | 21.6 | 37.6 | 36.7 | 1.821 | 0
1052 | 2022-12-23 17:33 | 7.5 | 21.2 | 37.6 | 36.6 | 1.823 | 0
1053 | 2022-12-23 17:34 | 7.3 | 21.1 | 37.8 | 36.7 | 1.796 | 0
1054 | 2022-12-23 17:35 | 7.2 | 21 | 38.1 | 36.7 | 1.459 | 0
1055 | 2022-12-23 17:36 | 7.2 | 20.8 | 38.6 | 36.7 | 1.085 | 0
1056 | 2022-12-23 17:37 | 7.3 | 20.9 | 39 | 37.2 | 1.08 | 0
1057 | 2022-12-23 17:38 | 7.2 | 20.8 | 39.2 | 37.6 | 1.089 | 0
1058 | 2022-12-23 17:39 | 7.3 | 20.5 | 39.8 | 37.7 | 1.087 | 0
1059 | 2022-12-23 17:40 | 7.2 | 20.5 | 40.1 | 38.2 | 1.09 | 0
1060 | 2022-12-23 17:41 | 7.1 | 20.5 | 40.4 | 38.6 | 1.086 | 0
1061 | 2022-12-23 17:42 | 7.1 | 20.5 | 40.9 | 38.8 | 1.083 | 0
1062 | 2022-12-23 17:43 | 7.1 | 20.4 | 41.2 | 39.3 | 1.089 | 0
1063 | 2022-12-23 17:44 | 7.2 | 20.4 | 41.6 | 35 | 1.562 | 0
1064 | 2022-12-23 17:45 | 7.1 | 20.4 | 42 | 39.1 | 1.627 | 0
1065 | 2022-12-23 17:46 | 7 | 20.4 | 41.9 | 39.5 | 1.631 | 0
1066 | 2022-12-23 17:47 | 7 | 20.4 | 42.3 | 39.5 | 1.63 | 0
1067 | 2022-12-23 17:48 | 6.9 | 20.5 | 42.7 | 39.8 | 1.628 | 0
1068 | 2022-12-23 17:49 | 7 | 20.7 | 43.1 | 37.5 | 1.825 | 0
1069 | 2022-12-23 17:50 | 6.8 | 20.9 | 42.7 | 39.9 | 1.849 | 0
1070 | 2022-12-23 17:51 | 6.9 | 21 | 42.4 | 38.8 | 1.995 | 0
1071 | 2022-12-23 17:52 | 6.8 | 21.1 | 42.2 | 39.8 | 2 | 0
1072 | 2022-12-23 17:53 | 6.7 | 21.3 | 41.9 | 40.1 | 2.01 | 0
1073 | 2022-12-23 17:54 | 6.8 | 21.6 | 41.8 | 39.9 | 2.001 | 0
1074 | 2022-12-23 17:55 | 6.7 | 21.6 | 41.8 | 39.6 | 1.83 | 0
1075 | 2022-12-23 17:56 | 6.8 | 21.6 | 41.6 | 39.7 | 1.829 | 0
1076 | 2022-12-23 17:57 | 6.7 | 21.6 | 41.4 | 39.5 | 1.802 | 0
1077 | 2022-12-23 17:58 | 6.8 | 21.6 | 41.3 | 39.2 | 1.724 | 0
1078 | 2022-12-23 17:59 | 6.7 | 21.6 | 41.1 | 39 | 1.559 | 0
1079 | 2022-12-23 18:00 | 6.9 | 21.6 | 41 | 38.8 | 1.559 | 0
1080 | 2022-12-23 18:01 | 6.7 | 21.7 | 40.9 | 38.7 | 1.557 | 0
1081 | 2022-12-23 18:02 | 6.6 | 21.8 | 40.8 | 38.6 | 1.557 | 0
1082 | 2022-12-23 18:03 | 6.6 | 21.8 | 40.6 | 39 | 1.554 | 0
1083 | 2022-12-23 18:04 | 6.8 | 21.6 | 40.6 | 39 | 1.559 | 0
1084 | 2022-12-23 18:05 | 6.8 | 21.7 | 40.6 | 38.9 | 0 | 0
1085 | 2022-12-23 18:06 | 6.7 | 21.5 | 40.5 | 38.6 | 0 | 0
1086 | 2022-12-23 18:07 | 6.5 | 21.3 | 41.9 | 40.6 | 0.954 | 0
1087 | 2022-12-23 18:08 | 6.6 | 20.9 | 42.3 | 39.5 | 1.494 | 0
1088 | 2022-12-23 18:09 | 6.5 | 20.7 | 42.5 | 40.8 | 1.553 | 0
1089 | 2022-12-23 18:10 | 6.6 | 20.6 | 42.9 | 40.7 | 1.087 | 0
1090 | 2022-12-23 18:11 | 6.5 | 20.5 | 43.2 | 41.1 | 1.085 | 0
1091 | 2022-12-23 18:12 | 6.4 | 20.5 | 43.7 | 41.4 | 1.089 | 0
1092 | 2022-12-23 18:13 | 6.4 | 20.4 | 44.1 | 41.9 | 1.084 | 0
1093 | 2022-12-23 18:14 | 6.4 | 20.4 | 44.5 | 42.2 | 1.093 | 0
1094 | 2022-12-23 18:15 | 6.4 | 20.4 | 44.7 | 42.6 | 1.093 | 0
1095 | 2022-12-23 18:16 | 6.4 | 20.4 | 45 | 42.7 | 1.091 | 0
1096 | 2022-12-23 18:17 | 6.4 | 20.4 | 45.5 | 43.1 | 1.091 | 0
1097 | 2022-12-23 18:18 | 6.3 | 20.4 | 45.9 | 43.6 | 1.091 | 0
1098 | 2022-12-23 18:19 | 6.3 | 20.4 | 46.2 | 43.9 | 1.093 | 0
1099 | 2022-12-23 18:20 | 6.2 | 20.3 | 46.7 | 44.2 | 1.097 | 0
1100 | 2022-12-23 18:21 | 6.4 | 20.3 | 46.9 | 40.4 | 1.783 | 0
1101 | 2022-12-23 18:22 | 6.3 | 20.4 | 47.2 | 43.3 | 1.845 | 0
1102 | 2022-12-23 18:23 | 6.3 | 20.6 | 47 | 43.6 | 1.85 | 0
1103 | 2022-12-23 18:24 | 6.2 | 20.8 | 47.5 | 41.8 | 2.002 | 0
1104 | 2022-12-23 18:25 | 6.2 | 21.1 | 47.4 | 43 | 2.007 | 0
1105 | 2022-12-23 18:26 | 6.3 | 21.4 | 46.8 | 43.6 | 2.008 | 0
1106 | 2022-12-23 18:27 | 6.1 | 21.7 | 46.5 | 44.3 | 2.01 | 0
1107 | 2022-12-23 18:28 | 6.3 | 22 | 46.4 | 44.1 | 2.012 | 0
1108 | 2022-12-23 18:29 | 6.3 | 22.1 | 46.3 | 44.1 | 2.002 | 0
1109 | 2022-12-23 18:30 | 6.2 | 22.1 | 46.2 | 44.1 | 0 | 0
1110 | 2022-12-23 18:31 | 6.3 | 21.8 | 45.9 | 43.7 | 0 | 0
1111 | 2022-12-23 18:32 | 6.1 | 21.5 | 45.6 | 43 | 0 | 0
1112 | 2022-12-23 18:33 | 6 | 21.3 | 45.3 | 42.4 | 0 | 0
1113 | 2022-12-23 18:34 | 6.3 | 21 | 45 | 41.8 | 0 | 0
1114 | 2022-12-23 18:35 | 6.1 | 20.8 | 44.7 | 41.2 | 0 | 0
1115 | 2022-12-23 18:36 | 6.3 | 20.6 | 44.3 | 40.6 | 0 | 0
1116 | 2022-12-23 18:37 | 6.2 | 20.5 | 44 | 40.1 | 0 | 0
1117 | 2022-12-23 18:38 | 6.3 | 20.4 | 43.7 | 39.6 | 0 | 0
1118 | 2022-12-23 18:39 | 6.1 | 20.3 | 43.4 | 39.1 | 0 | 0
1119 | 2022-12-23 18:40 | 6.3 | 20.3 | 43.1 | 38.6 | 0 | 0
1120 | 2022-12-23 18:41 | 6.1 | 20.3 | 42.7 | 38.6 | 0 | 0
1121 | 2022-12-23 18:42 | 6.1 | 20.1 | 44.4 | 40.6 | 0.546 | 0
1122 | 2022-12-23 18:43 | 6.2 | 20.2 | 45.5 | 41.9 | 1.083 | 0
1123 | 2022-12-23 18:44 | 6.3 | 20.2 | 44.5 | 43.2 | 1.095 | 0
1124 | 2022-12-23 18:45 | 6.2 | 20.2 | 44.9 | 42.6 | 1.096 | 0
1125 | 2022-12-23 18:46 | 6.1 | 20.3 | 44.8 | 41.1 | 1.622 | 0
1126 | 2022-12-23 18:47 | 6 | 20.5 | 44.7 | 41.9 | 1.627 | 0
1127 | 2022-12-23 18:48 | 6 | 20.7 | 44.4 | 41.9 | 1.793 | 0
1128 | 2022-12-23 18:49 | 6.1 | 21.1 | 44.4 | 41.1 | 1.835 | 0
1129 | 2022-12-23 18:50 | 6.2 | 21.3 | 44.3 | 41.2 | 1.834 | 0
1130 | 2022-12-23 18:51 | 6 | 21.5 | 43.9 | 41 | 1.83 | 0
1131 | 2022-12-23 18:52 | 6 | 21.6 | 43.8 | 40.8 | 1.835 | 0
1132 | 2022-12-23 18:53 | 6 | 21.7 | 43.6 | 40.7 | 1.838 | 0
1133 | 2022-12-23 18:54 | 6.1 | 21.9 | 43.4 | 40.5 | 1.833 | 0
1134 | 2022-12-23 18:55 | 5.9 | 21.9 | 43.1 | 40.3 | 1.831 | 0
1135 | 2022-12-23 18:56 | 6.2 | 21.9 | 42.9 | 40.1 | 1.83 | 0
1136 | 2022-12-23 18:57 | 6.1 | 21.9 | 42.6 | 40.2 | 1.832 | 0
1137 | 2022-12-23 18:58 | 6.1 | 21.8 | 42.4 | 40.7 | 1.836 | 0
1138 | 2022-12-23 18:59 | 6 | 21.5 | 42.3 | 40.6 | 0.759 | 0
1139 | 2022-12-23 19:00 | 6 | 21.2 | 42.2 | 40.3 | 0 | 0
1140 | 2022-12-23 19:01 | 6 | 21.1 | 41.9 | 39.8 | 0 | 0
1141 | 2022-12-23 19:02 | 5.8 | 20.9 | 41.7 | 39.2 | 0 | 0
1142 | 2022-12-23 19:03 | 5.8 | 20.7 | 41.4 | 38.6 | 0 | 0
1143 | 2022-12-23 19:04 | 5.9 | 20.6 | 42 | 38.6 | 1.052 | 0
1144 | 2022-12-23 19:05 | 5.8 | 20.4 | 42 | 41.4 | 0.831 | 0
1145 | 2022-12-23 19:06 | 5.9 | 20.4 | 41.8 | 41.5 | 0.385 | 0
1146 | 2022-12-23 19:07 | 5.8 | 20.3 | 41.9 | 38 | 0.964 | 0
1147 | 2022-12-23 19:08 | 5.8 | 20.3 | 41.8 | 39.3 | 0.981 | 0
1148 | 2022-12-23 19:09 | 5.7 | 20.3 | 41.8 | 39.4 | 0.977 | 0
1149 | 2022-12-23 19:10 | 5.7 | 20.3 | 41.7 | 39.4 | 0.982 | 0
1150 | 2022-12-23 19:11 | 5.7 | 20.4 | 41.3 | 39.2 | 0.982 | 0
1151 | 2022-12-23 19:12 | 5.7 | 20.5 | 41.2 | 39.2 | 1.424 | 0
1152 | 2022-12-23 19:13 | 5.7 | 20.5 | 41 | 39.7 | 1.624 | 0
1153 | 2022-12-23 19:14 | 5.6 | 20.6 | 40.9 | 39.8 | 1.638 | 0
1154 | 2022-12-23 19:15 | 5.7 | 20.6 | 41 | 39.7 | 1.635 | 0
1155 | 2022-12-23 19:16 | 5.7 | 20.5 | 41 | 39.7 | 1.54 | 0
1156 | 2022-12-23 19:17 | 5.7 | 20.5 | 40.9 | 39.3 | 1.092 | 0
1157 | 2022-12-23 19:18 | 5.7 | 20.4 | 40.9 | 39.3 | 1.094 | 0
1158 | 2022-12-23 19:19 | 5.8 | 20.5 | 40.8 | 39 | 1.431 | 0
1159 | 2022-12-23 19:20 | 5.6 | 20.6 | 40.6 | 36.4 | 1.816 | 0
1160 | 2022-12-23 19:21 | 5.7 | 20.6 | 40.5 | 37.8 | 1.829 | 0
1161 | 2022-12-23 19:22 | 5.6 | 20.8 | 40 | 37.7 | 1.824 | 0
1162 | 2022-12-23 19:23 | 5.7 | 21.1 | 39.9 | 37.3 | 1.824 | 0
1163 | 2022-12-23 19:24 | 5.5 | 21.4 | 39.7 | 37.2 | 1.831 | 0
1164 | 2022-12-23 19:25 | 5.7 | 21.5 | 39.4 | 37 | 1.826 | 0
1165 | 2022-12-23 19:26 | 5.7 | 21.6 | 39.3 | 36.9 | 1.824 | 0
1166 | 2022-12-23 19:27 | 5.7 | 21.7 | 39.2 | 36.7 | 1.827 | 0
1167 | 2022-12-23 19:28 | 5.7 | 21.8 | 38.9 | 36.6 | 1.822 | 0
1168 | 2022-12-23 19:29 | 5.7 | 21.8 | 38.8 | 36.4 | 1.829 | 0
1169 | 2022-12-23 19:30 | 5.7 | 21.8 | 38.6 | 36.3 | 1.829 | 0
1170 | 2022-12-23 19:31 | 5.6 | 21.8 | 38.4 | 36.1 | 1.827 | 0
1171 | 2022-12-23 19:32 | 5.6 | 21.9 | 38.2 | 35.9 | 1.82 | 0
1172 | 2022-12-23 19:33 | 5.4 | 21.8 | 38 | 36.6 | 1.829 | 0
1173 | 2022-12-23 19:34 | 5.6 | 21.6 | 38 | 36.4 | 1.823 | 0
1174 | 2022-12-23 19:35 | 5.4 | 21.3 | 38.4 | 36.5 | 1.82 | 0
1175 | 2022-12-23 19:36 | 5.5 | 21.1 | 38.8 | 36.9 | 1.809 | 0
1176 | 2022-12-23 19:37 | 5.6 | 20.9 | 39.1 | 37 | 1.622 | 0
1177 | 2022-12-23 19:38 | 5.3 | 20.9 | 39.4 | 37.4 | 1.506 | 0
1178 | 2022-12-23 19:39 | 5.6 | 20.7 | 39.7 | 37.6 | 1.507 | 0
1179 | 2022-12-23 19:40 | 5.7 | 20.6 | 40 | 37.9 | 1.507 | 0
1180 | 2022-12-23 19:41 | 5.5 | 20.6 | 40.4 | 38.2 | 1.507 | 0
1181 | 2022-12-23 19:42 | 5.6 | 20.6 | 40.9 | 38.6 | 1.505 | 0
1182 | 2022-12-23 19:43 | 5.5 | 20.5 | 41.1 | 39.6 | 1.51 | 0
1183 | 2022-12-23 19:44 | 5.6 | 20.5 | 41.6 | 39.7 | 1.527 | 0
1184 | 2022-12-23 19:45 | 5.5 | 20.5 | 42.1 | 39.8 | 1.834 | 0
1185 | 2022-12-23 19:46 | 5.6 | 20.5 | 42.3 | 40.5 | 1.826 | 0
1186 | 2022-12-23 19:47 | 5.5 | 20.4 | 42.6 | 40.6 | 1.638 | 0
1187 | 2022-12-23 19:48 | 5.6 | 20.4 | 43 | 41 | 1.624 | 0
1188 | 2022-12-23 19:49 | 5.6 | 20.4 | 43.3 | 41.4 | 1.596 | 0
1189 | 2022-12-23 19:50 | 5.7 | 20.5 | 43.6 | 41.5 | 1.419 | 0
1190 | 2022-12-23 19:51 | 5.5 | 20.5 | 43.9 | 41.4 | 0 | 0
1191 | 2022-12-23 19:52 | 5.5 | 20.6 | 43.7 | 41 | 0 | 0
1192 | 2022-12-23 19:53 | 5.5 | 20.6 | 44.4 | 42.9 | 0.988 | 0
1193 | 2022-12-23 19:54 | 5.6 | 20.6 | 44.1 | 44 | 0.967 | 0
1194 | 2022-12-23 19:55 | 5.5 | 20.7 | 44 | 36.1 | 1.137 | 0
1195 | 2022-12-23 19:56 | 5.7 | 20.7 | 44 | 41 | 0.951 | 0
1196 | 2022-12-23 19:57 | 5.5 | 20.8 | 44.1 | 38.3 | 1.545 | 0
1197 | 2022-12-23 19:58 | 5.4 | 20.9 | 43.6 | 40.9 | 1.782 | 0
1198 | 2022-12-23 19:59 | 5.6 | 21.1 | 43.3 | 40.4 | 1.836 | 0
1199 | 2022-12-23 20:00 | 5.5 | 21.3 | 43.2 | 40.2 | 1.829 | 0
1200 | 2022-12-23 20:01 | 5.6 | 21.4 | 43 | 40.1 | 1.833 | 0
1201 | 2022-12-23 20:02 | 5.4 | 21.5 | 42.8 | 40 | 1.829 | 0
1202 | 2022-12-23 20:03 | 5.6 | 21.6 | 42.7 | 39.8 | 1.829 | 0
1203 | 2022-12-23 20:04 | 5.4 | 21.8 | 42.4 | 39.6 | 1.833 | 0
1204 | 2022-12-23 20:05 | 5.5 | 21.8 | 42.2 | 39.4 | 1.832 | 0
1205 | 2022-12-23 20:06 | 5.4 | 21.8 | 42 | 39.2 | 1.828 | 0
1206 | 2022-12-23 20:07 | 5.5 | 21.8 | 41.7 | 39.1 | 1.834 | 0
1207 | 2022-12-23 20:08 | 5.6 | 21.8 | 41.5 | 39.8 | 1.831 | 0
1208 | 2022-12-23 20:09 | 5.5 | 21.5 | 41.3 | 39.6 | 1.833 | 0
1209 | 2022-12-23 20:10 | 5.5 | 21.3 | 41.3 | 39.5 | 1.829 | 0
1210 | 2022-12-23 20:11 | 5.5 | 21.1 | 41.1 | 39.4 | 1.79 | 0
1211 | 2022-12-23 20:12 | 5.5 | 21 | 41 | 39 | 1.505 | 0
1212 | 2022-12-23 20:13 | 5.6 | 20.9 | 40.9 | 39 | 1.509 | 0
1213 | 2022-12-23 20:14 | 5.5 | 20.8 | 40.8 | 39.5 | 1.507 | 0
1214 | 2022-12-23 20:15 | 5.5 | 20.7 | 40.6 | 39.4 | 1.503 | 0
1215 | 2022-12-23 20:16 | 5.5 | 20.6 | 40.6 | 39.3 | 1.501 | 0
1216 | 2022-12-23 20:17 | 5.4 | 20.6 | 40.5 | 39.3 | 1.46 | 0
1217 | 2022-12-23 20:18 | 5.7 | 20.6 | 40.4 | 38.9 | 1.087 | 0
1218 | 2022-12-23 20:19 | 5.5 | 20.5 | 40.4 | 38.8 | 1.089 | 0
1219 | 2022-12-23 20:20 | 5.4 | 20.4 | 40.3 | 38.8 | 1.093 | 0
1220 | 2022-12-23 20:21 | 5.5 | 20.5 | 40.2 | 37 | 1.615 | 0
1221 | 2022-12-23 20:22 | 5.6 | 20.4 | 40.2 | 37.8 | 1.637 | 0
1222 | 2022-12-23 20:23 | 5.6 | 20.5 | 39.8 | 37.8 | 1.64 | 0
1223 | 2022-12-23 20:24 | 5.5 | 20.5 | 39.6 | 37.5 | 1.625 | 0
1224 | 2022-12-23 20:25 | 5.7 | 20.5 | 39.6 | 37.4 | 1.633 | 0
1225 | 2022-12-23 20:26 | 5.6 | 20.6 | 39.4 | 38 | 1.633 | 0
1226 | 2022-12-23 20:27 | 5.4 | 20.7 | 39.2 | 37.9 | 1.641 | 0
1227 | 2022-12-23 20:28 | 5.6 | 20.6 | 39.2 | 37.2 | 1.834 | 0
1228 | 2022-12-23 20:29 | 5.5 | 20.7 | 39.1 | 38.1 | 1.836 | 0
1229 | 2022-12-23 20:30 | 5.5 | 20.7 | 38.9 | 38.1 | 1.819 | 0
1230 | 2022-12-23 20:31 | 5.4 | 20.5 | 38.9 | 37.9 | 1.748 | 0
1231 | 2022-12-23 20:32 | 5.5 | 20.4 | 38.9 | 37.9 | 1.501 | 0
1232 | 2022-12-23 20:33 | 5.4 | 20.4 | 38.8 | 37.5 | 0.984 | 0
1233 | 2022-12-23 20:34 | 5.5 | 20.5 | 38.8 | 37.4 | 0.997 | 0
1234 | 2022-12-23 20:35 | 5.5 | 20.4 | 39 | 36.4 | 1.548 | 0
1235 | 2022-12-23 20:36 | 5.5 | 20.5 | 39.3 | 36.9 | 1.552 | 0
1236 | 2022-12-23 20:37 | 5.4 | 20.6 | 39.5 | 37.2 | 1.556 | 0
1237 | 2022-12-23 20:38 | 5.4 | 20.7 | 39.8 | 37.1 | 1.768 | 0
1238 | 2022-12-23 20:39 | 5.4 | 20.9 | 40.2 | 37.2 | 1.826 | 0
1239 | 2022-12-23 20:40 | 5.3 | 21.1 | 40.4 | 37.5 | 1.826 | 0
1240 | 2022-12-23 20:41 | 5.3 | 21.1 | 40.7 | 37.7 | 1.826 | 0
1241 | 2022-12-23 20:42 | 5.4 | 21.4 | 41 | 38 | 1.831 | 0
1242 | 2022-12-23 20:43 | 5.4 | 21.5 | 41.1 | 38.3 | 1.826 | 0
1243 | 2022-12-23 20:44 | 5.2 | 21.6 | 41 | 38.3 | 1.83 | 0
1244 | 2022-12-23 20:45 | 5.3 | 21.7 | 40.9 | 38.2 | 1.827 | 0
1245 | 2022-12-23 20:46 | 5.3 | 21.7 | 40.8 | 38.1 | 1.827 | 0
1246 | 2022-12-23 20:47 | 5.4 | 21.8 | 40.5 | 38 | 1.826 | 0
1247 | 2022-12-23 20:48 | 5.4 | 21.8 | 40.3 | 37.8 | 1.833 | 0
1248 | 2022-12-23 20:49 | 5.3 | 21.8 | 40.1 | 37.6 | 1.823 | 0
1249 | 2022-12-23 20:50 | 5.3 | 21.9 | 40 | 37.5 | 1.827 | 0
1250 | 2022-12-23 20:51 | 5.2 | 21.8 | 39.7 | 38.7 | 1.826 | 0
1251 | 2022-12-23 20:52 | 5.3 | 21.6 | 39.6 | 38.6 | 1.83 | 0
1252 | 2022-12-23 20:53 | 5.1 | 21.3 | 39.7 | 38.5 | 1.829 | 0
1253 | 2022-12-23 20:54 | 5.3 | 21.1 | 39.7 | 38.6 | 1.791 | 0
1254 | 2022-12-23 20:55 | 5.3 | 20.9 | 39.6 | 38.3 | 1.393 | 0
1255 | 2022-12-23 20:56 | 5.2 | 20.8 | 39.6 | 38.1 | 1.086 | 0
1256 | 2022-12-23 20:57 | 5.1 | 20.8 | 39.4 | 38 | 1.086 | 0
1257 | 2022-12-23 20:58 | 5 | 20.6 | 39.4 | 37.9 | 1.085 | 0
1258 | 2022-12-23 20:59 | 4.9 | 20.6 | 39.4 | 37.8 | 1.087 | 0
1259 | 2022-12-23 21:00 | 5 | 20.6 | 39.3 | 37.8 | 0.011 | 0
1260 | 2022-12-23 21:01 | 5.1 | 20.5 | 39.2 | 37.6 | 0 | 0
1261 | 2022-12-23 21:02 | 5 | 20.4 | 38.9 | 37 | 0 | 0
1262 | 2022-12-23 21:03 | 5.1 | 20.4 | 38.7 | 36.5 | 0 | 0
1263 | 2022-12-23 21:04 | 5 | 20.3 | 38.4 | 36 | 0 | 0
1264 | 2022-12-23 21:05 | 5 | 20.2 | 38.1 | 35.4 | 0 | 0
1265 | 2022-12-23 21:06 | 5 | 20.2 | 37.9 | 35 | 0 | 0
1266 | 2022-12-23 21:07 | 4.9 | 20.1 | 37.6 | 34.5 | 0 | 0
1267 | 2022-12-23 21:08 | 4.8 | 20.1 | 37.4 | 34 | 0 | 0
1268 | 2022-12-23 21:09 | 5 | 20.1 | 37.1 | 33.6 | 0 | 0
1269 | 2022-12-23 21:10 | 4.8 | 20 | 36.8 | 33.2 | 0 | 0
1270 | 2022-12-23 21:11 | 5 | 20.1 | 36.6 | 32.8 | 0 | 0
1271 | 2022-12-23 21:12 | 5 | 19.9 | 36.3 | 32.4 | 0 | 0
1272 | 2022-12-23 21:13 | 5.1 | 19.9 | 36.1 | 32 | 0 | 0
1273 | 2022-12-23 21:14 | 4.8 | 19.9 | 35.8 | 31.6 | 0 | 0
1274 | 2022-12-23 21:15 | 4.9 | 20 | 35.6 | 31.3 | 0 | 0
1275 | 2022-12-23 21:16 | 5 | 19.9 | 35.3 | 30.9 | 0 | 0
1276 | 2022-12-23 21:17 | 5 | 19.9 | 35.1 | 30.6 | 0 | 0
1277 | 2022-12-23 21:18 | 4.8 | 19.9 | 34.8 | 30.3 | 0 | 0
1278 | 2022-12-23 21:19 | 5 | 19.8 | 34.6 | 30 | 0 | 0
1279 | 2022-12-23 21:20 | 5 | 19.8 | 34.4 | 29.7 | 0 | 0
1280 | 2022-12-23 21:21 | 5 | 19.8 | 34.1 | 29.4 | 0 | 0
1281 | 2022-12-23 21:22 | 4.8 | 19.8 | 33.9 | 29.1 | 0 | 0
1282 | 2022-12-23 21:23 | 4.8 | 19.8 | 33.7 | 28.8 | 0 | 0
1283 | 2022-12-23 21:24 | 5.1 | 19.7 | 33.4 | 28.6 | 0 | 0
1284 | 2022-12-23 21:25 | 4.9 | 19.7 | 33.2 | 28.3 | 0 | 0
1285 | 2022-12-23 21:26 | 4.9 | 19.7 | 33 | 28 | 0 | 0
1286 | 2022-12-23 21:27 | 5.1 | 19.8 | 32.7 | 27.8 | 0 | 0
1287 | 2022-12-23 21:28 | 5 | 19.7 | 32.5 | 27.5 | 0 | 0
1288 | 2022-12-23 21:29 | 5 | 19.7 | 32.3 | 27.3 | 0 | 0
1289 | 2022-12-23 21:30 | 5.1 | 19.6 | 32.1 | 27.1 | 0 | 0
1290 | 2022-12-23 21:31 | 4.8 | 19.7 | 31.9 | 26.8 | 0 | 0
1291 | 2022-12-23 21:32 | 5 | 19.7 | 31.6 | 26.6 | 0 | 0
1292 | 2022-12-23 21:33 | 4.9 | 19.7 | 31.4 | 26.4 | 0 | 0
1293 | 2022-12-23 21:34 | 4.9 | 19.6 | 31.2 | 26.1 | 0 | 0
1294 | 2022-12-23 21:35 | 4.9 | 19.7 | 31 | 25.9 | 0 | 0
1295 | 2022-12-23 21:36 | 5 | 19.6 | 30.8 | 25.7 | 0 | 0
1296 | 2022-12-23 21:37 | 5.1 | 19.6 | 30.6 | 25.5 | 0 | 0
1297 | 2022-12-23 21:38 | 5 | 19.5 | 30.4 | 25.3 | 0 | 0
1298 | 2022-12-23 21:39 | 5 | 19.5 | 30.2 | 25.1 | 0 | 0
1299 | 2022-12-23 21:40 | 4.9 | 19.5 | 30 | 24.9 | 0 | 0
1300 | 2022-12-23 21:41 | 5 | 19.5 | 29.8 | 24.7 | 0 | 0
1301 | 2022-12-23 21:42 | 5 | 19.5 | 29.6 | 24.5 | 0 | 0
1302 | 2022-12-23 21:43 | 5 | 19.5 | 29.4 | 24.3 | 0 | 0
1303 | 2022-12-23 21:44 | 4.9 | 19.5 | 29.2 | 24.1 | 0 | 0
1304 | 2022-12-23 21:45 | 5 | 19.5 | 29 | 23.9 | 0 | 0
1305 | 2022-12-23 21:46 | 4.8 | 19.5 | 28.8 | 23.8 | 0 | 0
1306 | 2022-12-23 21:47 | 4.8 | 19.5 | 28.6 | 23.6 | 0 | 0
1307 | 2022-12-23 21:48 | 4.8 | 19.5 | 28.4 | 23.4 | 0 | 0
1308 | 2022-12-23 21:49 | 4.9 | 19.6 | 28.2 | 23.2 | 0 | 0
1309 | 2022-12-23 21:50 | 4.9 | 19.5 | 28 | 23.1 | 0 | 0
1310 | 2022-12-23 21:51 | 4.9 | 19.5 | 27.8 | 22.9 | 0 | 0
1311 | 2022-12-23 21:52 | 5 | 19.5 | 27.6 | 22.7 | 0 | 0
1312 | 2022-12-23 21:53 | 4.8 | 19.5 | 27.4 | 22.6 | 0 | 0
1313 | 2022-12-23 21:54 | 5 | 19.5 | 27.2 | 22.4 | 0 | 0
1314 | 2022-12-23 21:55 | 5 | 19.5 | 27 | 22.2 | 0 | 0
1315 | 2022-12-23 21:56 | 5 | 19.4 | 26.8 | 22.1 | 0 | 0
1316 | 2022-12-23 21:57 | 5 | 19.5 | 26.7 | 21.9 | 0 | 0
1317 | 2022-12-23 21:58 | 4.8 | 19.4 | 26.5 | 21.8 | 0 | 0
1318 | 2022-12-23 21:59 | 5 | 19.5 | 26.3 | 21.6 | 0 | 0
1319 | 2022-12-23 22:00 | 4.8 | 19.5 | 26.1 | 21.5 | 0 | 0
1320 | 2022-12-23 22:01 | 4.8 | 19.4 | 26 | 21.3 | 0 | 0
1321 | 2022-12-23 22:02 | 4.8 | 19.4 | 25.8 | 21.2 | 0 | 0
1322 | 2022-12-23 22:03 | 4.7 | 19.4 | 25.6 | 21.1 | 0 | 0
1323 | 2022-12-23 22:04 | 4.6 | 19.4 | 25.5 | 20.9 | 0 | 0
1324 | 2022-12-23 22:05 | 4.7 | 19.4 | 25.3 | 20.8 | 0 | 0
1325 | 2022-12-23 22:06 | 4.9 | 19.4 | 25.1 | 20.6 | 0 | 0
1326 | 2022-12-23 22:07 | 4.7 | 19.4 | 25 | 20.5 | 0 | 0
1327 | 2022-12-23 22:08 | 4.7 | 19.4 | 24.8 | 20.4 | 0 | 0
1328 | 2022-12-23 22:09 | 4.7 | 19.4 | 24.7 | 20.2 | 0 | 0
1329 | 2022-12-23 22:10 | 4.6 | 19.4 | 24.5 | 20.1 | 0 | 0
1330 | 2022-12-23 22:11 | 4.8 | 19.4 | 24.3 | 20 | 0 | 0
1331 | 2022-12-23 22:12 | 4.7 | 19.4 | 24.2 | 19.9 | 0 | 0
1332 | 2022-12-23 22:13 | 4.7 | 19.4 | 24 | 19.7 | 0 | 0
1333 | 2022-12-23 22:14 | 4.7 | 19.4 | 23.9 | 19.6 | 0 | 0
1334 | 2022-12-23 22:15 | 4.8 | 19.3 | 23.7 | 19.5 | 0 | 0
1335 | 2022-12-23 22:16 | 4.7 | 19.3 | 23.6 | 19.4 | 0 | 0
1336 | 2022-12-23 22:17 | 4.9 | 19.3 | 23.4 | 19.2 | 0 | 0
1337 | 2022-12-23 22:18 | 4.7 | 19.3 | 23.3 | 19.1 | 0 | 0
1338 | 2022-12-23 22:19 | 4.7 | 19.3 | 23.1 | 19 | 0 | 0
1339 | 2022-12-23 22:20 | 4.6 | 19.3 | 23 | 18.9 | 0 | 0
1340 | 2022-12-23 22:21 | 4.8 | 19.3 | 22.8 | 18.8 | 0 | 0
1341 | 2022-12-23 22:22 | 4.6 | 19.3 | 22.7 | 18.7 | 0 | 0
1342 | 2022-12-23 22:23 | 4.8 | 19.3 | 22.5 | 18.6 | 0 | 0
1343 | 2022-12-23 22:24 | 4.6 | 19.3 | 22.4 | 18.5 | 0 | 0
1344 | 2022-12-23 22:25 | 4.6 | 19.3 | 22.3 | 18.4 | 0 | 0
1345 | 2022-12-23 22:26 | 4.8 | 19.3 | 22.1 | 18.3 | 0 | 0
1346 | 2022-12-23 22:27 | 4.7 | 19.3 | 22 | 18.1 | 0 | 0
1347 | 2022-12-23 22:28 | 4.7 | 19.3 | 21.9 | 18 | 0 | 0
1348 | 2022-12-23 22:29 | 4.8 | 19.3 | 21.7 | 17.9 | 0 | 0
1349 | 2022-12-23 22:30 | 4.7 | 19.4 | 21.6 | 17.8 | 0 | 0
1350 | 2022-12-23 22:31 | 4.7 | 19.3 | 21.5 | 17.7 | 0 | 0
1351 | 2022-12-23 22:32 | 4.7 | 19.3 | 21.4 | 17.6 | 0 | 0
1352 | 2022-12-23 22:33 | 4.7 | 19.3 | 21.2 | 17.5 | 0 | 0
1353 | 2022-12-23 22:34 | 4.8 | 19.2 | 21.1 | 17.4 | 0 | 0
1354 | 2022-12-23 22:35 | 4.7 | 19.3 | 21 | 17.4 | 0 | 0
1355 | 2022-12-23 22:36 | 4.9 | 19.3 | 20.9 | 17.3 | 0 | 0
1356 | 2022-12-23 22:37 | 4.7 | 19.3 | 20.8 | 17.2 | 0 | 0
1357 | 2022-12-23 22:38 | 4.8 | 19.2 | 20.6 | 17.1 | 0 | 0
1358 | 2022-12-23 22:39 | 4.9 | 19.2 | 20.5 | 17 | 0 | 0
1359 | 2022-12-23 22:40 | 4.7 | 19.3 | 20.4 | 16.9 | 0 | 0
1360 | 2022-12-23 22:41 | 4.8 | 19.2 | 20.3 | 16.8 | 0 | 0
1361 | 2022-12-23 22:42 | 4.9 | 19.2 | 20.2 | 16.7 | 0 | 0
1362 | 2022-12-23 22:43 | 4.8 | 19.2 | 20.1 | 16.6 | 0 | 0
1363 | 2022-12-23 22:44 | 4.8 | 19.1 | 20 | 16.5 | 0 | 0
1364 | 2022-12-23 22:45 | 4.9 | 19.2 | 19.9 | 16.5 | 0 | 0
1365 | 2022-12-23 22:46 | 4.9 | 19.2 | 19.8 | 16.4 | 0 | 0
1366 | 2022-12-23 22:47 | 4.9 | 19.1 | 19.7 | 16.3 | 0 | 0
1367 | 2022-12-23 22:48 | 4.9 | 19.1 | 19.6 | 16.2 | 0 | 0
1368 | 2022-12-23 22:49 | 4.9 | 19.2 | 19.5 | 16.1 | 0 | 0
1369 | 2022-12-23 22:50 | 4.9 | 19.2 | 19.4 | 16.1 | 0 | 0
1370 | 2022-12-23 22:51 | 5 | 19.1 | 19.3 | 16 | 0 | 0
1371 | 2022-12-23 22:52 | 4.9 | 19.1 | 19.2 | 15.9 | 0 | 0
1372 | 2022-12-23 22:53 | 4.7 | 19.1 | 19.1 | 15.8 | 0 | 0
1373 | 2022-12-23 22:54 | 5 | 19.1 | 19 | 15.7 | 0 | 0
1374 | 2022-12-23 22:55 | 4.8 | 19.1 | 18.9 | 15.7 | 0 | 0
1375 | 2022-12-23 22:56 | 5 | 19.1 | 18.8 | 15.6 | 0 | 0
1376 | 2022-12-23 22:57 | 4.8 | 19.1 | 18.7 | 15.5 | 0 | 0
1377 | 2022-12-23 22:58 | 4.8 | 19.2 | 18.6 | 15.4 | 0 | 0
1378 | 2022-12-23 22:59 | 5 | 19.1 | 18.5 | 15.4 | 0 | 0
1379 | 2022-12-23 23:00 | 4.8 | 19.1 | 18.4 | 15.3 | 0 | 0
1380 | 2022-12-23 23:01 | 4.9 | 19.1 | 18.3 | 15.2 | 0 | 0
1381 | 2022-12-23 23:02 | 4.8 | 19 | 18.2 | 15.2 | 0 | 0
1382 | 2022-12-23 23:03 | 4.8 | 19.1 | 18.2 | 15.1 | 0 | 0
1383 | 2022-12-23 23:04 | 4.9 | 19.1 | 18.1 | 15 | 0 | 0
1384 | 2022-12-23 23:05 | 4.7 | 19.1 | 18 | 15 | 0 | 0
1385 | 2022-12-23 23:06 | 4.7 | 19.1 | 17.9 | 14.9 | 0 | 0
1386 | 2022-12-23 23:07 | 4.8 | 19.1 | 17.8 | 14.8 | 0 | 0
1387 | 2022-12-23 23:08 | 4.8 | 19.1 | 17.7 | 14.8 | 0 | 0
1388 | 2022-12-23 23:09 | 5 | 19.1 | 17.7 | 14.7 | 0 | 0
1389 | 2022-12-23 23:10 | 4.8 | 19.1 | 17.6 | 14.7 | 0 | 0
1390 | 2022-12-23 23:11 | 4.8 | 19.2 | 17.5 | 14.6 | 0 | 0
1391 | 2022-12-23 23:12 | 4.8 | 19.2 | 17.4 | 14.5 | 0 | 0
1392 | 2022-12-23 23:13 | 4.8 | 19.1 | 17.4 | 14.5 | 0 | 0
1393 | 2022-12-23 23:14 | 4.8 | 19.1 | 17.3 | 14.4 | 0 | 0
1394 | 2022-12-23 23:15 | 5 | 19 | 17.2 | 14.4 | 0 | 0
1395 | 2022-12-23 23:16 | 5.1 | 19 | 17.2 | 14.3 | 0 | 0
1396 | 2022-12-23 23:17 | 5 | 19 | 17.1 | 14.2 | 0 | 0
1397 | 2022-12-23 23:18 | 4.9 | 19 | 17 | 14.2 | 0 | 0
1398 | 2022-12-23 23:19 | 5 | 19 | 17 | 14.1 | 0 | 0
1399 | 2022-12-23 23:20 | 5 | 19 | 16.9 | 14.1 | 0 | 0
1400 | 2022-12-23 23:21 | 5.1 | 19 | 16.8 | 14 | 0 | 0
1401 | 2022-12-23 23:22 | 5 | 18.9 | 16.7 | 14 | 0 | 0
1402 | 2022-12-23 23:23 | 4.9 | 19 | 16.7 | 13.9 | 0 | 0
1403 | 2022-12-23 23:24 | 4.9 | 19 | 16.6 | 13.9 | 0 | 0
1404 | 2022-12-23 23:25 | 5 | 19 | 16.6 | 13.8 | 0 | 0
1405 | 2022-12-23 23:26 | 5 | 19 | 16.5 | 13.8 | 0 | 0
1406 | 2022-12-23 23:27 | 5 | 19 | 16.5 | 13.7 | 0 | 0
1407 | 2022-12-23 23:28 | 5.2 | 19 | 16.4 | 13.7 | 0 | 0
1408 | 2022-12-23 23:29 | 5.1 | 18.9 | 16.4 | 13.6 | 0 | 0
1409 | 2022-12-23 23:30 | 5.2 | 19 | 16.3 | 13.6 | 0 | 0
1410 | 2022-12-23 23:31 | 5.1 | 19 | 16.3 | 13.5 | 0 | 0
1411 | 2022-12-23 23:32 | 5.3 | 18.9 | 16.2 | 13.5 | 0 | 0
1412 | 2022-12-23 23:33 | 5.2 | 18.9 | 16.1 | 13.4 | 0 | 0
1413 | 2022-12-23 23:34 | 5.2 | 18.9 | 16.1 | 13.4 | 0 | 0
1414 | 2022-12-23 23:35 | 5.2 | 18.9 | 16 | 13.3 | 0 | 0
1415 | 2022-12-23 23:36 | 5.1 | 18.9 | 16 | 13.3 | 0 | 0
1416 | 2022-12-23 23:37 | 5.1 | 18.9 | 15.9 | 13.2 | 0 | 0
1417 | 2022-12-23 23:38 | 5.2 | 18.9 | 15.9 | 13.2 | 0 | 0
1418 | 2022-12-23 23:39 | 5.4 | 18.8 | 15.8 | 13.1 | 0 | 0
1419 | 2022-12-23 23:40 | 5.1 | 18.9 | 15.7 | 13.1 | 0 | 0
1420 | 2022-12-23 23:41 | 5.1 | 18.8 | 15.7 | 13.1 | 0 | 0
1421 | 2022-12-23 23:42 | 5.1 | 18.9 | 15.7 | 13 | 0 | 0
1422 | 2022-12-23 23:43 | 5.2 | 18.9 | 15.6 | 13 | 0 | 0
1423 | 2022-12-23 23:44 | 5.2 | 18.9 | 15.6 | 12.9 | 0 | 0
1424 | 2022-12-23 23:45 | 5.1 | 18.8 | 15.6 | 12.9 | 0 | 0
1425 | 2022-12-23 23:46 | 4.9 | 18.8 | 15.5 | 12.8 | 0 | 0
1426 | 2022-12-23 23:47 | 5.3 | 18.9 | 15.5 | 12.8 | 0 | 0
1427 | 2022-12-23 23:48 | 5.5 | 18.9 | 15.5 | 12.8 | 0 | 0
1428 | 2022-12-23 23:49 | 5.5 | 18.8 | 15.5 | 12.7 | 0 | 0
1429 | 2022-12-23 23:50 | 5.4 | 18.8 | 15.4 | 12.7 | 0 | 0
1430 | 2022-12-23 23:51 | 5.2 | 18.8 | 15.4 | 12.7 | 0 | 0
1431 | 2022-12-23 23:52 | 5.3 | 18.9 | 15.3 | 12.6 | 0 | 0
1432 | 2022-12-23 23:53 | 5.2 | 18.8 | 15.3 | 12.6 | 0 | 0
1433 | 2022-12-23 23:54 | 5.3 | 18.8 | 15.3 | 12.5 | 0 | 0
1434 | 2022-12-23 23:55 | 5.1 | 18.9 | 15.2 | 12.5 | 0 | 0
1435 | 2022-12-23 23:56 | 5.1 | 18.8 | 15.2 | 12.5 | 0 | 0
1436 | 2022-12-23 23:57 | 5.3 | 18.9 | 15.2 | 12.4 | 0 | 0
1437 | 2022-12-23 23:58 | 5.1 | 18.8 | 15.1 | 12.4 | 0 | 0
1438 | 2022-12-23 23:59 | 5.3 | 18.8 | 15.1 | 12.4 | 0 | 0
1439 | 2022-12-24 | 5.4 | 18.9 | 15.1 | 12.3 | 0 | 0

## 24-12-2022_WITH HEAT
| Date&time_x | OUTDOOR_TEMP | INDOOR_TEMP | SH_INLET | SH_RETURN | FLOW_FAN_COILS_INDOOR | PYRANOMETER
0 | 2022-12-24 00:01 | 5.3 | 18.8 | 15.1 | 12.3 | 0 | 0
1 | 2022-12-24 00:02 | 5.3 | 18.8 | 15 | 12.3 | 0 | 0
2 | 2022-12-24 00:03 | 5.4 | 18.8 | 15 | 12.2 | 0 | 0
3 | 2022-12-24 00:04 | 5.2 | 18.8 | 15 | 12.2 | 0 | 0
4 | 2022-12-24 00:05 | 5.2 | 18.7 | 15 | 12.2 | 0 | 0
5 | 2022-12-24 00:06 | 5.4 | 18.8 | 15 | 12.1 | 0 | 0
6 | 2022-12-24 00:07 | 5.2 | 18.8 | 14.9 | 12.1 | 0 | 0
7 | 2022-12-24 00:08 | 5.3 | 18.8 | 14.9 | 12.1 | 0 | 0
8 | 2022-12-24 00:09 | 5.4 | 18.8 | 14.9 | 12 | 0 | 0
9 | 2022-12-24 00:10 | 5.2 | 18.8 | 14.8 | 13.4 | 0 | 0
10 | 2022-12-24 00:11 | 5.2 | 18.7 | 14.8 | 13.4 | 0 | 0
11 | 2022-12-24 00:12 | 5.4 | 18.8 | 18.7 | 14.9 | 0 | 0
12 | 2022-12-24 00:13 | 5.2 | 18.7 | 41.2 | 26.1 | 0.862 | 0
13 | 2022-12-24 00:14 | 5.4 | 18.8 | 40.8 | 37.1 | 0.918 | 0
14 | 2022-12-24 00:15 | 5.3 | 18.8 | 40.1 | 37.6 | 0.95 | 0
15 | 2022-12-24 00:16 | 5.2 | 18.7 | 39.9 | 37.4 | 0.949 | 0
16 | 2022-12-24 00:17 | 5.2 | 18.8 | 40.1 | 37.5 | 0.98 | 0
17 | 2022-12-24 00:18 | 5.3 | 18.9 | 40.7 | 37.8 | 0.067 | 0
18 | 2022-12-24 00:19 | 5.3 | 18.9 | 40.5 | 37.5 | 0 | 0
19 | 2022-12-24 00:20 | 5.2 | 19 | 40 | 36.7 | 0 | 0
20 | 2022-12-24 00:21 | 5.3 | 18.9 | 39.6 | 35.8 | 0 | 0
21 | 2022-12-24 00:22 | 5.2 | 18.9 | 39.2 | 35.1 | 0 | 0
22 | 2022-12-24 00:23 | 5.2 | 18.8 | 38.9 | 34.4 | 0 | 0
23 | 2022-12-24 00:24 | 5.3 | 18.8 | 38.5 | 33.8 | 0 | 0
24 | 2022-12-24 00:25 | 5.4 | 18.8 | 38.2 | 33.2 | 0 | 0
25 | 2022-12-24 00:26 | 5.2 | 18.8 | 37.9 | 32.6 | 0 | 0
26 | 2022-12-24 00:27 | 5.3 | 18.8 | 37.5 | 32.1 | 0 | 0
27 | 2022-12-24 00:28 | 5.2 | 18.8 | 37.3 | 31.6 | 0 | 0
28 | 2022-12-24 00:29 | 5.2 | 18.8 | 37 | 31.2 | 0 | 0
29 | 2022-12-24 00:30 | 5.3 | 18.8 | 36.7 | 30.8 | 0 | 0
30 | 2022-12-24 00:31 | 5.5 | 18.7 | 36.4 | 30.3 | 0 | 0
31 | 2022-12-24 00:32 | 5.6 | 18.7 | 36.2 | 29.9 | 0 | 0
32 | 2022-12-24 00:33 | 5.3 | 18.8 | 35.9 | 29.6 | 0 | 0
33 | 2022-12-24 00:34 | 5.2 | 18.7 | 35.7 | 29.2 | 0 | 0
34 | 2022-12-24 00:35 | 5.3 | 18.6 | 35.4 | 28.9 | 0 | 0
35 | 2022-12-24 00:36 | 5.2 | 18.6 | 35.2 | 28.5 | 0 | 0
36 | 2022-12-24 00:37 | 5.4 | 18.6 | 34.9 | 28.2 | 0 | 0
37 | 2022-12-24 00:38 | 5.4 | 18.6 | 34.7 | 27.9 | 0 | 0
38 | 2022-12-24 00:39 | 5.2 | 18.7 | 34.4 | 27.6 | 0 | 0
39 | 2022-12-24 00:40 | 5.2 | 18.7 | 34.2 | 27.3 | 0 | 0
40 | 2022-12-24 00:41 | 5.3 | 18.6 | 34 | 27 | 0 | 0
41 | 2022-12-24 00:42 | 5.6 | 18.6 | 33.7 | 26.7 | 0 | 0
42 | 2022-12-24 00:43 | 5.5 | 18.6 | 33.5 | 26.5 | 0 | 0
43 | 2022-12-24 00:44 | 5.4 | 18.6 | 33.3 | 26.2 | 0 | 0
44 | 2022-12-24 00:45 | 5.5 | 18.6 | 33.1 | 26 | 0 | 0
45 | 2022-12-24 00:46 | 5.4 | 18.5 | 32.9 | 25.7 | 0 | 0
46 | 2022-12-24 00:47 | 5.4 | 18.6 | 32.6 | 25.5 | 0 | 0
47 | 2022-12-24 00:48 | 5.4 | 18.6 | 32.4 | 25.3 | 0 | 0
48 | 2022-12-24 00:49 | 5.2 | 18.6 | 32.2 | 25 | 0 | 0
49 | 2022-12-24 00:50 | 5.3 | 18.6 | 32 | 24.8 | 0 | 0
50 | 2022-12-24 00:51 | 5.3 | 18.6 | 31.8 | 24.6 | 0 | 0
51 | 2022-12-24 00:52 | 5.3 | 18.6 | 31.6 | 24.4 | 0 | 0
52 | 2022-12-24 00:53 | 5.2 | 18.6 | 31.4 | 24.2 | 0 | 0
53 | 2022-12-24 00:54 | 5.3 | 18.6 | 31.1 | 24 | 0 | 0
54 | 2022-12-24 00:55 | 5.3 | 18.6 | 31 | 23.8 | 0 | 0
55 | 2022-12-24 00:56 | 5.3 | 18.6 | 30.8 | 23.6 | 0 | 0
56 | 2022-12-24 00:57 | 5.3 | 18.6 | 30.6 | 23.4 | 0 | 0
57 | 2022-12-24 00:58 | 5.3 | 18.6 | 30.4 | 26.6 | 0 | 0
58 | 2022-12-24 00:59 | 5.2 | 18.6 | 30.2 | 26.1 | 0 | 0
59 | 2022-12-24 01:00 | 5.1 | 18.6 | 36.9 | 28.5 | 0.359 | 0
60 | 2022-12-24 01:01 | 5.1 | 18.6 | 43.5 | 38.4 | 0.973 | 0
61 | 2022-12-24 01:02 | 5.2 | 18.6 | 43 | 40.4 | 0.982 | 0
62 | 2022-12-24 01:03 | 5.2 | 18.6 | 43.4 | 40.2 | 0.985 | 0
63 | 2022-12-24 01:04 | 5.2 | 18.6 | 43.8 | 40.8 | 0.988 | 0
64 | 2022-12-24 01:05 | 5.2 | 18.7 | 44.3 | 41 | 0.986 | 0
65 | 2022-12-24 01:06 | 5.2 | 18.7 | 44.1 | 40.7 | 0 | 0
66 | 2022-12-24 01:07 | 5.1 | 18.8 | 43.6 | 39.9 | 0 | 0
67 | 2022-12-24 01:08 | 5.1 | 18.7 | 43.2 | 39 | 0 | 0
68 | 2022-12-24 01:09 | 5.2 | 18.7 | 42.8 | 38.3 | 0 | 0
69 | 2022-12-24 01:10 | 5.1 | 18.7 | 42.4 | 37.6 | 0 | 0
70 | 2022-12-24 01:11 | 5.2 | 18.7 | 42 | 36.9 | 0 | 0
71 | 2022-12-24 01:12 | 5.1 | 18.6 | 41.7 | 36.3 | 0 | 0
72 | 2022-12-24 01:13 | 5.2 | 18.6 | 41.3 | 35.7 | 0 | 0
73 | 2022-12-24 01:14 | 5.1 | 18.6 | 41 | 35.2 | 0 | 0
74 | 2022-12-24 01:15 | 5.2 | 18.6 | 40.6 | 34.6 | 0 | 0
75 | 2022-12-24 01:16 | 5.1 | 18.6 | 40.3 | 34.1 | 0 | 0
76 | 2022-12-24 01:17 | 5 | 18.6 | 40 | 33.7 | 0 | 0
77 | 2022-12-24 01:18 | 5 | 18.6 | 39.7 | 33.2 | 0 | 0
78 | 2022-12-24 01:19 | 4.9 | 18.6 | 39.4 | 32.8 | 0 | 0
79 | 2022-12-24 01:20 | 4.8 | 18.6 | 39.2 | 32.4 | 0 | 0
80 | 2022-12-24 01:21 | 5.1 | 18.6 | 38.9 | 32 | 0 | 0
81 | 2022-12-24 01:22 | 5.1 | 18.5 | 38.6 | 31.6 | 0 | 0
82 | 2022-12-24 01:23 | 5 | 18.5 | 38.3 | 31.2 | 0 | 0
83 | 2022-12-24 01:24 | 4.9 | 18.5 | 38.1 | 30.9 | 0 | 0
84 | 2022-12-24 01:25 | 4.9 | 18.6 | 37.8 | 30.5 | 0 | 0
85 | 2022-12-24 01:26 | 4.8 | 18.5 | 37.5 | 30.2 | 0 | 0
86 | 2022-12-24 01:27 | 4.9 | 18.6 | 37.3 | 29.8 | 0 | 0
87 | 2022-12-24 01:28 | 4.8 | 18.5 | 37 | 29.5 | 0 | 0
88 | 2022-12-24 01:29 | 4.7 | 18.5 | 36.7 | 29.2 | 0 | 0
89 | 2022-12-24 01:30 | 4.9 | 18.5 | 36.5 | 28.9 | 0 | 0
90 | 2022-12-24 01:31 | 4.7 | 18.5 | 36.2 | 28.6 | 0 | 0
91 | 2022-12-24 01:32 | 4.8 | 18.5 | 36 | 28.3 | 0 | 0
92 | 2022-12-24 01:33 | 4.8 | 18.5 | 35.7 | 28 | 0 | 0
93 | 2022-12-24 01:34 | 4.8 | 18.5 | 35.5 | 27.8 | 0 | 0
94 | 2022-12-24 01:35 | 4.9 | 18.5 | 35.2 | 27.5 | 0 | 0
95 | 2022-12-24 01:36 | 4.8 | 18.5 | 35 | 27.2 | 0 | 0
96 | 2022-12-24 01:37 | 4.8 | 18.5 | 34.7 | 27.8 | 0 | 0
97 | 2022-12-24 01:38 | 4.8 | 18.5 | 34.5 | 30.9 | 0 | 0
98 | 2022-12-24 01:39 | 4.7 | 18.4 | 34.3 | 30.7 | 0 | 0
99 | 2022-12-24 01:40 | 4.8 | 18.4 | 42.9 | 29 | 0.9 | 0
100 | 2022-12-24 01:41 | 4.9 | 18.4 | 42.7 | 39.8 | 0.984 | 0
101 | 2022-12-24 01:42 | 4.9 | 18.4 | 42.2 | 39.5 | 0.982 | 0
102 | 2022-12-24 01:43 | 4.8 | 18.5 | 42.3 | 39.6 | 0.982 | 0
103 | 2022-12-24 01:44 | 4.9 | 18.5 | 42.1 | 39.7 | 0.984 | 0
104 | 2022-12-24 01:45 | 4.7 | 18.6 | 42 | 39.5 | 0 | 0
105 | 2022-12-24 01:46 | 4.7 | 18.6 | 41.8 | 39.1 | 0 | 0
106 | 2022-12-24 01:47 | 4.7 | 18.7 | 41.4 | 38.3 | 0 | 0
107 | 2022-12-24 01:48 | 4.7 | 18.7 | 41.1 | 37.6 | 0 | 0
108 | 2022-12-24 01:49 | 4.7 | 18.6 | 40.7 | 36.9 | 0 | 0
109 | 2022-12-24 01:50 | 4.6 | 18.5 | 40.4 | 36.3 | 0 | 0
110 | 2022-12-24 01:51 | 4.6 | 18.5 | 40.1 | 35.7 | 0 | 0
111 | 2022-12-24 01:52 | 4.6 | 18.5 | 39.8 | 35.1 | 0 | 0
112 | 2022-12-24 01:53 | 4.5 | 18.5 | 39.5 | 34.6 | 0 | 0
113 | 2022-12-24 01:54 | 4.7 | 18.4 | 39.2 | 34.1 | 0 | 0
114 | 2022-12-24 01:55 | 4.5 | 18.5 | 38.9 | 33.6 | 0 | 0
115 | 2022-12-24 01:56 | 4.5 | 18.4 | 38.6 | 33.2 | 0 | 0
116 | 2022-12-24 01:57 | 4.4 | 18.4 | 38.3 | 32.7 | 0 | 0
117 | 2022-12-24 01:58 | 4.6 | 18.4 | 38 | 32.3 | 0 | 0
118 | 2022-12-24 01:59 | 4.6 | 18.4 | 37.7 | 31.9 | 0 | 0
119 | 2022-12-24 02:00 | 4.6 | 18.5 | 37.5 | 31.5 | 0 | 0
120 | 2022-12-24 02:01 | 4.5 | 18.4 | 37.2 | 31.1 | 0 | 0
121 | 2022-12-24 02:02 | 4.5 | 18.4 | 36.9 | 30.7 | 0 | 0
122 | 2022-12-24 02:03 | 4.6 | 18.4 | 36.7 | 30.4 | 0 | 0
123 | 2022-12-24 02:04 | 4.4 | 18.4 | 36.4 | 30 | 0 | 0
124 | 2022-12-24 02:05 | 4.6 | 18.4 | 36.2 | 29.7 | 0 | 0
125 | 2022-12-24 02:06 | 4.5 | 18.4 | 35.9 | 29.4 | 0 | 0
126 | 2022-12-24 02:07 | 4.5 | 18.4 | 35.7 | 29.1 | 0 | 0
127 | 2022-12-24 02:08 | 4.4 | 18.5 | 35.4 | 28.7 | 0 | 0
128 | 2022-12-24 02:09 | 4.4 | 18.4 | 35.2 | 28.4 | 0 | 0
129 | 2022-12-24 02:10 | 4.3 | 18.4 | 34.9 | 28.2 | 0 | 0
130 | 2022-12-24 02:11 | 4.3 | 18.4 | 34.7 | 32 | 0.014 | 0
131 | 2022-12-24 02:12 | 4.3 | 18.3 | 34.4 | 31.9 | 0 | 0
132 | 2022-12-24 02:13 | 4.3 | 18.4 | 40.7 | 30.3 | 0.785 | 0
133 | 2022-12-24 02:14 | 4.5 | 18.3 | 40.9 | 37.8 | 0.955 | 0
134 | 2022-12-24 02:15 | 4.3 | 18.3 | 40 | 37.8 | 0.954 | 0
135 | 2022-12-24 02:16 | 4.2 | 18.4 | 40.2 | 37.6 | 0.977 | 0
136 | 2022-12-24 02:17 | 4.4 | 18.4 | 40.1 | 37.8 | 0.977 | 0
137 | 2022-12-24 02:18 | 4.4 | 18.5 | 40 | 37.7 | 0.975 | 0
138 | 2022-12-24 02:19 | 4.4 | 18.5 | 39.9 | 37.6 | 0 | 0
139 | 2022-12-24 02:20 | 4.4 | 18.6 | 39.6 | 37.1 | 0 | 0
140 | 2022-12-24 02:21 | 4.3 | 18.6 | 39.3 | 36.5 | 0 | 0
141 | 2022-12-24 02:22 | 4.2 | 18.6 | 39 | 35.8 | 0 | 0
142 | 2022-12-24 02:23 | 4.2 | 18.5 | 38.7 | 35.2 | 0 | 0
143 | 2022-12-24 02:24 | 4.3 | 18.5 | 38.4 | 34.6 | 0 | 0
144 | 2022-12-24 02:25 | 4.3 | 18.5 | 38.1 | 34.1 | 0 | 0
145 | 2022-12-24 02:26 | 4.1 | 18.5 | 37.8 | 33.6 | 0 | 0
146 | 2022-12-24 02:27 | 4.4 | 18.4 | 37.5 | 33.1 | 0 | 0
147 | 2022-12-24 02:28 | 4.4 | 18.4 | 37.2 | 32.6 | 0 | 0
148 | 2022-12-24 02:29 | 4.2 | 18.4 | 37 | 32.2 | 0 | 0
149 | 2022-12-24 02:30 | 4.3 | 18.4 | 36.7 | 31.7 | 0 | 0
150 | 2022-12-24 02:31 | 4.1 | 18.4 | 36.4 | 31.3 | 0 | 0
151 | 2022-12-24 02:32 | 4.1 | 18.4 | 36.2 | 30.9 | 0 | 0
152 | 2022-12-24 02:33 | 4.2 | 18.3 | 35.9 | 30.5 | 0 | 0
153 | 2022-12-24 02:34 | 4 | 18.4 | 35.6 | 30.2 | 0 | 0
154 | 2022-12-24 02:35 | 4 | 18.4 | 35.4 | 29.8 | 0 | 0
155 | 2022-12-24 02:36 | 4.1 | 18.3 | 35.1 | 29.5 | 0 | 0
156 | 2022-12-24 02:37 | 4 | 18.3 | 34.9 | 29.1 | 0 | 0
157 | 2022-12-24 02:38 | 4.2 | 18.3 | 34.6 | 28.8 | 0 | 0
158 | 2022-12-24 02:39 | 4 | 18.3 | 34.4 | 28.5 | 0 | 0
159 | 2022-12-24 02:40 | 4.1 | 18.3 | 34.1 | 28.2 | 0 | 0
160 | 2022-12-24 02:41 | 4 | 18.3 | 33.9 | 31.8 | 0 | 0
161 | 2022-12-24 02:42 | 4.3 | 18.3 | 33.7 | 31.4 | 0 | 0
162 | 2022-12-24 02:43 | 4.1 | 18.2 | 44.1 | 30.3 | 0.829 | 0
163 | 2022-12-24 02:44 | 4.2 | 18.3 | 44.7 | 40.9 | 0.947 | 0
164 | 2022-12-24 02:45 | 4.1 | 18.3 | 44.3 | 41.3 | 0.935 | 0
165 | 2022-12-24 02:46 | 4.1 | 18.3 | 45 | 41.6 | 0.988 | 0
166 | 2022-12-24 02:47 | 4.2 | 18.3 | 45.3 | 42.2 | 0.986 | 0
167 | 2022-12-24 02:48 | 4.1 | 18.5 | 45.3 | 42 | 0 | 0
168 | 2022-12-24 02:49 | 4.1 | 18.5 | 44.8 | 41.2 | 0 | 0
169 | 2022-12-24 02:50 | 4.2 | 18.5 | 44.4 | 40.3 | 0 | 0
170 | 2022-12-24 02:51 | 4.2 | 18.5 | 44 | 39.6 | 0 | 0
171 | 2022-12-24 02:52 | 4.1 | 18.4 | 43.6 | 38.9 | 0 | 0
172 | 2022-12-24 02:53 | 4 | 18.4 | 43.2 | 38.2 | 0 | 0
173 | 2022-12-24 02:54 | 4.1 | 18.3 | 42.8 | 37.6 | 0 | 0
174 | 2022-12-24 02:55 | 4 | 18.3 | 42.4 | 37 | 0 | 0
175 | 2022-12-24 02:56 | 4 | 18.3 | 42.1 | 36.4 | 0 | 0
176 | 2022-12-24 02:57 | 4 | 18.3 | 41.8 | 35.9 | 0 | 0
177 | 2022-12-24 02:58 | 4 | 18.3 | 41.4 | 35.4 | 0 | 0
178 | 2022-12-24 02:59 | 4 | 18.3 | 41.1 | 34.9 | 0 | 0
179 | 2022-12-24 03:00 | 3.8 | 18.3 | 40.8 | 34.4 | 0 | 0
180 | 2022-12-24 03:01 | 4 | 18.3 | 40.5 | 33.9 | 0 | 0
181 | 2022-12-24 03:02 | 3.9 | 18.3 | 40.1 | 36.1 | 0 | 0
182 | 2022-12-24 03:03 | 4.1 | 18.2 | 39.8 | 35.5 | 0 | 0
183 | 2022-12-24 03:04 | 3.9 | 18.3 | 40.2 | 37.5 | 0.202 | 0
184 | 2022-12-24 03:05 | 4.1 | 18.3 | 44.8 | 22.5 | 1.058 | 0
185 | 2022-12-24 03:06 | 3.9 | 18.3 | 44.3 | 41.8 | 1.097 | 0
186 | 2022-12-24 03:07 | 3.9 | 18.3 | 44.6 | 41.8 | 1.098 | 0
187 | 2022-12-24 03:08 | 4.2 | 18.3 | 44.2 | 42.4 | 1.1 | 0
188 | 2022-12-24 03:09 | 4.2 | 18.2 | 43.7 | 42 | 1.1 | 0
189 | 2022-12-24 03:10 | 4 | 18.2 | 43.6 | 41.6 | 1.096 | 0
190 | 2022-12-24 03:11 | 4.1 | 18.3 | 43.4 | 41.1 | 1.229 | 0
191 | 2022-12-24 03:12 | 4.1 | 18.3 | 43.3 | 40.3 | 1.636 | 0
192 | 2022-12-24 03:13 | 4 | 18.3 | 43.2 | 40.4 | 1.637 | 0
193 | 2022-12-24 03:14 | 4 | 18.4 | 43 | 40.4 | 1.636 | 0
194 | 2022-12-24 03:15 | 4 | 18.4 | 43 | 40.3 | 1.649 | 0
195 | 2022-12-24 03:16 | 4.2 | 18.6 | 43 | 40.3 | 1.645 | 0
196 | 2022-12-24 03:17 | 4.2 | 18.7 | 42.9 | 41.3 | 1.641 | 0
197 | 2022-12-24 03:18 | 4 | 18.7 | 42.9 | 41.4 | 1.647 | 0
198 | 2022-12-24 03:19 | 4 | 18.8 | 43 | 41.4 | 1.64 | 0
199 | 2022-12-24 03:20 | 4.2 | 18.7 | 43 | 41.5 | 1.598 | 0
200 | 2022-12-24 03:21 | 4.1 | 18.7 | 43 | 41.1 | 1.097 | 0
201 | 2022-12-24 03:22 | 4 | 18.6 | 42.9 | 41 | 1.094 | 0
202 | 2022-12-24 03:23 | 4 | 18.6 | 42.8 | 40.9 | 1.091 | 0
203 | 2022-12-24 03:24 | 4.1 | 18.5 | 42.7 | 40.8 | 1.098 | 0
204 | 2022-12-24 03:25 | 4 | 18.5 | 42.5 | 40.7 | 1.091 | 0
205 | 2022-12-24 03:26 | 4.2 | 18.5 | 42.3 | 40.6 | 1.089 | 0
206 | 2022-12-24 03:27 | 4 | 18.5 | 42.2 | 40.4 | 1.094 | 0
207 | 2022-12-24 03:28 | 4 | 18.4 | 42.1 | 40.2 | 0 | 0
208 | 2022-12-24 03:29 | 4.2 | 18.4 | 41.8 | 39.6 | 0 | 0
209 | 2022-12-24 03:30 | 4 | 18.4 | 41.5 | 38.9 | 0 | 0
210 | 2022-12-24 03:31 | 4 | 18.4 | 41.2 | 38.3 | 0 | 0
211 | 2022-12-24 03:32 | 4.1 | 18.4 | 40.9 | 37.6 | 0 | 0
212 | 2022-12-24 03:33 | 4.1 | 18.4 | 40.6 | 37 | 0 | 0
213 | 2022-12-24 03:34 | 4 | 18.4 | 40.3 | 36.4 | 0 | 0
214 | 2022-12-24 03:35 | 4 | 18.3 | 40 | 35.9 | 0 | 0
215 | 2022-12-24 03:36 | 4.1 | 18.3 | 39.7 | 35.3 | 0 | 0
216 | 2022-12-24 03:37 | 4 | 18.3 | 39.4 | 34.8 | 0 | 0
217 | 2022-12-24 03:38 | 4.1 | 18.3 | 39.1 | 34.3 | 0 | 0
218 | 2022-12-24 03:39 | 4.2 | 18.3 | 38.8 | 33.8 | 0 | 0
219 | 2022-12-24 03:40 | 4.1 | 18.3 | 38.5 | 36.7 | 0.02 | 0
220 | 2022-12-24 03:41 | 4 | 18.3 | 38.2 | 36.8 | 0 | 0
221 | 2022-12-24 03:42 | 4.2 | 18.3 | 41.2 | 31.9 | 0.818 | 0
222 | 2022-12-24 03:43 | 4 | 18.3 | 41.3 | 38.4 | 0.951 | 0
223 | 2022-12-24 03:44 | 4.1 | 18.3 | 40.8 | 37.8 | 1.381 | 0
224 | 2022-12-24 03:45 | 4.1 | 18.3 | 40.6 | 37.6 | 1.571 | 0
225 | 2022-12-24 03:46 | 4.2 | 18.3 | 40.5 | 38.1 | 1.573 | 0
226 | 2022-12-24 03:47 | 4 | 18.4 | 40.2 | 38 | 1.579 | 0
227 | 2022-12-24 03:48 | 4 | 18.5 | 40.3 | 38.9 | 1.577 | 0
228 | 2022-12-24 03:49 | 4.1 | 18.5 | 40.4 | 39.1 | 1.57 | 0
229 | 2022-12-24 03:50 | 4.1 | 18.6 | 40.4 | 39.2 | 1.575 | 0
230 | 2022-12-24 03:51 | 4.2 | 18.5 | 40.5 | 39.2 | 1.507 | 0
231 | 2022-12-24 03:52 | 4.2 | 18.5 | 40.5 | 38.8 | 0.986 | 0
232 | 2022-12-24 03:53 | 4.1 | 18.4 | 40.4 | 38.8 | 0.976 | 0
233 | 2022-12-24 03:54 | 4.1 | 18.3 | 40.3 | 38.7 | 0.979 | 0
234 | 2022-12-24 03:55 | 4.1 | 18.4 | 40.2 | 38.7 | 0.976 | 0
235 | 2022-12-24 03:56 | 4.1 | 18.3 | 40.1 | 38.5 | 0.977 | 0
236 | 2022-12-24 03:57 | 4.2 | 18.3 | 40 | 38.4 | 0.972 | 0
237 | 2022-12-24 03:58 | 4.1 | 18.3 | 39.8 | 38.4 | 0.974 | 0
238 | 2022-12-24 03:59 | 4.2 | 18.3 | 39.8 | 38.2 | 0.974 | 0
239 | 2022-12-24 04:00 | 4 | 18.2 | 39.6 | 38.2 | 0.974 | 0
240 | 2022-12-24 04:01 | 4.1 | 18.3 | 39.6 | 38.1 | 0.975 | 0
241 | 2022-12-24 04:02 | 4.1 | 18.3 | 39.5 | 38 | 0.974 | 0
242 | 2022-12-24 04:03 | 4.2 | 18.3 | 39.4 | 37.9 | 0.975 | 0
243 | 2022-12-24 04:04 | 4.2 | 18.3 | 39.3 | 37.8 | 0.974 | 0
244 | 2022-12-24 04:05 | 4 | 18.2 | 39.2 | 37.7 | 0 | 0
245 | 2022-12-24 04:06 | 4.1 | 18.3 | 39 | 37.3 | 0 | 0
246 | 2022-12-24 04:07 | 4.2 | 18.3 | 38.7 | 36.7 | 0 | 0
247 | 2022-12-24 04:08 | 4.1 | 18.2 | 39 | 36.7 | 0.961 | 0
248 | 2022-12-24 04:09 | 4.1 | 18.3 | 38.9 | 38.4 | 0.535 | 0
249 | 2022-12-24 04:10 | 4.1 | 18.2 | 38.8 | 33 | 0.829 | 0
250 | 2022-12-24 04:11 | 4.2 | 18.2 | 38.7 | 36.3 | 0.979 | 0
251 | 2022-12-24 04:12 | 4.3 | 18.2 | 38.6 | 36.4 | 0.977 | 0
252 | 2022-12-24 04:13 | 4.1 | 18.2 | 38.5 | 36.4 | 0.976 | 0
253 | 2022-12-24 04:14 | 4.2 | 18.2 | 38.3 | 36.3 | 0.976 | 0
254 | 2022-12-24 04:15 | 4.2 | 18.3 | 38.2 | 36.1 | 0.978 | 0
255 | 2022-12-24 04:16 | 4.3 | 18.4 | 38.1 | 36 | 0.979 | 0
256 | 2022-12-24 04:17 | 4.2 | 18.5 | 38 | 35.8 | 0 | 0
257 | 2022-12-24 04:18 | 4.3 | 18.5 | 37.7 | 35.3 | 0 | 0
258 | 2022-12-24 04:19 | 4.1 | 18.5 | 37.4 | 34.7 | 0 | 0
259 | 2022-12-24 04:20 | 4.2 | 18.4 | 37.2 | 34.2 | 0 | 0
260 | 2022-12-24 04:21 | 4.4 | 18.3 | 36.9 | 33.6 | 0 | 0
261 | 2022-12-24 04:22 | 4.2 | 18.3 | 36.6 | 33.1 | 0 | 0
262 | 2022-12-24 04:23 | 4.3 | 18.3 | 36.3 | 32.6 | 0 | 0
263 | 2022-12-24 04:24 | 4.3 | 18.2 | 36.1 | 32.1 | 0 | 0
264 | 2022-12-24 04:25 | 4.2 | 18.2 | 35.8 | 31.7 | 0 | 0
265 | 2022-12-24 04:26 | 4.2 | 18.2 | 35.5 | 31.2 | 0 | 0
266 | 2022-12-24 04:27 | 4.2 | 18.2 | 35.2 | 30.8 | 0 | 0
267 | 2022-12-24 04:28 | 4 | 18.2 | 35 | 30.4 | 0 | 0
268 | 2022-12-24 04:29 | 4.1 | 18.1 | 34.7 | 30.1 | 0 | 0
269 | 2022-12-24 04:30 | 4.1 | 18.1 | 34.5 | 29.7 | 0 | 0
270 | 2022-12-24 04:31 | 4 | 18.2 | 34.2 | 29.3 | 0 | 0
271 | 2022-12-24 04:32 | 4.2 | 18.1 | 34 | 29 | 0 | 0
272 | 2022-12-24 04:33 | 3.9 | 18.2 | 33.7 | 28.7 | 0 | 0
273 | 2022-12-24 04:34 | 4.1 | 18.1 | 33.5 | 29.3 | 0 | 0
274 | 2022-12-24 04:35 | 4.2 | 18 | 33.2 | 31.7 | 0.01 | 0
275 | 2022-12-24 04:36 | 4.1 | 18.1 | 34.1 | 32.3 | 0.14 | 0
276 | 2022-12-24 04:37 | 3.9 | 18.1 | 38.5 | 29.9 | 0.36 | 0
277 | 2022-12-24 04:38 | 3.8 | 18.1 | 39.1 | 33.5 | 0.368 | 0
278 | 2022-12-24 04:39 | 3.9 | 18.1 | 39.4 | 33.3 | 0.681 | 0
279 | 2022-12-24 04:40 | 4 | 18 | 38.9 | 36.4 | 0.938 | 0
280 | 2022-12-24 04:41 | 3.9 | 18.1 | 39.3 | 36.5 | 0.944 | 0
281 | 2022-12-24 04:42 | 4 | 18.2 | 39.8 | 33.8 | 1.543 | 0
282 | 2022-12-24 04:43 | 3.9 | 18.3 | 40.4 | 37 | 1.636 | 0
283 | 2022-12-24 04:44 | 4 | 18.4 | 40.9 | 39.1 | 1.644 | 0
284 | 2022-12-24 04:45 | 3.9 | 18.4 | 41.3 | 39.6 | 1.639 | 0
285 | 2022-12-24 04:46 | 4 | 18.4 | 41.9 | 40.1 | 1.637 | 0
286 | 2022-12-24 04:47 | 3.9 | 18.4 | 42.2 | 40.5 | 1.526 | 0
287 | 2022-12-24 04:48 | 3.9 | 18.3 | 42.1 | 40.3 | 1.099 | 0
288 | 2022-12-24 04:49 | 3.8 | 18.3 | 42.1 | 40.2 | 1.089 | 0
289 | 2022-12-24 04:50 | 4 | 18.3 | 41.9 | 40.2 | 1.092 | 0
290 | 2022-12-24 04:51 | 3.9 | 18.2 | 41.8 | 40 | 1.09 | 0
291 | 2022-12-24 04:52 | 3.9 | 18.2 | 41.6 | 39.9 | 1.089 | 0
292 | 2022-12-24 04:53 | 3.9 | 18.2 | 41.5 | 39.8 | 1.092 | 0
293 | 2022-12-24 04:54 | 4.1 | 18.3 | 41.4 | 39.7 | 1.091 | 0
294 | 2022-12-24 04:55 | 4 | 18.2 | 41.3 | 39.6 | 1.094 | 0
295 | 2022-12-24 04:56 | 3.9 | 18.2 | 41.2 | 39.5 | 1.088 | 0
296 | 2022-12-24 04:57 | 3.9 | 18.2 | 41.1 | 39.4 | 1.088 | 0
297 | 2022-12-24 04:58 | 4.1 | 18.2 | 40.9 | 39.2 | 1.091 | 0
298 | 2022-12-24 04:59 | 4 | 18.2 | 40.8 | 39.1 | 1.089 | 0
299 | 2022-12-24 05:00 | 4 | 18.1 | 40.7 | 39 | 1.087 | 0
300 | 2022-12-24 05:01 | 3.9 | 18.2 | 40.7 | 38.9 | 1.088 | 0
301 | 2022-12-24 05:02 | 4 | 18.2 | 40.5 | 38.9 | 1.091 | 0
302 | 2022-12-24 05:03 | 3.9 | 18.1 | 40.4 | 38.7 | 1.088 | 0
303 | 2022-12-24 05:04 | 3.9 | 18.3 | 40.7 | 37.5 | 1.543 | 0
304 | 2022-12-24 05:05 | 4.2 | 18.1 | 41 | 38.2 | 1.638 | 0
305 | 2022-12-24 05:06 | 4 | 18.3 | 41.2 | 38.5 | 1.641 | 0
306 | 2022-12-24 05:07 | 4 | 18.3 | 41.4 | 38.6 | 1.638 | 0
307 | 2022-12-24 05:08 | 4 | 18.4 | 41.3 | 38.9 | 1.634 | 0
308 | 2022-12-24 05:09 | 3.9 | 18.4 | 41.2 | 38.7 | 1.636 | 0
309 | 2022-12-24 05:10 | 4 | 18.5 | 41 | 38.6 | 1.633 | 0
310 | 2022-12-24 05:11 | 4.2 | 18.6 | 40.8 | 39.5 | 1.638 | 0
311 | 2022-12-24 05:12 | 4.2 | 18.7 | 40.7 | 39.4 | 0.008 | 0
312 | 2022-12-24 05:13 | 4.1 | 18.7 | 40.6 | 39.2 | 0 | 0
313 | 2022-12-24 05:14 | 4 | 18.5 | 40.3 | 38.5 | 0 | 0
314 | 2022-12-24 05:15 | 4.1 | 18.5 | 40 | 37.9 | 0 | 0
315 | 2022-12-24 05:16 | 4.1 | 18.4 | 39.7 | 37.3 | 0 | 0
316 | 2022-12-24 05:17 | 4.2 | 18.4 | 39.4 | 36.7 | 0 | 0
317 | 2022-12-24 05:18 | 4.1 | 18.4 | 39.1 | 36.1 | 0 | 0
318 | 2022-12-24 05:19 | 4.1 | 18.3 | 39.4 | 37.6 | 0.024 | 0
319 | 2022-12-24 05:20 | 4.1 | 18.3 | 39.5 | 38.3 | 0.021 | 0
320 | 2022-12-24 05:21 | 4.1 | 18.2 | 39.2 | 38.2 | 0 | 0
321 | 2022-12-24 05:22 | 4.3 | 18.3 | 40 | 37.1 | 0.661 | 0
322 | 2022-12-24 05:23 | 4.1 | 18.2 | 40.2 | 36.8 | 0.978 | 0
323 | 2022-12-24 05:24 | 4.1 | 18.1 | 39.6 | 38.3 | 0.975 | 0
324 | 2022-12-24 05:25 | 4.2 | 18.1 | 39.8 | 38 | 0.977 | 0
325 | 2022-12-24 05:26 | 4.4 | 18.2 | 39.7 | 38.2 | 0.974 | 0
326 | 2022-12-24 05:27 | 4.2 | 18.2 | 39.6 | 38.1 | 0.973 | 0
327 | 2022-12-24 05:28 | 4.1 | 18.1 | 39.6 | 38 | 0.978 | 0
328 | 2022-12-24 05:29 | 4.3 | 18.1 | 39.5 | 38 | 0.974 | 0
329 | 2022-12-24 05:30 | 4.3 | 18.1 | 39.4 | 37.9 | 0.977 | 0
330 | 2022-12-24 05:31 | 4.3 | 18.1 | 39.4 | 37.9 | 0.972 | 0
331 | 2022-12-24 05:32 | 4 | 18.1 | 39.3 | 34.7 | 1.362 | 0
332 | 2022-12-24 05:33 | 4 | 18.1 | 39.1 | 36.8 | 1.576 | 0
333 | 2022-12-24 05:34 | 4.3 | 18.1 | 39.3 | 36.8 | 1.569 | 0
334 | 2022-12-24 05:35 | 4.4 | 18.1 | 39.6 | 37.1 | 1.574 | 0
335 | 2022-12-24 05:36 | 4.3 | 18.1 | 39.9 | 37.4 | 1.576 | 0
336 | 2022-12-24 05:37 | 4.2 | 18.2 | 40.2 | 37.6 | 1.576 | 0
337 | 2022-12-24 05:38 | 4.2 | 18.3 | 40.4 | 37.9 | 1.571 | 0
338 | 2022-12-24 05:39 | 4.2 | 18.4 | 40.8 | 39.2 | 1.578 | 0
339 | 2022-12-24 05:40 | 4.2 | 18.4 | 41.1 | 39.6 | 1.58 | 0
340 | 2022-12-24 05:41 | 4.4 | 18.4 | 41.6 | 40.1 | 1.578 | 0
341 | 2022-12-24 05:42 | 4.3 | 18.3 | 42.1 | 40.4 | 1.539 | 0
342 | 2022-12-24 05:43 | 4.3 | 18.2 | 42.5 | 40.4 | 0.994 | 0
343 | 2022-12-24 05:44 | 4.4 | 18.3 | 42.8 | 40.7 | 0.973 | 0
344 | 2022-12-24 05:45 | 4.4 | 18.3 | 42.8 | 40.5 | 0 | 0
345 | 2022-12-24 05:46 | 4.3 | 18.2 | 42.4 | 39.9 | 0 | 0
346 | 2022-12-24 05:47 | 4.5 | 18.1 | 42 | 39.2 | 0 | 0
347 | 2022-12-24 05:48 | 4.4 | 18.1 | 41.7 | 38.6 | 0 | 0
348 | 2022-12-24 05:49 | 4.2 | 18 | 41.4 | 37.9 | 0 | 0
349 | 2022-12-24 05:50 | 4.2 | 18.1 | 41 | 37.4 | 0 | 0
350 | 2022-12-24 05:51 | 4.1 | 18.1 | 40.7 | 36.8 | 0 | 0
351 | 2022-12-24 05:52 | 4.2 | 18.1 | 40.4 | 36.3 | 0 | 0
352 | 2022-12-24 05:53 | 4.2 | 18.1 | 40 | 35.8 | 0 | 0
353 | 2022-12-24 05:54 | 4.1 | 18 | 39.7 | 35.3 | 0 | 0
354 | 2022-12-24 05:55 | 4.2 | 18 | 39.4 | 34.8 | 0 | 0
355 | 2022-12-24 05:56 | 4.3 | 18 | 39.1 | 37.2 | 0.01 | 0
356 | 2022-12-24 05:57 | 4.2 | 18.1 | 38.9 | 37.9 | 0.011 | 0
357 | 2022-12-24 05:58 | 4.2 | 18 | 43.1 | 34.9 | 0.917 | 0
358 | 2022-12-24 05:59 | 4.4 | 18 | 42.6 | 40.2 | 0.984 | 0
359 | 2022-12-24 06:00 | 4.2 | 18.1 | 42.3 | 39.6 | 0.982 | 0
360 | 2022-12-24 06:01 | 4.4 | 18 | 42.8 | 39.9 | 0.986 | 0
361 | 2022-12-24 06:02 | 4.3 | 18.1 | 42.7 | 40.1 | 0.98 | 0
362 | 2022-12-24 06:03 | 4.4 | 18.2 | 42.6 | 40 | 0 | 0
363 | 2022-12-24 06:04 | 4.1 | 18.4 | 42.6 | 39.7 | 0 | 0
364 | 2022-12-24 06:05 | 4.4 | 18.2 | 42.7 | 42.2 | 0.984 | 0
365 | 2022-12-24 06:06 | 4.3 | 18.2 | 42.4 | 42 | 0.976 | 0
366 | 2022-12-24 06:07 | 4.3 | 18.2 | 42 | 33.2 | 1.291 | 0
367 | 2022-12-24 06:08 | 4.2 | 18.2 | 42.1 | 39.9 | 1.091 | 0
368 | 2022-12-24 06:09 | 4.3 | 18.2 | 42.1 | 40.1 | 1.097 | 0
369 | 2022-12-24 06:10 | 4.2 | 18.1 | 41.6 | 40.2 | 1.094 | 0
370 | 2022-12-24 06:11 | 4.3 | 18.2 | 41.2 | 39.7 | 1.091 | 0
371 | 2022-12-24 06:12 | 4.2 | 18 | 41.2 | 39.4 | 1.097 | 0
372 | 2022-12-24 06:13 | 4.4 | 18.1 | 41.2 | 39.4 | 1.094 | 0
373 | 2022-12-24 06:14 | 4.2 | 18.1 | 41.1 | 39.4 | 1.093 | 0
374 | 2022-12-24 06:15 | 4.2 | 18.1 | 40.9 | 39.2 | 1.091 | 0
375 | 2022-12-24 06:16 | 4.2 | 18 | 40.9 | 39.1 | 1.092 | 0
376 | 2022-12-24 06:17 | 4.1 | 18.1 | 40.8 | 39.1 | 1.092 | 0
377 | 2022-12-24 06:18 | 4.3 | 18 | 40.7 | 39 | 1.095 | 0
378 | 2022-12-24 06:19 | 4.2 | 18.1 | 40.5 | 38.9 | 1.092 | 0
379 | 2022-12-24 06:20 | 4.3 | 18.1 | 40.5 | 38.8 | 1.093 | 0
380 | 2022-12-24 06:21 | 4.1 | 18 | 40.4 | 36.5 | 1.412 | 0
381 | 2022-12-24 06:22 | 4.2 | 18 | 40.3 | 37.8 | 1.631 | 0
382 | 2022-12-24 06:23 | 4.2 | 18.1 | 40.3 | 37.9 | 1.638 | 0
383 | 2022-12-24 06:24 | 4.2 | 18.2 | 40.2 | 37.8 | 1.633 | 0
384 | 2022-12-24 06:25 | 4.1 | 18.3 | 40.2 | 37.7 | 1.64 | 0
385 | 2022-12-24 06:26 | 4.3 | 18.4 | 40.1 | 37.7 | 1.636 | 0
386 | 2022-12-24 06:27 | 4.2 | 18.5 | 40.1 | 37.8 | 1.638 | 0
387 | 2022-12-24 06:28 | 4.2 | 18.6 | 40 | 38.7 | 1.643 | 0
388 | 2022-12-24 06:29 | 4.1 | 18.6 | 39.9 | 38.7 | 1.636 | 0
389 | 2022-12-24 06:30 | 4.3 | 18.5 | 39.9 | 38.6 | 1.631 | 0
390 | 2022-12-24 06:31 | 4.3 | 18.5 | 39.8 | 38.5 | 1.552 | 0
391 | 2022-12-24 06:32 | 4.3 | 18.4 | 39.8 | 38.1 | 1.092 | 0
392 | 2022-12-24 06:33 | 4.3 | 18.3 | 39.6 | 38.1 | 1.087 | 0
393 | 2022-12-24 06:34 | 4 | 18.4 | 39.7 | 37.9 | 1.094 | 0
394 | 2022-12-24 06:35 | 4.2 | 18.3 | 39.8 | 38 | 1.089 | 0
395 | 2022-12-24 06:36 | 4.1 | 18.3 | 40.2 | 38.1 | 1.089 | 0
396 | 2022-12-24 06:37 | 4 | 18.2 | 40.4 | 38.3 | 0 | 0
397 | 2022-12-24 06:38 | 4.1 | 18.1 | 40.2 | 37.9 | 0 | 0
398 | 2022-12-24 06:39 | 4 | 18.3 | 39.9 | 37.3 | 0 | 0
399 | 2022-12-24 06:40 | 3.9 | 18.3 | 39.6 | 36.7 | 0 | 0
400 | 2022-12-24 06:41 | 4 | 18.1 | 39.3 | 36.2 | 0 | 0
401 | 2022-12-24 06:42 | 4.1 | 18.2 | 39 | 35.7 | 0 | 0
402 | 2022-12-24 06:43 | 4.1 | 18.1 | 38.7 | 35.1 | 0 | 0
403 | 2022-12-24 06:44 | 4 | 18.1 | 38.4 | 34.7 | 0 | 0
404 | 2022-12-24 06:45 | 4.1 | 18.1 | 38.1 | 36.1 | 0.086 | 0
405 | 2022-12-24 06:46 | 3.9 | 18 | 37.8 | 36.2 | 0.01 | 0
406 | 2022-12-24 06:47 | 4.2 | 18.1 | 41.9 | 32.1 | 0.662 | 0
407 | 2022-12-24 06:48 | 4.1 | 18 | 42 | 39.2 | 0.978 | 0
408 | 2022-12-24 06:49 | 4 | 18 | 41.2 | 38.9 | 0.979 | 0
409 | 2022-12-24 06:50 | 4.1 | 18.1 | 41.6 | 38.5 | 1.134 | 0
410 | 2022-12-24 06:51 | 3.9 | 18.1 | 41.3 | 37.7 | 1.569 | 0
411 | 2022-12-24 06:52 | 4.1 | 18.3 | 41.2 | 38.7 | 1.579 | 0
412 | 2022-12-24 06:53 | 4 | 18.4 | 40.9 | 39.8 | 1.583 | 0
413 | 2022-12-24 06:54 | 3.9 | 18.4 | 41.1 | 39.7 | 1.576 | 0
414 | 2022-12-24 06:55 | 4 | 18.4 | 41.2 | 39.9 | 1.578 | 0
415 | 2022-12-24 06:56 | 3.9 | 18.3 | 41.3 | 39.9 | 1.502 | 0
416 | 2022-12-24 06:57 | 3.9 | 18.2 | 41.2 | 39.6 | 0.985 | 0
417 | 2022-12-24 06:58 | 4 | 18.2 | 41.2 | 39.5 | 0.981 | 0
418 | 2022-12-24 06:59 | 3.8 | 18.1 | 41.1 | 39.5 | 0.979 | 0
419 | 2022-12-24 07:00 | 3.8 | 18.1 | 40.9 | 39.4 | 0.977 | 0
420 | 2022-12-24 07:01 | 3.7 | 18 | 40.9 | 39.3 | 0.979 | 0
421 | 2022-12-24 07:02 | 3.8 | 18 | 40.7 | 39.2 | 0.977 | 0
422 | 2022-12-24 07:03 | 3.8 | 18 | 40.6 | 39.1 | 0.976 | 0
423 | 2022-12-24 07:04 | 3.9 | 18 | 40.5 | 39 | 0.973 | 0
424 | 2022-12-24 07:05 | 3.9 | 18 | 40.4 | 38.9 | 0.974 | 0
425 | 2022-12-24 07:06 | 3.8 | 18 | 40.3 | 38.8 | 0.975 | 0
426 | 2022-12-24 07:07 | 3.8 | 18 | 40.2 | 38.7 | 0.979 | 0
427 | 2022-12-24 07:08 | 3.9 | 18 | 40.1 | 38.6 | 0.978 | 0
428 | 2022-12-24 07:09 | 3.7 | 17.9 | 40 | 38.5 | 0.982 | 0
429 | 2022-12-24 07:10 | 3.8 | 18 | 39.9 | 38.5 | 0.974 | 0
430 | 2022-12-24 07:11 | 3.9 | 18.1 | 39.9 | 37 | 1.552 | 0
431 | 2022-12-24 07:12 | 3.7 | 18 | 39.8 | 37.5 | 1.574 | 0
432 | 2022-12-24 07:13 | 3.7 | 18 | 39.5 | 37.5 | 1.581 | 0
433 | 2022-12-24 07:14 | 3.8 | 18 | 39.5 | 37.9 | 1.575 | 0
434 | 2022-12-24 07:15 | 3.7 | 18 | 39.5 | 37.9 | 1.576 | 0
435 | 2022-12-24 07:16 | 3.9 | 18.2 | 39.4 | 37.9 | 1.573 | 0
436 | 2022-12-24 07:17 | 3.9 | 18.3 | 39.3 | 37.7 | 0.202 | 0
437 | 2022-12-24 07:18 | 3.9 | 18.4 | 39.2 | 37.5 | 0 | 0
438 | 2022-12-24 07:19 | 3.9 | 18.4 | 38.9 | 36.9 | 0 | 0
439 | 2022-12-24 07:20 | 3.8 | 18.4 | 38.6 | 36.3 | 0 | 0
440 | 2022-12-24 07:21 | 3.8 | 18.1 | 38.4 | 35.7 | 0 | 0
441 | 2022-12-24 07:22 | 3.7 | 18.1 | 38.1 | 35.2 | 0 | 0
442 | 2022-12-24 07:23 | 4 | 18.1 | 37.8 | 34.7 | 0 | 0
443 | 2022-12-24 07:24 | 3.7 | 18 | 37.5 | 34.1 | 0 | 0
444 | 2022-12-24 07:25 | 3.7 | 17.9 | 37.2 | 33.7 | 0 | 0
445 | 2022-12-24 07:26 | 4 | 17.9 | 37 | 33.2 | 0 | 0
446 | 2022-12-24 07:27 | 3.8 | 17.9 | 36.7 | 32.8 | 0 | 0
447 | 2022-12-24 07:28 | 3.8 | 17.9 | 36.4 | 34.9 | 0.021 | 0
448 | 2022-12-24 07:29 | 3.9 | 17.9 | 36.1 | 34.7 | 0 | 0
449 | 2022-12-24 07:30 | 3.8 | 17.8 | 35.9 | 34.5 | 0 | 0
450 | 2022-12-24 07:31 | 4 | 17.9 | 38.5 | 28.4 | 0.79 | 0
451 | 2022-12-24 07:32 | 3.7 | 17.8 | 37.8 | 35.5 | 1.609 | 0
452 | 2022-12-24 07:33 | 4 | 17.8 | 37.6 | 35.4 | 1.617 | 1
453 | 2022-12-24 07:34 | 3.7 | 18.1 | 37.6 | 35.2 | 1.622 | 1
454 | 2022-12-24 07:35 | 3.7 | 18.4 | 38.3 | 34.2 | 1.884 | 1
455 | 2022-12-24 07:36 | 3.8 | 18.7 | 38.7 | 35.4 | 1.889 | 1
456 | 2022-12-24 07:37 | 3.9 | 19 | 38.8 | 35.7 | 1.895 | 2
457 | 2022-12-24 07:38 | 4 | 19.2 | 39.2 | 35.9 | 1.894 | 2
458 | 2022-12-24 07:39 | 3.7 | 19.4 | 39.5 | 36.2 | 1.896 | 2
459 | 2022-12-24 07:40 | 3.7 | 19.6 | 39.7 | 36.5 | 1.895 | 3
460 | 2022-12-24 07:41 | 3.6 | 19.7 | 40 | 36.7 | 1.892 | 3
461 | 2022-12-24 07:42 | 3.6 | 19.8 | 40.3 | 37.5 | 1.895 | 4
462 | 2022-12-24 07:43 | 3.7 | 19.9 | 40.7 | 38.1 | 1.892 | 4
463 | 2022-12-24 07:44 | 3.8 | 20 | 41 | 38.5 | 1.895 | 5
464 | 2022-12-24 07:45 | 3.8 | 20.1 | 41.4 | 38.8 | 1.888 | 6
465 | 2022-12-24 07:46 | 3.6 | 20 | 41.7 | 38.7 | 1.733 | 6
466 | 2022-12-24 07:47 | 3.8 | 20 | 41.8 | 40.2 | 1.628 | 7
467 | 2022-12-24 07:48 | 3.8 | 19.8 | 42.1 | 40.5 | 1.631 | 7
468 | 2022-12-24 07:49 | 3.7 | 19.5 | 42.5 | 40.8 | 1.627 | 7
469 | 2022-12-24 07:50 | 3.6 | 19.3 | 42.9 | 41.1 | 1.61 | 8
470 | 2022-12-24 07:51 | 3.5 | 19.1 | 42.9 | 41.1 | 1.285 | 8
471 | 2022-12-24 07:52 | 3.6 | 18.9 | 42.9 | 41 | 1.087 | 8
472 | 2022-12-24 07:53 | 3.6 | 18.9 | 43.3 | 41 | 1.091 | 9
473 | 2022-12-24 07:54 | 3.8 | 18.8 | 43.8 | 41.4 | 1.1 | 9
474 | 2022-12-24 07:55 | 3.8 | 18.7 | 44.1 | 41.8 | 1.099 | 9
475 | 2022-12-24 07:56 | 3.8 | 18.7 | 44.3 | 42.1 | 1.092 | 10
476 | 2022-12-24 07:57 | 3.7 | 18.6 | 44.6 | 42.2 | 1.089 | 10
477 | 2022-12-24 07:58 | 3.9 | 18.5 | 44.5 | 42 | 0 | 11
478 | 2022-12-24 07:59 | 3.9 | 18.6 | 44.1 | 41.3 | 0 | 11
479 | 2022-12-24 08:00 | 3.7 | 18.5 | 45.6 | 41.2 | 1.098 | 12
480 | 2022-12-24 08:01 | 3.8 | 18.5 | 46 | 43.6 | 1.099 | 12
481 | 2022-12-24 08:02 | 3.7 | 18.6 | 46.1 | 36.3 | 1.742 | 13
482 | 2022-12-24 08:03 | 3.7 | 18.7 | 45.5 | 40.6 | 1.993 | 13
483 | 2022-12-24 08:04 | 3.7 | 18.9 | 45.3 | 40.9 | 2.013 | 14
484 | 2022-12-24 08:05 | 3.7 | 19.3 | 45.5 | 41 | 2.014 | 14
485 | 2022-12-24 08:06 | 3.7 | 19.7 | 45.7 | 41.1 | 2.019 | 15
486 | 2022-12-24 08:07 | 3.7 | 20 | 45.7 | 41.3 | 2.018 | 15
487 | 2022-12-24 08:08 | 3.9 | 20.3 | 45.8 | 41.4 | 2.011 | 16
488 | 2022-12-24 08:09 | 3.9 | 20.5 | 46 | 41.5 | 2.016 | 16
489 | 2022-12-24 08:10 | 3.9 | 20.7 | 46 | 41.6 | 2.021 | 16
490 | 2022-12-24 08:11 | 4 | 20.9 | 46.2 | 41.7 | 2.013 | 17
491 | 2022-12-24 08:12 | 3.9 | 21 | 46.3 | 41.8 | 2.023 | 17
492 | 2022-12-24 08:13 | 3.9 | 21.1 | 46.5 | 41.9 | 2.012 | 18
493 | 2022-12-24 08:14 | 4.1 | 21.1 | 46.5 | 42 | 2.016 | 18
494 | 2022-12-24 08:15 | 4 | 21.2 | 46.7 | 42.1 | 2.016 | 19
495 | 2022-12-24 08:16 | 4.1 | 21.3 | 46.6 | 42.2 | 2.016 | 19
496 | 2022-12-24 08:17 | 4.1 | 21.4 | 46.5 | 42.2 | 2.019 | 19
497 | 2022-12-24 08:18 | 4 | 21.4 | 46.2 | 42.1 | 2.016 | 20
498 | 2022-12-24 08:19 | 4 | 21.5 | 45.8 | 42.8 | 2.017 | 20
499 | 2022-12-24 08:20 | 4.1 | 21.5 | 45.6 | 42.5 | 2.016 | 21
500 | 2022-12-24 08:21 | 4.1 | 21.4 | 45.4 | 42.4 | 2.02 | 21
501 | 2022-12-24 08:22 | 4 | 21.3 | 45.1 | 42.2 | 2.014 | 21
502 | 2022-12-24 08:23 | 3.9 | 21.3 | 44.9 | 41.8 | 1.976 | 22
503 | 2022-12-24 08:24 | 3.9 | 21.2 | 44.6 | 41.5 | 1.84 | 22
504 | 2022-12-24 08:25 | 4 | 21.1 | 44.4 | 41.3 | 1.841 | 23
505 | 2022-12-24 08:26 | 4.2 | 21.2 | 44.2 | 41.1 | 1.832 | 24
506 | 2022-12-24 08:27 | 4.2 | 21.1 | 43.9 | 40.9 | 1.839 | 24
507 | 2022-12-24 08:28 | 4.2 | 21 | 43.6 | 40.6 | 1.835 | 25
508 | 2022-12-24 08:29 | 4.1 | 21 | 43.3 | 40.4 | 1.84 | 25
509 | 2022-12-24 08:30 | 4 | 21.1 | 43.1 | 39.3 | 2.001 | 25
510 | 2022-12-24 08:31 | 4.1 | 21.1 | 42.8 | 39.2 | 2.011 | 25
511 | 2022-12-24 08:32 | 4.1 | 21.1 | 42.3 | 38.9 | 2.005 | 26
512 | 2022-12-24 08:33 | 4.3 | 21.2 | 42.2 | 38.6 | 2.006 | 26
513 | 2022-12-24 08:34 | 4.2 | 21.1 | 42.1 | 38.4 | 2.009 | 27
514 | 2022-12-24 08:35 | 4 | 21.1 | 42.4 | 38.4 | 2.004 | 27
515 | 2022-12-24 08:36 | 4.3 | 21.4 | 42.6 | 38.6 | 2.01 | 28
516 | 2022-12-24 08:37 | 4 | 21.4 | 42.6 | 38.8 | 2.009 | 28
517 | 2022-12-24 08:38 | 4.3 | 21.4 | 42.8 | 38.8 | 2.008 | 28
518 | 2022-12-24 08:39 | 4.1 | 21.4 | 43 | 39.4 | 2.004 | 29
519 | 2022-12-24 08:40 | 4.1 | 21.5 | 43.1 | 40.1 | 2.011 | 29
520 | 2022-12-24 08:41 | 4 | 21.5 | 43.4 | 40.2 | 2.007 | 29
521 | 2022-12-24 08:42 | 4.1 | 21.4 | 43.6 | 40.5 | 2.013 | 30
522 | 2022-12-24 08:43 | 4.1 | 21.3 | 43.5 | 40.6 | 2 | 30
523 | 2022-12-24 08:44 | 4.1 | 21.3 | 43.2 | 40.1 | 1.839 | 30
524 | 2022-12-24 08:45 | 4.4 | 21.3 | 43.1 | 40.1 | 1.834 | 30
525 | 2022-12-24 08:46 | 4.5 | 21.2 | 42.9 | 39.9 | 1.839 | 31
526 | 2022-12-24 08:47 | 4.3 | 21.3 | 42.6 | 39.7 | 1.84 | 31
527 | 2022-12-24 08:48 | 4.4 | 21.2 | 42.4 | 39.5 | 1.838 | 32
528 | 2022-12-24 08:49 | 4.3 | 21.2 | 42.1 | 39.3 | 1.838 | 32
529 | 2022-12-24 08:50 | 4.5 | 21.2 | 41.9 | 39.1 | 1.831 | 32
530 | 2022-12-24 08:51 | 4.4 | 21.3 | 41.8 | 38.8 | 1.96 | 33
531 | 2022-12-24 08:52 | 4.6 | 21.3 | 41.4 | 38 | 2.004 | 33
532 | 2022-12-24 08:53 | 4.5 | 21.3 | 41 | 37.8 | 2.009 | 34
533 | 2022-12-24 08:54 | 4.6 | 21.3 | 40.7 | 37.5 | 2.008 | 34
534 | 2022-12-24 08:55 | 4.6 | 21.3 | 40.5 | 37.2 | 2.003 | 35
535 | 2022-12-24 08:56 | 4.6 | 21.3 | 40.2 | 37 | 2.013 | 35
536 | 2022-12-24 08:57 | 4.5 | 21.4 | 40 | 36.8 | 2.004 | 36
537 | 2022-12-24 08:58 | 4.6 | 21.4 | 39.7 | 36.6 | 1.997 | 37
538 | 2022-12-24 08:59 | 4.8 | 21.4 | 39.5 | 36.4 | 2.001 | 38
539 | 2022-12-24 09:00 | 4.8 | 21.5 | 39.2 | 36.1 | 2.001 | 39
540 | 2022-12-24 09:01 | 4.7 | 21.5 | 39 | 35.9 | 2.005 | 40
541 | 2022-12-24 09:02 | 4.8 | 21.4 | 38.7 | 35.7 | 2.001 | 41
542 | 2022-12-24 09:03 | 4.9 | 21.4 | 38.5 | 35.6 | 1.999 | 42
543 | 2022-12-24 09:04 | 4.9 | 21.4 | 38.5 | 36.1 | 2.003 | 43
544 | 2022-12-24 09:05 | 4.8 | 21.4 | 38.9 | 36.2 | 1.998 | 44
545 | 2022-12-24 09:06 | 4.9 | 21.4 | 39.2 | 36.5 | 2.002 | 44
546 | 2022-12-24 09:07 | 4.8 | 21.3 | 39.4 | 36.8 | 2.006 | 45
547 | 2022-12-24 09:08 | 4.9 | 21.3 | 39.7 | 36.7 | 1.95 | 45
548 | 2022-12-24 09:09 | 4.8 | 21.3 | 39.9 | 37 | 1.833 | 46
549 | 2022-12-24 09:10 | 4.8 | 21.3 | 40.1 | 37.2 | 1.83 | 46
550 | 2022-12-24 09:11 | 4.9 | 21.1 | 40.4 | 37.4 | 1.83 | 46
551 | 2022-12-24 09:12 | 5 | 21.3 | 40.7 | 37.6 | 1.831 | 46
552 | 2022-12-24 09:13 | 5 | 21.2 | 40.9 | 37.9 | 1.83 | 47
553 | 2022-12-24 09:14 | 4.9 | 21.3 | 41.2 | 38.1 | 1.838 | 47
554 | 2022-12-24 09:15 | 4.9 | 21.1 | 41.4 | 38.4 | 1.838 | 48
555 | 2022-12-24 09:16 | 5 | 21.2 | 41.6 | 38.6 | 1.832 | 49
556 | 2022-12-24 09:17 | 4.9 | 21.2 | 41.9 | 36.6 | 1.99 | 49
557 | 2022-12-24 09:18 | 5.1 | 21.3 | 42.1 | 38.2 | 1.999 | 50
558 | 2022-12-24 09:19 | 5 | 21.4 | 42.2 | 38.4 | 2 | 51
559 | 2022-12-24 09:20 | 4.9 | 21.3 | 42.4 | 38.5 | 2 | 52
560 | 2022-12-24 09:21 | 5.1 | 21.5 | 42.6 | 38.7 | 2.002 | 54
561 | 2022-12-24 09:22 | 5.2 | 21.6 | 42.7 | 38.8 | 1.998 | 56
562 | 2022-12-24 09:23 | 5 | 21.7 | 42.9 | 39 | 2.009 | 58
563 | 2022-12-24 09:24 | 5.2 | 21.7 | 43.1 | 39.1 | 2.007 | 59
564 | 2022-12-24 09:25 | 5 | 21.7 | 43.2 | 39.3 | 2.005 | 61
565 | 2022-12-24 09:26 | 5.1 | 21.8 | 43.4 | 40.2 | 1.999 | 62
566 | 2022-12-24 09:27 | 5.2 | 21.8 | 43.5 | 40.5 | 2.016 | 64
567 | 2022-12-24 09:28 | 5.3 | 21.9 | 43.9 | 40.7 | 2.009 | 66
568 | 2022-12-24 09:29 | 5.1 | 21.8 | 43.9 | 40.9 | 2.01 | 68
569 | 2022-12-24 09:30 | 5.2 | 21.8 | 43.7 | 40.6 | 1.967 | 135
570 | 2022-12-24 09:31 | 5.3 | 21.7 | 43.6 | 40.5 | 1.838 | 320
571 | 2022-12-24 09:32 | 5.7 | 21.7 | 43.4 | 40.4 | 1.841 | 501
572 | 2022-12-24 09:33 | 6.2 | 21.8 | 43.1 | 40.2 | 1.83 | 571
573 | 2022-12-24 09:34 | 6.5 | 21.6 | 43.1 | 40 | 1.835 | 577
574 | 2022-12-24 09:35 | 7.1 | 21.6 | 43.4 | 40 | 1.841 | 583
575 | 2022-12-24 09:36 | 7.2 | 21.5 | 43.7 | 40.4 | 1.835 | 588
576 | 2022-12-24 09:37 | 7.1 | 21.5 | 43.9 | 40.6 | 1.832 | 594
577 | 2022-12-24 09:38 | 7 | 21.7 | 44.1 | 40.7 | 1.836 | 600
578 | 2022-12-24 09:39 | 7.1 | 21.7 | 44.3 | 40.9 | 1.836 | 604
579 | 2022-12-24 09:40 | 7.3 | 21.6 | 44.5 | 41.1 | 1.84 | 610
580 | 2022-12-24 09:41 | 7.2 | 21.6 | 44.6 | 41.3 | 1.836 | 614
581 | 2022-12-24 09:42 | 7.5 | 21.7 | 44.5 | 41.4 | 1.838 | 620
582 | 2022-12-24 09:43 | 7.8 | 21.8 | 44.3 | 41.2 | 1.835 | 625
583 | 2022-12-24 09:44 | 7.9 | 21.8 | 44.1 | 41.1 | 1.838 | 630
584 | 2022-12-24 09:45 | 7.9 | 21.9 | 43.8 | 38.4 | 1.991 | 634
585 | 2022-12-24 09:46 | 7.9 | 21.9 | 43.5 | 39.8 | 2.005 | 638
586 | 2022-12-24 09:47 | 8 | 21.9 | 43 | 39.6 | 2 | 643
587 | 2022-12-24 09:48 | 8.3 | 21.9 | 42.8 | 39.2 | 2.001 | 647
588 | 2022-12-24 09:49 | 8.4 | 21.9 | 42.5 | 39 | 2.005 | 650
589 | 2022-12-24 09:50 | 8.7 | 22.1 | 42.1 | 39 | 2.006 | 653
590 | 2022-12-24 09:51 | 8.9 | 21.9 | 41.9 | 39.4 | 2.007 | 656
591 | 2022-12-24 09:52 | 9 | 21.6 | 41.7 | 39.2 | 2.004 | 657
592 | 2022-12-24 09:53 | 8.9 | 21.6 | 41.6 | 39.9 | 1.999 | 659
593 | 2022-12-24 09:54 | 9 | 21.3 | 41.5 | 39.8 | 1.999 | 660
594 | 2022-12-24 09:55 | 9.5 | 21 | 41.4 | 39.6 | 1.868 | 660
595 | 2022-12-24 09:56 | 9.8 | 20.8 | 41.3 | 39.6 | 1.829 | 661
596 | 2022-12-24 09:57 | 9.8 | 20.6 | 41.2 | 39.1 | 1.581 | 660
597 | 2022-12-24 09:58 | 9.7 | 20.5 | 41.1 | 39.1 | 1.511 | 659
598 | 2022-12-24 09:59 | 9.6 | 20.4 | 40.9 | 39 | 1.508 | 659
599 | 2022-12-24 10:00 | 9.6 | 20.3 | 40.7 | 38.8 | 1.508 | 658
600 | 2022-12-24 10:01 | 9.6 | 20.2 | 40.7 | 38.7 | 1.509 | 658
601 | 2022-12-24 10:02 | 9.7 | 20.3 | 40.6 | 36.9 | 1.776 | 657
602 | 2022-12-24 10:03 | 9.7 | 20.4 | 40.4 | 37.8 | 1.831 | 657
603 | 2022-12-24 10:04 | 10.1 | 20.5 | 40.2 | 37.6 | 1.832 | 657
604 | 2022-12-24 10:05 | 10.5 | 20.9 | 40.4 | 37.5 | 1.833 | 657
605 | 2022-12-24 10:06 | 10.2 | 21.1 | 40.8 | 37.8 | 1.876 | 658
606 | 2022-12-24 10:07 | 10.4 | 21.3 | 41 | 37.3 | 1.997 | 660
607 | 2022-12-24 10:08 | 10.4 | 21.5 | 41.1 | 37.6 | 2.002 | 658
608 | 2022-12-24 10:09 | 10.7 | 21.5 | 41.3 | 37.6 | 2 | 660
609 | 2022-12-24 10:10 | 10.3 | 21.6 | 41.5 | 37.8 | 2 | 661
610 | 2022-12-24 10:11 | 10.5 | 21.7 | 41.6 | 38 | 1.997 | 662
611 | 2022-12-24 10:12 | 10.7 | 21.7 | 41.9 | 38.1 | 2.005 | 664
612 | 2022-12-24 10:13 | 10.7 | 21.8 | 42 | 38.4 | 1.998 | 665
613 | 2022-12-24 10:14 | 10.6 | 21.9 | 42.3 | 38.5 | 1.997 | 666
614 | 2022-12-24 10:15 | 10.9 | 22 | 42.5 | 39.6 | 2.008 | 669
615 | 2022-12-24 10:16 | 11.2 | 22.1 | 42.7 | 39.9 | 2.006 | 672
616 | 2022-12-24 10:17 | 10.9 | 21.9 | 43.1 | 41 | 2.011 | 675
617 | 2022-12-24 10:18 | 11 | 21.6 | 43.5 | 41.2 | 1.99 | 677
618 | 2022-12-24 10:19 | 10.8 | 21.2 | 43.8 | 41.5 | 1.836 | 680
619 | 2022-12-24 10:20 | 11.4 | 20.9 | 44.2 | 41.8 | 1.809 | 682
620 | 2022-12-24 10:21 | 11.3 | 20.6 | 44.5 | 41.9 | 1.558 | 684
621 | 2022-12-24 10:22 | 11.1 | 20.5 | 44.8 | 42.2 | 1.51 | 689
622 | 2022-12-24 10:23 | 11.5 | 20.5 | 44.9 | 42.4 | 1.511 | 692
623 | 2022-12-24 10:24 | 11.7 | 20.4 | 44.7 | 42.5 | 1.511 | 695
624 | 2022-12-24 10:25 | 11.5 | 20.4 | 44.6 | 42.3 | 1.508 | 699
625 | 2022-12-24 10:26 | 11.5 | 20.3 | 44.4 | 42.2 | 1.513 | 700
626 | 2022-12-24 10:27 | 12.1 | 20.4 | 44.3 | 42 | 1.596 | 703
627 | 2022-12-24 10:28 | 12.1 | 20.5 | 44.2 | 41 | 1.83 | 706
628 | 2022-12-24 10:29 | 12 | 20.8 | 43.9 | 41 | 1.837 | 708
629 | 2022-12-24 10:30 | 12.2 | 21 | 43.6 | 40.7 | 1.833 | 711
630 | 2022-12-24 10:31 | 12.5 | 21.4 | 43.4 | 40.5 | 1.831 | 714
631 | 2022-12-24 10:32 | 13 | 21.6 | 43.1 | 38.2 | 1.982 | 717
632 | 2022-12-24 10:33 | 13.6 | 21.8 | 42.9 | 39.3 | 2.004 | 719
633 | 2022-12-24 10:34 | 13.8 | 21.9 | 42.4 | 39.1 | 2.001 | 722
634 | 2022-12-24 10:35 | 13.7 | 22 | 42.1 | 38.7 | 2.004 | 723
635 | 2022-12-24 10:36 | 13.1 | 22 | 41.9 | 38.5 | 2.002 | 725
636 | 2022-12-24 10:37 | 13.2 | 22.1 | 41.6 | 38.3 | 2.006 | 726
637 | 2022-12-24 10:38 | 13.7 | 22.1 | 41.3 | 39.4 | 2.003 | 730
638 | 2022-12-24 10:39 | 14 | 22 | 41.2 | 39.6 | 2 | 732
639 | 2022-12-24 10:40 | 13.9 | 21.6 | 41.1 | 39.5 | 1.998 | 734
640 | 2022-12-24 10:41 | 14.1 | 21.3 | 41.1 | 39.5 | 1.998 | 736
641 | 2022-12-24 10:42 | 14.3 | 21.1 | 41 | 39.1 | 1.829 | 734
642 | 2022-12-24 10:43 | 14.4 | 20.9 | 40.8 | 38.9 | 1.51 | 734
643 | 2022-12-24 10:44 | 14.7 | 20.7 | 40.7 | 38.8 | 1.503 | 735
644 | 2022-12-24 10:45 | 14.7 | 20.6 | 40.5 | 38.7 | 1.505 | 736
645 | 2022-12-24 10:46 | 14.4 | 20.5 | 40.5 | 38.6 | 1.501 | 738
646 | 2022-12-24 10:47 | 15 | 20.4 | 40.3 | 38.5 | 1.498 | 738
647 | 2022-12-24 10:48 | 14.7 | 20.4 | 40.3 | 38.3 | 1.501 | 740
648 | 2022-12-24 10:49 | 14.5 | 20.4 | 40.2 | 38.3 | 1.504 | 740
649 | 2022-12-24 10:50 | 14.6 | 20.5 | 40 | 38.2 | 1.505 | 742
650 | 2022-12-24 10:51 | 15 | 20.5 | 39.8 | 37.2 | 1.828 | 745
651 | 2022-12-24 10:52 | 15.1 | 20.6 | 39.6 | 37.1 | 1.828 | 749
652 | 2022-12-24 10:53 | 15.4 | 20.8 | 39.3 | 36.9 | 1.828 | 754
653 | 2022-12-24 10:54 | 15.1 | 21.3 | 39.1 | 36.8 | 1.827 | 755
654 | 2022-12-24 10:55 | 15.6 | 21.4 | 39 | 36.6 | 1.824 | 757
655 | 2022-12-24 10:56 | 15.8 | 21.6 | 38.8 | 36.5 | 1.827 | 761
656 | 2022-12-24 10:57 | 15.6 | 21.7 | 38.6 | 36.3 | 1.827 | 764
657 | 2022-12-24 10:58 | 15.1 | 21.7 | 38.5 | 36.2 | 1.824 | 766
658 | 2022-12-24 10:59 | 15.6 | 21.7 | 38.3 | 36.1 | 1.828 | 769
659 | 2022-12-24 11:00 | 15.7 | 21.8 | 38.1 | 35.9 | 1.827 | 772
660 | 2022-12-24 11:01 | 15.5 | 21.8 | 38 | 35.7 | 1.824 | 773
661 | 2022-12-24 11:02 | 15.6 | 21.8 | 37.8 | 35.6 | 1.825 | 777
662 | 2022-12-24 11:03 | 15.9 | 22 | 37.6 | 35.4 | 1.823 | 777
663 | 2022-12-24 11:04 | 16.2 | 22 | 37.7 | 35.3 | 1.818 | 778
664 | 2022-12-24 11:05 | 16 | 21.8 | 38 | 35.4 | 1.821 | 781
665 | 2022-12-24 11:06 | 15.9 | 21.8 | 38.3 | 36.5 | 1.83 | 783
666 | 2022-12-24 11:07 | 15.8 | 21.4 | 38.8 | 36.8 | 1.827 | 784
667 | 2022-12-24 11:08 | 16.1 | 21.1 | 39.2 | 37.2 | 1.826 | 785
668 | 2022-12-24 11:09 | 16.1 | 20.8 | 39.6 | 37.6 | 1.817 | 788
669 | 2022-12-24 11:10 | 16.6 | 20.6 | 39.9 | 37.8 | 1.672 | 789
670 | 2022-12-24 11:11 | 16.7 | 20.7 | 40.2 | 38.1 | 1.504 | 790
671 | 2022-12-24 11:12 | 16.4 | 20.5 | 40.5 | 35.1 | 1.783 | 790
672 | 2022-12-24 11:13 | 16.3 | 20.5 | 40.7 | 37.8 | 1.827 | 792
673 | 2022-12-24 11:14 | 16.5 | 20.4 | 41 | 38.1 | 1.836 | 793
674 | 2022-12-24 11:15 | 16.2 | 20.5 | 41.1 | 38.2 | 1.846 | 795
675 | 2022-12-24 11:16 | 15.9 | 20.6 | 40.9 | 38.4 | 1.841 | 797
676 | 2022-12-24 11:17 | 16 | 20.7 | 40.8 | 38.2 | 1.838 | 798
677 | 2022-12-24 11:18 | 16 | 20.9 | 40.6 | 38.1 | 1.838 | 800
678 | 2022-12-24 11:19 | 16 | 21 | 40.4 | 36.8 | 1.988 | 799
679 | 2022-12-24 11:20 | 15.9 | 21.3 | 40.2 | 37.1 | 1.994 | 801
680 | 2022-12-24 11:21 | 16 | 21.4 | 39.9 | 37.7 | 2.002 | 804
681 | 2022-12-24 11:22 | 15.9 | 21.6 | 39.7 | 37.5 | 1.995 | 804
682 | 2022-12-24 11:23 | 16.2 | 21.7 | 39.6 | 37.3 | 1.997 | 805
683 | 2022-12-24 11:24 | 16 | 21.8 | 39.5 | 37.2 | 1.988 | 808
684 | 2022-12-24 11:25 | 15.8 | 21.9 | 39.3 | 36.9 | 1.826 | 810
685 | 2022-12-24 11:26 | 15.6 | 22 | 39.1 | 36.8 | 1.829 | 808
686 | 2022-12-24 11:27 | 15.8 | 22 | 38.9 | 36.6 | 1.828 | 808
687 | 2022-12-24 11:28 | 16.2 | 21.9 | 38.8 | 37.3 | 1.822 | 814
688 | 2022-12-24 11:29 | 16.2 | 21.5 | 38.6 | 37.2 | 1.827 | 819
689 | 2022-12-24 11:30 | 16.3 | 21.2 | 38.6 | 37.1 | 1.819 | 818
690 | 2022-12-24 11:31 | 15.8 | 21 | 38.5 | 37 | 1.808 | 817
691 | 2022-12-24 11:32 | 15.6 | 20.8 | 38.4 | 36.7 | 1.599 | 813
692 | 2022-12-24 11:33 | 15.9 | 20.7 | 38.4 | 36.7 | 1.505 | 817
693 | 2022-12-24 11:34 | 16.1 | 20.5 | 38.5 | 36.6 | 1.502 | 823
694 | 2022-12-24 11:35 | 16.1 | 20.5 | 38.7 | 36.8 | 1.505 | 823
695 | 2022-12-24 11:36 | 15.8 | 20.5 | 39.1 | 37 | 1.499 | 823
696 | 2022-12-24 11:37 | 16.1 | 20.4 | 39.5 | 37.3 | 1.505 | 823
697 | 2022-12-24 11:38 | 16 | 20.4 | 39.8 | 37.7 | 1.507 | 823
698 | 2022-12-24 11:39 | 16.1 | 20.3 | 40.3 | 38 | 1.504 | 829
699 | 2022-12-24 11:40 | 16.8 | 20.4 | 40.6 | 38.4 | 1.502 | 830
700 | 2022-12-24 11:41 | 17.1 | 20.5 | 41 | 37 | 1.816 | 832
701 | 2022-12-24 11:42 | 16.8 | 20.6 | 41.3 | 38.3 | 1.832 | 833
702 | 2022-12-24 11:43 | 16.5 | 20.8 | 41.2 | 38.5 | 1.824 | 838
703 | 2022-12-24 11:44 | 16.5 | 21.2 | 41.2 | 38.5 | 1.828 | 831
704 | 2022-12-24 11:45 | 16.4 | 21.5 | 41.1 | 38.5 | 1.827 | 833
705 | 2022-12-24 11:46 | 16.5 | 21.7 | 40.9 | 38.9 | 1.825 | 836
706 | 2022-12-24 11:47 | 16.7 | 21.8 | 40.7 | 38.7 | 1.832 | 836
707 | 2022-12-24 11:48 | 16.6 | 21.9 | 40.7 | 38.6 | 1.829 | 837
708 | 2022-12-24 11:49 | 16.8 | 21.9 | 40.5 | 38.5 | 1.823 | 830
709 | 2022-12-24 11:50 | 17.1 | 22 | 40.4 | 38.3 | 1.679 | 834
710 | 2022-12-24 11:51 | 17.1 | 22.1 | 40.3 | 38.1 | 1.626 | 838
711 | 2022-12-24 11:52 | 16.7 | 21.9 | 40.2 | 39 | 1.628 | 834
712 | 2022-12-24 11:53 | 17 | 21.6 | 40.1 | 39 | 1.617 | 840
713 | 2022-12-24 11:54 | 17.2 | 21.3 | 40 | 38.9 | 1.615 | 842
714 | 2022-12-24 11:55 | 17.7 | 21 | 40 | 38.9 | 1.592 | 845
715 | 2022-12-24 11:56 | 17.5 | 20.9 | 39.9 | 37.9 | 1.607 | 846
716 | 2022-12-24 11:57 | 16.8 | 20.8 | 39.8 | 38 | 1.504 | 847
717 | 2022-12-24 11:58 | 16.9 | 20.6 | 39.6 | 37.9 | 1.507 | 846
718 | 2022-12-24 11:59 | 16.7 | 20.6 | 39.5 | 37.7 | 1.499 | 848
719 | 2022-12-24 12:00 | 16.8 | 20.6 | 39.4 | 37.6 | 1.504 | 848
720 | 2022-12-24 12:01 | 16.6 | 20.5 | 39.3 | 37.6 | 1.5 | 852
721 | 2022-12-24 12:02 | 16.5 | 20.4 | 39.2 | 37.5 | 1.508 | 854
722 | 2022-12-24 12:03 | 16.3 | 20.3 | 39.1 | 37.3 | 1.497 | 855
723 | 2022-12-24 12:04 | 16.2 | 20.4 | 39.3 | 37.3 | 1.501 | 854
724 | 2022-12-24 12:05 | 16.3 | 20.5 | 39.6 | 37.4 | 1.721 | 854
725 | 2022-12-24 12:06 | 16.2 | 20.7 | 40 | 34.8 | 1.973 | 854
726 | 2022-12-24 12:07 | 16.4 | 20.8 | 40.2 | 36.6 | 1.997 | 858
727 | 2022-12-24 12:08 | 16.4 | 21 | 40 | 36.8 | 2 | 861
728 | 2022-12-24 12:09 | 17.1 | 21.4 | 40.4 | 36.8 | 1.995 | 864
729 | 2022-12-24 12:10 | 16.7 | 21.6 | 40.6 | 37.1 | 1.996 | 866
730 | 2022-12-24 12:11 | 16.8 | 21.7 | 40.6 | 37.3 | 1.996 | 868
731 | 2022-12-24 12:12 | 16.7 | 21.9 | 40.4 | 37.3 | 1.999 | 867
732 | 2022-12-24 12:13 | 16.7 | 22.1 | 40.1 | 37.6 | 2 | 868
733 | 2022-12-24 12:14 | 16.4 | 22.1 | 39.9 | 37.7 | 2.003 | 864
734 | 2022-12-24 12:15 | 16.4 | 22.1 | 39.8 | 38.3 | 1.997 | 850
735 | 2022-12-24 12:16 | 16.9 | 21.7 | 39.8 | 38.3 | 1.993 | 858
736 | 2022-12-24 12:17 | 17.3 | 21.5 | 39.7 | 38 | 1.834 | 852
737 | 2022-12-24 12:18 | 17 | 21.2 | 39.6 | 38 | 1.778 | 860
738 | 2022-12-24 12:19 | 17 | 21 | 39.6 | 37.8 | 1.508 | 848
739 | 2022-12-24 12:20 | 17.2 | 20.9 | 39.4 | 37.7 | 1.502 | 857
740 | 2022-12-24 12:21 | 17.7 | 20.8 | 39.3 | 37.6 | 1.497 | 833
741 | 2022-12-24 12:22 | 17.1 | 20.6 | 39.2 | 37.5 | 1.508 | 820
742 | 2022-12-24 12:23 | 17.4 | 20.6 | 39.1 | 37.4 | 1.504 | 801
743 | 2022-12-24 12:24 | 17.4 | 20.5 | 39 | 37.3 | 1.502 | 807
744 | 2022-12-24 12:25 | 16.5 | 20.5 | 38.9 | 37.2 | 1.505 | 776
745 | 2022-12-24 12:26 | 16.3 | 20.5 | 38.8 | 37.2 | 1.505 | 704
746 | 2022-12-24 12:27 | 16.6 | 20.4 | 38.7 | 37 | 1.502 | 756
747 | 2022-12-24 12:28 | 16.8 | 20.4 | 38.6 | 36.9 | 1.506 | 776
748 | 2022-12-24 12:29 | 16.1 | 20.4 | 38.6 | 36.9 | 1.504 | 717
749 | 2022-12-24 12:30 | 15.6 | 20.5 | 38.4 | 36.8 | 1.501 | 672
750 | 2022-12-24 12:31 | 15.7 | 20.6 | 38.3 | 34.9 | 1.806 | 608
751 | 2022-12-24 12:32 | 15.5 | 20.6 | 38.1 | 35.8 | 1.827 | 648
752 | 2022-12-24 12:33 | 16.3 | 20.9 | 37.8 | 35.7 | 1.828 | 652
753 | 2022-12-24 12:34 | 16.4 | 21.2 | 37.9 | 35.5 | 1.824 | 650
754 | 2022-12-24 12:35 | 16.3 | 21.4 | 38.3 | 35.6 | 1.825 | 628
755 | 2022-12-24 12:36 | 16.4 | 21.5 | 38.6 | 36 | 1.83 | 665
756 | 2022-12-24 12:37 | 16.2 | 21.6 | 38.9 | 36.2 | 1.832 | 697
757 | 2022-12-24 12:38 | 16.5 | 21.7 | 39.2 | 36.5 | 1.83 | 630
758 | 2022-12-24 12:39 | 16.8 | 21.8 | 39.5 | 36.7 | 1.825 | 672
759 | 2022-12-24 12:40 | 16.7 | 21.9 | 39.8 | 37 | 1.827 | 674
760 | 2022-12-24 12:41 | 17 | 21.9 | 40.1 | 37.3 | 1.827 | 566
761 | 2022-12-24 12:42 | 16.6 | 21.9 | 40.5 | 37.6 | 1.833 | 559
762 | 2022-12-24 12:43 | 16.7 | 21.9 | 40.6 | 39.4 | 1.832 | 646
763 | 2022-12-24 12:44 | 17.2 | 21.5 | 40.6 | 39.5 | 1.833 | 466
764 | 2022-12-24 12:45 | 17.1 | 21.3 | 40.7 | 39.5 | 1.832 | 426
765 | 2022-12-24 12:46 | 16.9 | 21 | 40.7 | 39.5 | 1.786 | 381
766 | 2022-12-24 12:47 | 16.3 | 20.9 | 40.7 | 39.2 | 1.107 | 428
767 | 2022-12-24 12:48 | 16.4 | 20.8 | 40.7 | 39.1 | 1.09 | 441
768 | 2022-12-24 12:49 | 16.3 | 20.7 | 40.6 | 39.1 | 1.091 | 391
769 | 2022-12-24 12:50 | 16 | 20.6 | 40.6 | 39 | 1.092 | 461
770 | 2022-12-24 12:51 | 16 | 20.5 | 40.5 | 39 | 1.094 | 518
771 | 2022-12-24 12:52 | 16.1 | 20.4 | 40.4 | 38.9 | 1.085 | 542
772 | 2022-12-24 12:53 | 16.2 | 20.5 | 40.2 | 38.8 | 1.088 | 563
773 | 2022-12-24 12:54 | 16.1 | 20.4 | 40.1 | 38 | 1.448 | 671
774 | 2022-12-24 12:55 | 16.2 | 20.4 | 40 | 38.2 | 1.505 | 725
775 | 2022-12-24 12:56 | 16.3 | 20.3 | 40 | 38.1 | 1.507 | 775
776 | 2022-12-24 12:57 | 16.3 | 20.5 | 39.7 | 38 | 1.505 | 777
777 | 2022-12-24 12:58 | 15.9 | 20.6 | 39.6 | 35.9 | 1.8 | 787
778 | 2022-12-24 12:59 | 16.4 | 20.7 | 39.5 | 36.7 | 1.845 | 805
779 | 2022-12-24 13:00 | 16.5 | 20.8 | 39.1 | 36 | 1.999 | 897
780 | 2022-12-24 13:01 | 16.6 | 21.2 | 38.7 | 35.9 | 2.004 | 859
781 | 2022-12-24 13:02 | 16.5 | 21.4 | 38.5 | 35.6 | 1.998 | 877
782 | 2022-12-24 13:03 | 17.1 | 21.6 | 38.4 | 35.5 | 1.993 | 871
783 | 2022-12-24 13:04 | 17.2 | 21.8 | 38.3 | 35.5 | 1.996 | 882
784 | 2022-12-24 13:05 | 17.2 | 21.8 | 38.7 | 35.4 | 1.994 | 889
785 | 2022-12-24 13:06 | 16.9 | 21.9 | 39 | 35.7 | 1.999 | 889
786 | 2022-12-24 13:07 | 16.8 | 22.1 | 39.1 | 36.7 | 1.999 | 895
787 | 2022-12-24 13:08 | 16.9 | 22 | 39.1 | 37.6 | 2.002 | 893
788 | 2022-12-24 13:09 | 17 | 21.8 | 39.2 | 37.6 | 1.996 | 880
789 | 2022-12-24 13:10 | 17 | 21.4 | 39.5 | 37.6 | 1.966 | 849
790 | 2022-12-24 13:11 | 16.9 | 21.3 | 39.9 | 37.9 | 1.795 | 835
791 | 2022-12-24 13:12 | 17.4 | 21.1 | 40.3 | 38.1 | 1.501 | 726
792 | 2022-12-24 13:13 | 16.8 | 20.9 | 40.6 | 38.5 | 1.511 | 636
793 | 2022-12-24 13:14 | 17.1 | 20.8 | 40.9 | 38.8 | 1.501 | 549
794 | 2022-12-24 13:15 | 17.1 | 20.6 | 41.2 | 39.1 | 1.503 | 365
795 | 2022-12-24 13:16 | 16.9 | 20.6 | 41.6 | 39.4 | 1.507 | 456
796 | 2022-12-24 13:17 | 17 | 20.6 | 41.9 | 39.6 | 1.508 | 533
797 | 2022-12-24 13:18 | 16.6 | 20.5 | 42.3 | 40 | 1.508 | 484
798 | 2022-12-24 13:19 | 17 | 20.6 | 42.6 | 40.3 | 1.504 | 516
799 | 2022-12-24 13:20 | 17 | 20.5 | 42.6 | 40.6 | 1.509 | 623
800 | 2022-12-24 13:21 | 17 | 20.5 | 42.5 | 41.2 | 1.508 | 657
801 | 2022-12-24 13:22 | 17.2 | 20.5 | 42.4 | 41.1 | 1.506 | 671
802 | 2022-12-24 13:23 | 16.9 | 20.6 | 42.4 | 40.9 | 1.543 | 644
803 | 2022-12-24 13:24 | 16.7 | 20.8 | 42.4 | 39.8 | 1.819 | 544
804 | 2022-12-24 13:25 | 16.7 | 20.9 | 42.2 | 39.8 | 1.623 | 461
805 | 2022-12-24 13:26 | 16.7 | 21.2 | 41.9 | 39.7 | 1.617 | 428
806 | 2022-12-24 13:27 | 17 | 21.4 | 41.7 | 39.4 | 1.622 | 339
807 | 2022-12-24 13:28 | 16.8 | 21.6 | 41.6 | 39.3 | 1.621 | 354
808 | 2022-12-24 13:29 | 16.5 | 21.8 | 41.4 | 39.2 | 1.625 | 369
809 | 2022-12-24 13:30 | 16.5 | 22 | 41.3 | 39 | 1.625 | 363
810 | 2022-12-24 13:31 | 16.3 | 22 | 41.1 | 38.9 | 1.627 | 352
811 | 2022-12-24 13:32 | 15.9 | 22 | 41 | 38.3 | 1.808 | 383
812 | 2022-12-24 13:33 | 15.9 | 22.2 | 40.8 | 38.3 | 1.832 | 319
813 | 2022-12-24 13:34 | 16.2 | 22.1 | 40.5 | 39 | 1.826 | 362
814 | 2022-12-24 13:35 | 16.5 | 21.6 | 40.4 | 38.8 | 1.831 | 343
815 | 2022-12-24 13:36 | 16.2 | 21.3 | 40.3 | 38.7 | 1.829 | 404
816 | 2022-12-24 13:37 | 16.2 | 21.1 | 40.3 | 38.6 | 1.789 | 437
817 | 2022-12-24 13:38 | 16.1 | 20.9 | 40.1 | 38.3 | 1.506 | 442
818 | 2022-12-24 13:39 | 16.1 | 20.9 | 40 | 38.2 | 1.505 | 490
819 | 2022-12-24 13:40 | 16.4 | 20.7 | 39.9 | 38.1 | 1.507 | 528
820 | 2022-12-24 13:41 | 16.3 | 20.6 | 39.8 | 38 | 1.499 | 525
821 | 2022-12-24 13:42 | 16 | 20.6 | 39.7 | 37.9 | 1.507 | 454
822 | 2022-12-24 13:43 | 16.2 | 20.6 | 39.6 | 37.8 | 1.501 | 369
823 | 2022-12-24 13:44 | 15.9 | 20.5 | 39.5 | 37.7 | 1.5 | 452
824 | 2022-12-24 13:45 | 16.1 | 20.5 | 39.4 | 37.6 | 1.505 | 493
825 | 2022-12-24 13:46 | 15.8 | 20.4 | 39.3 | 37.6 | 1.5 | 501
826 | 2022-12-24 13:47 | 16.2 | 20.5 | 39.2 | 37.5 | 1.503 | 445
827 | 2022-12-24 13:48 | 16.4 | 20.4 | 39.1 | 37.4 | 1.502 | 470
828 | 2022-12-24 13:49 | 16.3 | 20.6 | 39 | 37.3 | 1.507 | 592
829 | 2022-12-24 13:50 | 16.3 | 20.8 | 38.8 | 35.6 | 1.754 | 594
830 | 2022-12-24 13:51 | 16.5 | 20.7 | 38.6 | 36.3 | 1.82 | 531
831 | 2022-12-24 13:52 | 16.5 | 20.8 | 38.4 | 34.3 | 1.954 | 417
832 | 2022-12-24 13:53 | 16.8 | 21.1 | 38.1 | 35.2 | 1.99 | 331
833 | 2022-12-24 13:54 | 16.2 | 21.3 | 37.7 | 35.1 | 1.996 | 227
834 | 2022-12-24 13:55 | 15.8 | 21.5 | 37.5 | 34.8 | 1.994 | 210
835 | 2022-12-24 13:56 | 16 | 21.7 | 37.4 | 34.7 | 1.991 | 211
836 | 2022-12-24 13:57 | 15.6 | 21.7 | 37.2 | 34.6 | 1.985 | 220
837 | 2022-12-24 13:58 | 15.5 | 21.8 | 36.9 | 34.4 | 1.989 | 213
838 | 2022-12-24 13:59 | 15.7 | 21.9 | 36.8 | 34.2 | 1.992 | 228
839 | 2022-12-24 14:00 | 15.8 | 21.9 | 36.6 | 34.6 | 1.99 | 257
840 | 2022-12-24 14:01 | 15.5 | 21.9 | 36.7 | 34.7 | 1.988 | 226
841 | 2022-12-24 14:02 | 15.4 | 21.8 | 37.2 | 35.5 | 1.986 | 217
842 | 2022-12-24 14:03 | 15.7 | 21.5 | 37.7 | 35.9 | 1.986 | 206
843 | 2022-12-24 14:04 | 15.5 | 21.2 | 38 | 36.2 | 1.823 | 197
844 | 2022-12-24 14:05 | 15.5 | 21.1 | 38.4 | 36.5 | 1.762 | 194
845 | 2022-12-24 14:06 | 15.4 | 20.9 | 38.8 | 36.7 | 1.498 | 192
846 | 2022-12-24 14:07 | 15.3 | 20.8 | 39.1 | 37.1 | 1.512 | 194
847 | 2022-12-24 14:08 | 15.4 | 20.8 | 39.5 | 37.4 | 1.501 | 200
848 | 2022-12-24 14:09 | 15.3 | 20.6 | 39.9 | 37.7 | 1.502 | 206
849 | 2022-12-24 14:10 | 15.1 | 20.5 | 40.1 | 38.8 | 1.505 | 216
850 | 2022-12-24 14:11 | 15 | 20.5 | 40 | 38.8 | 1.506 | 235
851 | 2022-12-24 14:12 | 15.1 | 20.5 | 40 | 38.8 | 1.502 | 252
852 | 2022-12-24 14:13 | 15.1 | 20.4 | 40 | 38.8 | 1.457 | 275
853 | 2022-12-24 14:14 | 15.1 | 20.5 | 40 | 38.5 | 1.09 | 260
854 | 2022-12-24 14:15 | 14.9 | 20.4 | 40 | 38.4 | 1.09 | 258
855 | 2022-12-24 14:16 | 15.1 | 20.4 | 39.8 | 38.4 | 1.094 | 274
856 | 2022-12-24 14:17 | 15.2 | 20.4 | 39.7 | 38.3 | 1.086 | 267
857 | 2022-12-24 14:18 | 15 | 20.4 | 39.7 | 38.2 | 1.089 | 281
858 | 2022-12-24 14:19 | 14.8 | 20.5 | 39.6 | 38.1 | 1.092 | 275
859 | 2022-12-24 14:20 | 14.9 | 20.6 | 39.5 | 37.5 | 1.322 | 273
860 | 2022-12-24 14:21 | 15 | 20.7 | 39.4 | 35.5 | 1.812 | 306
861 | 2022-12-24 14:22 | 15.1 | 20.7 | 39.1 | 36.8 | 1.821 | 318
862 | 2022-12-24 14:23 | 14.9 | 20.9 | 38.8 | 36.6 | 1.828 | 351
863 | 2022-12-24 14:24 | 15.1 | 21.1 | 38.6 | 36.3 | 1.823 | 342
864 | 2022-12-24 14:25 | 15.3 | 21.4 | 38.5 | 36.2 | 1.824 | 339
865 | 2022-12-24 14:26 | 14.9 | 21.6 | 38.3 | 36.1 | 1.823 | 286
866 | 2022-12-24 14:27 | 15 | 21.7 | 38.2 | 35.9 | 1.825 | 395
867 | 2022-12-24 14:28 | 15.2 | 21.7 | 38 | 35.8 | 1.823 | 507
868 | 2022-12-24 14:29 | 15.4 | 21.8 | 37.8 | 35.7 | 1.823 | 536
869 | 2022-12-24 14:30 | 15.9 | 21.9 | 37.7 | 35.5 | 1.828 | 377
870 | 2022-12-24 14:31 | 16.1 | 21.9 | 37.5 | 35.4 | 1.821 | 472
871 | 2022-12-24 14:32 | 15.8 | 21.9 | 37.4 | 36 | 1.828 | 678
872 | 2022-12-24 14:33 | 15.7 | 21.4 | 37.3 | 36.2 | 1.825 | 714
873 | 2022-12-24 14:34 | 16.1 | 21.2 | 37.4 | 36.5 | 1.826 | 712
874 | 2022-12-24 14:35 | 16.6 | 21.1 | 38 | 36.7 | 1.814 | 706
875 | 2022-12-24 14:36 | 16.2 | 20.9 | 38.5 | 37.2 | 1.623 | 695
876 | 2022-12-24 14:37 | 16.3 | 20.8 | 38.9 | 37.7 | 1.496 | 688
877 | 2022-12-24 14:38 | 16.3 | 20.7 | 39.3 | 38 | 1.463 | 681
878 | 2022-12-24 14:39 | 16.3 | 20.6 | 39.7 | 38.3 | 1.294 | 673
879 | 2022-12-24 14:40 | 16.6 | 20.6 | 40.2 | 38.4 | 1.016 | 670
880 | 2022-12-24 14:41 | 16.3 | 20.5 | 40.6 | 38.8 | 0.979 | 668
881 | 2022-12-24 14:42 | 16.5 | 20.5 | 40.6 | 39.1 | 0.975 | 667
882 | 2022-12-24 14:43 | 16.3 | 20.5 | 40.2 | 39.1 | 0.981 | 641
883 | 2022-12-24 14:44 | 16.4 | 20.4 | 40.2 | 38.8 | 0.963 | 628
884 | 2022-12-24 14:45 | 16.5 | 20.3 | 40.2 | 39.8 | 0.982 | 638
885 | 2022-12-24 14:46 | 16.7 | 20.3 | 40.2 | 38.7 | 1.501 | 635
886 | 2022-12-24 14:47 | 16.8 | 20.4 | 40.2 | 39 | 1.511 | 641
887 | 2022-12-24 14:48 | 16.7 | 20.5 | 40.2 | 36.7 | 1.796 | 640
888 | 2022-12-24 14:49 | 17 | 20.5 | 40.1 | 37.8 | 1.622 | 633
889 | 2022-12-24 14:50 | 17.1 | 20.7 | 39.8 | 37.6 | 1.627 | 624
890 | 2022-12-24 14:51 | 16.9 | 21.1 | 39.6 | 36.4 | 1.883 | 618
891 | 2022-12-24 14:52 | 16.7 | 21.4 | 39.4 | 36.7 | 1.892 | 619
892 | 2022-12-24 14:53 | 16.9 | 21.5 | 38.9 | 36.5 | 1.887 | 595
893 | 2022-12-24 14:54 | 17.3 | 21.7 | 38.8 | 36.2 | 1.886 | 534
894 | 2022-12-24 14:55 | 16.9 | 21.8 | 38.6 | 36.1 | 1.885 | 547
895 | 2022-12-24 14:56 | 16.7 | 22 | 38.5 | 36 | 1.891 | 561
896 | 2022-12-24 14:57 | 16.6 | 22 | 38.2 | 36.4 | 1.892 | 621
897 | 2022-12-24 14:58 | 16.6 | 22 | 38.1 | 36.6 | 1.999 | 634
898 | 2022-12-24 14:59 | 16.8 | 21.8 | 38 | 36.7 | 1.992 | 669
899 | 2022-12-24 15:00 | 17.1 | 21.5 | 38 | 36.6 | 1.992 | 677
900 | 2022-12-24 15:01 | 16.8 | 21.3 | 37.9 | 36.3 | 1.757 | 602
901 | 2022-12-24 15:02 | 16.5 | 21.1 | 37.8 | 36.2 | 1.491 | 666
902 | 2022-12-24 15:03 | 16.6 | 21 | 37.6 | 36.1 | 1.496 | 550
903 | 2022-12-24 15:04 | 16.7 | 20.8 | 37.7 | 36 | 1.504 | 494
904 | 2022-12-24 15:05 | 16.9 | 20.8 | 37.9 | 36.1 | 1.497 | 293
905 | 2022-12-24 15:06 | 16.6 | 20.7 | 38.4 | 36.4 | 1.503 | 552
906 | 2022-12-24 15:07 | 16.7 | 20.7 | 38.7 | 36.8 | 1.505 | 255
907 | 2022-12-24 15:08 | 16.5 | 20.7 | 39.1 | 37 | 1.502 | 266
908 | 2022-12-24 15:09 | 16 | 20.6 | 39.5 | 37.4 | 1.512 | 264
909 | 2022-12-24 15:10 | 16 | 20.6 | 39.9 | 37.8 | 1.505 | 227
910 | 2022-12-24 15:11 | 15.9 | 20.5 | 40.3 | 38.1 | 1.508 | 219
911 | 2022-12-24 15:12 | 15.9 | 20.5 | 40.6 | 38.4 | 1.506 | 221
912 | 2022-12-24 15:13 | 15.8 | 20.5 | 41 | 38.8 | 1.5 | 189
913 | 2022-12-24 15:14 | 16 | 20.6 | 41.5 | 39.1 | 1.506 | 175
914 | 2022-12-24 15:15 | 15.7 | 20.4 | 41.8 | 39.5 | 1.508 | 166
915 | 2022-12-24 15:16 | 15.5 | 20.5 | 42.1 | 39.8 | 1.502 | 159
916 | 2022-12-24 15:17 | 15.4 | 20.5 | 42.5 | 40.1 | 1.507 | 154
917 | 2022-12-24 15:18 | 15.4 | 20.6 | 42.8 | 41.1 | 1.507 | 144
918 | 2022-12-24 15:19 | 15.4 | 20.7 | 43.4 | 40 | 1.706 | 136
919 | 2022-12-24 15:20 | 15.3 | 20.6 | 43.1 | 40.8 | 1.833 | 130
920 | 2022-12-24 15:21 | 15.3 | 20.7 | 42.9 | 41.3 | 1.835 | 128
921 | 2022-12-24 15:22 | 15 | 21 | 42.7 | 41.1 | 1.703 | 126
922 | 2022-12-24 15:23 | 14.9 | 21.3 | 42.7 | 41.1 | 1.626 | 124
923 | 2022-12-24 15:24 | 14.8 | 21.5 | 42.6 | 41 | 1.626 | 124
924 | 2022-12-24 15:25 | 14.8 | 21.6 | 42.5 | 40.9 | 1.619 | 125
925 | 2022-12-24 15:26 | 14.7 | 21.8 | 42.4 | 40.8 | 1.56 | 128
926 | 2022-12-24 15:27 | 14.9 | 21.8 | 42.4 | 40.5 | 1.417 | 138
927 | 2022-12-24 15:28 | 15 | 21.8 | 42.3 | 40 | 0.957 | 155
928 | 2022-12-24 15:29 | 15 | 21.8 | 42.2 | 39.9 | 0.955 | 368
929 | 2022-12-24 15:30 | 15.2 | 21.9 | 42.1 | 39.7 | 0.948 | 501
930 | 2022-12-24 15:31 | 15.4 | 22 | 42 | 40 | 1.483 | 451
931 | 2022-12-24 15:32 | 15.5 | 22 | 41.7 | 39.5 | 1.564 | 430
932 | 2022-12-24 15:33 | 15.3 | 21.8 | 41.5 | 40.5 | 1.566 | 451
933 | 2022-12-24 15:34 | 15 | 21.5 | 41.4 | 40.4 | 1.565 | 365
934 | 2022-12-24 15:35 | 15.2 | 21.3 | 41.5 | 40.3 | 1.56 | 432
935 | 2022-12-24 15:36 | 15.3 | 21 | 41.4 | 40.3 | 1.53 | 450
936 | 2022-12-24 15:37 | 15.6 | 20.9 | 41.4 | 40.1 | 1.188 | 411
937 | 2022-12-24 15:38 | 15.9 | 20.7 | 41.3 | 37.2 | 1.433 | 427
938 | 2022-12-24 15:39 | 15.6 | 20.6 | 41.1 | 39.2 | 1.507 | 413
939 | 2022-12-24 15:40 | 15.8 | 20.7 | 41.1 | 39.2 | 1.511 | 434
940 | 2022-12-24 15:41 | 15.7 | 20.6 | 40.8 | 39.1 | 1.504 | 411
941 | 2022-12-24 15:42 | 15.5 | 20.5 | 40.7 | 38.8 | 1.508 | 358
942 | 2022-12-24 15:43 | 15.4 | 20.5 | 40.6 | 38.7 | 1.508 | 464
943 | 2022-12-24 15:44 | 15.3 | 20.6 | 40.4 | 38.6 | 1.508 | 223
944 | 2022-12-24 15:45 | 15.3 | 20.5 | 40.3 | 38.5 | 1.502 | 346
945 | 2022-12-24 15:46 | 15.3 | 20.5 | 40.1 | 39 | 1.505 | 380
946 | 2022-12-24 15:47 | 15.3 | 20.5 | 40 | 38.9 | 1.507 | 354
947 | 2022-12-24 15:48 | 15.4 | 20.5 | 40 | 38.8 | 1.504 | 386
948 | 2022-12-24 15:49 | 15.3 | 20.5 | 39.9 | 38.8 | 1.498 | 301
949 | 2022-12-24 15:50 | 15.3 | 20.4 | 39.9 | 38.7 | 1.189 | 259
950 | 2022-12-24 15:51 | 14.8 | 20.5 | 39.9 | 38.4 | 1.091 | 303
951 | 2022-12-24 15:52 | 14.6 | 20.6 | 39.8 | 32.4 | 1.808 | 295
952 | 2022-12-24 15:53 | 14.7 | 20.7 | 39.7 | 36.8 | 1.887 | 281
953 | 2022-12-24 15:54 | 14.7 | 20.9 | 38.9 | 36.8 | 1.885 | 203
954 | 2022-12-24 15:55 | 14.5 | 21.1 | 38.8 | 36.1 | 1.88 | 270
955 | 2022-12-24 15:56 | 14.5 | 21.4 | 38.7 | 36.1 | 1.885 | 302
956 | 2022-12-24 15:57 | 14.1 | 21.6 | 38.5 | 36 | 1.886 | 359
957 | 2022-12-24 15:58 | 14.2 | 21.7 | 38.3 | 35.8 | 1.883 | 366
958 | 2022-12-24 15:59 | 14.3 | 21.9 | 38.1 | 36.4 | 1.889 | 364
959 | 2022-12-24 16:00 | 14.4 | 22 | 38 | 36.5 | 1.987 | 337
960 | 2022-12-24 16:01 | 14.1 | 22 | 37.9 | 36.3 | 1.997 | 358
961 | 2022-12-24 16:02 | 14.4 | 21.9 | 37.8 | 37 | 1.965 | 328
962 | 2022-12-24 16:03 | 14.1 | 21.6 | 37.7 | 36.9 | 1.826 | 312
963 | 2022-12-24 16:04 | 14.3 | 21.3 | 37.9 | 36.9 | 1.813 | 236
964 | 2022-12-24 16:05 | 14.3 | 21 | 38.3 | 37.1 | 1.712 | 304
965 | 2022-12-24 16:06 | 14.2 | 20.8 | 38.7 | 37.2 | 1.193 | 318
966 | 2022-12-24 16:07 | 14.1 | 20.7 | 39.1 | 37.4 | 0.973 | 282
967 | 2022-12-24 16:08 | 13.8 | 20.6 | 39.5 | 37.7 | 0.974 | 257
968 | 2022-12-24 16:09 | 13.2 | 20.4 | 39.9 | 38.1 | 0.975 | 263
969 | 2022-12-24 16:10 | 13 | 20.4 | 40.3 | 38.5 | 0.971 | 262
970 | 2022-12-24 16:11 | 12.5 | 20.4 | 40.7 | 38.9 | 0.975 | 225
971 | 2022-12-24 16:12 | 12.4 | 20.4 | 41.3 | 39.2 | 0.977 | 235
972 | 2022-12-24 16:13 | 12.3 | 20.3 | 40.5 | 39.7 | 0.976 | 288
973 | 2022-12-24 16:14 | 12.4 | 20.2 | 40.8 | 39.1 | 0.977 | 214
974 | 2022-12-24 16:15 | 12.3 | 20.2 | 40.5 | 39.2 | 1.094 | 224
975 | 2022-12-24 16:16 | 12.3 | 20.3 | 40.6 | 38.4 | 1.505 | 165
976 | 2022-12-24 16:17 | 12.2 | 20.4 | 40.5 | 37.6 | 1.822 | 198
977 | 2022-12-24 16:18 | 12.1 | 20.5 | 40.3 | 37.9 | 1.83 | 184
978 | 2022-12-24 16:19 | 12 | 20.8 | 40.1 | 38.2 | 1.831 | 127
979 | 2022-12-24 16:20 | 12.1 | 21 | 40 | 38.1 | 1.826 | 120
980 | 2022-12-24 16:21 | 12.1 | 21.3 | 39.9 | 38 | 1.829 | 119
981 | 2022-12-24 16:22 | 11.8 | 21.4 | 39.8 | 37.8 | 1.806 | 103
982 | 2022-12-24 16:23 | 11.7 | 21.6 | 39.7 | 37.5 | 1.621 | 90
983 | 2022-12-24 16:24 | 11.4 | 21.7 | 39.5 | 37.4 | 1.614 | 85
984 | 2022-12-24 16:25 | 11.2 | 21.8 | 39.3 | 37.2 | 1.616 | 80
985 | 2022-12-24 16:26 | 10.9 | 21.9 | 39.2 | 37.1 | 1.613 | 67
986 | 2022-12-24 16:27 | 11.1 | 21.9 | 39.1 | 37 | 1.623 | 70
987 | 2022-12-24 16:28 | 10.9 | 21.9 | 39 | 37.8 | 1.618 | 69
988 | 2022-12-24 16:29 | 10.8 | 21.6 | 38.9 | 37.9 | 1.62 | 99
989 | 2022-12-24 16:30 | 10.7 | 21.3 | 38.7 | 37.7 | 1.621 | 83
990 | 2022-12-24 16:31 | 10.6 | 21.1 | 38.8 | 37.6 | 1.61 | 95
991 | 2022-12-24 16:32 | 10.5 | 20.9 | 38.7 | 36.2 | 1.688 | 136
992 | 2022-12-24 16:33 | 10.5 | 20.8 | 38.6 | 36.9 | 1.505 | 146
993 | 2022-12-24 16:34 | 10.4 | 20.8 | 38.7 | 36.8 | 1.504 | 141
994 | 2022-12-24 16:35 | 10.5 | 20.6 | 39.2 | 37 | 1.499 | 151
995 | 2022-12-24 16:36 | 10.5 | 20.6 | 39.5 | 37.4 | 1.508 | 165
996 | 2022-12-24 16:37 | 10.5 | 20.6 | 39.8 | 37.7 | 1.508 | 157
997 | 2022-12-24 16:38 | 10.4 | 20.7 | 40.2 | 38 | 1.505 | 86
998 | 2022-12-24 16:39 | 10.3 | 20.6 | 40.5 | 38.3 | 1.502 | 62
999 | 2022-12-24 16:40 | 10.2 | 20.5 | 40.8 | 38.6 | 1.503 | 45
1000 | 2022-12-24 16:41 | 10.1 | 20.5 | 40.7 | 38.8 | 1.509 | 38
1001 | 2022-12-24 16:42 | 10.1 | 20.4 | 40.6 | 35.8 | 1.757 | 32
1002 | 2022-12-24 16:43 | 10 | 20.4 | 40.4 | 37.7 | 1.836 | 29
1003 | 2022-12-24 16:44 | 10.1 | 20.5 | 40.1 | 37.7 | 1.831 | 27
1004 | 2022-12-24 16:45 | 10 | 20.6 | 39.8 | 37.2 | 1.885 | 25
1005 | 2022-12-24 16:46 | 9.8 | 20.7 | 39.7 | 36.4 | 1.993 | 23
1006 | 2022-12-24 16:47 | 10 | 20.9 | 39.3 | 36.5 | 1.992 | 21
1007 | 2022-12-24 16:48 | 9.9 | 21.2 | 39 | 36.7 | 1.988 | 20
1008 | 2022-12-24 16:49 | 10 | 21.4 | 38.9 | 36.6 | 1.997 | 18
1009 | 2022-12-24 16:50 | 9.9 | 21.7 | 38.8 | 36.5 | 1.998 | 17
1010 | 2022-12-24 16:51 | 9.8 | 21.9 | 38.6 | 37.5 | 1.997 | 16
1011 | 2022-12-24 16:52 | 9.7 | 21.9 | 38.5 | 37.4 | 1.991 | 15
1012 | 2022-12-24 16:53 | 9.9 | 21.8 | 38.5 | 37.3 | 1.959 | 14
1013 | 2022-12-24 16:54 | 9.9 | 21.8 | 38.5 | 37.2 | 0 | 13
1014 | 2022-12-24 16:55 | 9.6 | 21.6 | 38.3 | 37 | 0 | 13
1015 | 2022-12-24 16:56 | 9.8 | 21.4 | 38.1 | 36.6 | 0 | 12
1016 | 2022-12-24 16:57 | 9.6 | 21.1 | 37.9 | 36.2 | 0 | 12
1017 | 2022-12-24 16:58 | 9.5 | 20.9 | 37.6 | 35.8 | 0 | 13
1018 | 2022-12-24 16:59 | 9.7 | 20.6 | 37.4 | 35.4 | 0 | 12
1019 | 2022-12-24 17:00 | 9.5 | 20.6 | 37.2 | 35.1 | 0 | 10
1020 | 2022-12-24 17:01 | 9.5 | 20.4 | 37 | 34.7 | 0 | 9
1021 | 2022-12-24 17:02 | 9.3 | 20.4 | 36.7 | 35.1 | 0 | 8
1022 | 2022-12-24 17:03 | 9.3 | 20.3 | 36.5 | 36.2 | 0.007 | 7
1023 | 2022-12-24 17:04 | 9.7 | 20.3 | 38.1 | 34.2 | 0.784 | 5
1024 | 2022-12-24 17:05 | 9.7 | 20.2 | 38 | 36.2 | 1.503 | 4
1025 | 2022-12-24 17:06 | 9.7 | 20.2 | 38.6 | 36.3 | 1.509 | 3
1026 | 2022-12-24 17:07 | 9.5 | 20.2 | 39 | 36.9 | 1.502 | 3
1027 | 2022-12-24 17:08 | 9.5 | 20.4 | 39.5 | 37.2 | 1.524 | 2
1028 | 2022-12-24 17:09 | 9.4 | 20.4 | 39.9 | 36.6 | 1.821 | 1
1029 | 2022-12-24 17:10 | 9.7 | 20.4 | 40.1 | 37.2 | 1.828 | 1
1030 | 2022-12-24 17:11 | 9.6 | 20.7 | 40.3 | 37.5 | 1.832 | 1
1031 | 2022-12-24 17:12 | 9.7 | 21 | 40.2 | 37.6 | 1.832 | 0
1032 | 2022-12-24 17:13 | 9.4 | 21.3 | 40 | 37.5 | 1.827 | 0
1033 | 2022-12-24 17:14 | 9.2 | 21.4 | 40 | 37.4 | 1.83 | 0
1034 | 2022-12-24 17:15 | 9 | 21.7 | 39.8 | 37.3 | 1.827 | 0
1035 | 2022-12-24 17:16 | 9.1 | 21.7 | 39.6 | 37.2 | 1.829 | 0
1036 | 2022-12-24 17:17 | 8.8 | 21.8 | 39.5 | 37 | 1.83 | 0
1037 | 2022-12-24 17:18 | 8.9 | 21.9 | 39.4 | 36.9 | 1.831 | 0
1038 | 2022-12-24 17:19 | 8.9 | 21.9 | 39.1 | 36.8 | 1.827 | 0
1039 | 2022-12-24 17:20 | 8.9 | 21.8 | 39 | 36.6 | 1.826 | 0
1040 | 2022-12-24 17:21 | 8.8 | 21.9 | 38.8 | 37.1 | 1.832 | 0
1041 | 2022-12-24 17:22 | 8.7 | 21.7 | 38.7 | 37.2 | 1.824 | 0
1042 | 2022-12-24 17:23 | 8.8 | 21.3 | 38.6 | 37.1 | 1.831 | 0
1043 | 2022-12-24 17:24 | 8.6 | 21.1 | 38.6 | 37.1 | 1.82 | 0
1044 | 2022-12-24 17:25 | 8.6 | 21 | 38.5 | 37.4 | 1.736 | 0
1045 | 2022-12-24 17:26 | 8.6 | 20.9 | 38.4 | 37.3 | 1.5 | 0
1046 | 2022-12-24 17:27 | 8.9 | 20.7 | 38.3 | 37.2 | 1.501 | 0
1047 | 2022-12-24 17:28 | 8.7 | 20.6 | 38.2 | 37.2 | 1.483 | 0
1048 | 2022-12-24 17:29 | 8.6 | 20.6 | 38.2 | 36.8 | 1.092 | 0
1049 | 2022-12-24 17:30 | 8.4 | 20.6 | 38.1 | 36.8 | 1.089 | 0
1050 | 2022-12-24 17:31 | 8.5 | 20.5 | 38 | 33.3 | 1.526 | 0
1051 | 2022-12-24 17:32 | 8.4 | 20.5 | 37.8 | 35.8 | 1.625 | 0
1052 | 2022-12-24 17:33 | 8.5 | 20.5 | 37.7 | 35.8 | 1.641 | 0
1053 | 2022-12-24 17:34 | 8.4 | 20.5 | 37.6 | 35.6 | 1.631 | 0
1054 | 2022-12-24 17:35 | 8.3 | 20.5 | 38.1 | 35.7 | 1.623 | 0
1055 | 2022-12-24 17:36 | 8.2 | 20.6 | 38.4 | 36.1 | 1.624 | 0
1056 | 2022-12-24 17:37 | 8.2 | 20.7 | 38.7 | 34.9 | 1.823 | 0
1057 | 2022-12-24 17:38 | 8.2 | 20.6 | 39 | 36.2 | 1.833 | 0
1058 | 2022-12-24 17:39 | 8.2 | 20.6 | 39.2 | 36.6 | 1.835 | 0
1059 | 2022-12-24 17:40 | 8.1 | 20.6 | 39.6 | 37.6 | 1.833 | 0
1060 | 2022-12-24 17:41 | 8.1 | 20.7 | 39.7 | 38 | 1.841 | 0
1061 | 2022-12-24 17:42 | 8 | 20.6 | 39.7 | 38.1 | 1.836 | 0
1062 | 2022-12-24 17:43 | 8.2 | 20.6 | 39.6 | 38 | 1.814 | 0
1063 | 2022-12-24 17:44 | 8.3 | 20.6 | 39.5 | 37.7 | 1.506 | 0
1064 | 2022-12-24 17:45 | 8.1 | 20.7 | 39.4 | 37.7 | 1.503 | 0
1065 | 2022-12-24 17:46 | 8.1 | 20.6 | 39.3 | 35.9 | 1.82 | 0
1066 | 2022-12-24 17:47 | 8 | 20.7 | 39.1 | 36.7 | 1.832 | 0
1067 | 2022-12-24 17:48 | 7.9 | 20.8 | 38.7 | 36.6 | 1.828 | 0
1068 | 2022-12-24 17:49 | 8 | 21.1 | 38.6 | 36.8 | 1.826 | 0
1069 | 2022-12-24 17:50 | 8 | 21.4 | 38.5 | 36.8 | 1.829 | 0
1070 | 2022-12-24 17:51 | 7.9 | 21.5 | 38.4 | 36.7 | 1.829 | 0
1071 | 2022-12-24 17:52 | 7.9 | 21.6 | 38.3 | 36.6 | 1.824 | 0
1072 | 2022-12-24 17:53 | 7.9 | 21.6 | 38.2 | 36.6 | 1.818 | 0
1073 | 2022-12-24 17:54 | 7.8 | 21.6 | 38.1 | 36.4 | 1.777 | 0
1074 | 2022-12-24 17:55 | 7.8 | 21.6 | 38 | 36.2 | 1.627 | 0
1075 | 2022-12-24 17:56 | 7.9 | 21.6 | 37.9 | 36 | 1.557 | 0
1076 | 2022-12-24 17:57 | 7.8 | 21.6 | 37.7 | 35.9 | 1.554 | 0
1077 | 2022-12-24 17:58 | 7.9 | 21.7 | 37.6 | 35.7 | 1.564 | 0
1078 | 2022-12-24 17:59 | 7.7 | 21.7 | 37.4 | 35.6 | 1.557 | 0
1079 | 2022-12-24 18:00 | 7.8 | 21.7 | 37.3 | 36 | 1.563 | 0
1080 | 2022-12-24 18:01 | 7.8 | 21.7 | 37.2 | 36 | 1.554 | 0
1081 | 2022-12-24 18:02 | 7.8 | 21.7 | 37.2 | 35.9 | 1.553 | 0
1082 | 2022-12-24 18:03 | 7.9 | 21.7 | 37.1 | 36.4 | 1.601 | 0
1083 | 2022-12-24 18:04 | 8 | 21.5 | 37.2 | 35.9 | 1.607 | 0
1084 | 2022-12-24 18:05 | 7.7 | 21.2 | 37.6 | 36.2 | 1.609 | 0
1085 | 2022-12-24 18:06 | 8 | 21 | 38 | 36.6 | 1.613 | 0
1086 | 2022-12-24 18:07 | 8 | 20.9 | 38.5 | 36.9 | 1.478 | 0
1087 | 2022-12-24 18:08 | 8.1 | 20.7 | 38.8 | 37 | 1.088 | 0
1088 | 2022-12-24 18:09 | 8 | 20.8 | 39.3 | 37.4 | 1.09 | 0
1089 | 2022-12-24 18:10 | 8 | 20.7 | 39.5 | 37.7 | 1.09 | 0
1090 | 2022-12-24 18:11 | 7.9 | 20.5 | 40 | 38.1 | 1.082 | 0
1091 | 2022-12-24 18:12 | 7.8 | 20.5 | 40.2 | 38.4 | 1.089 | 0
1092 | 2022-12-24 18:13 | 7.8 | 20.4 | 40.2 | 38 | 1.495 | 0
1093 | 2022-12-24 18:14 | 8 | 20.4 | 39.8 | 34.7 | 1.774 | 0
1094 | 2022-12-24 18:15 | 8 | 20.5 | 39.7 | 37.1 | 1.829 | 0
1095 | 2022-12-24 18:16 | 8 | 20.5 | 39.5 | 37.2 | 1.836 | 0
1096 | 2022-12-24 18:17 | 8 | 20.5 | 39.2 | 36.9 | 1.839 | 0
1097 | 2022-12-24 18:18 | 8.1 | 20.6 | 39.1 | 36.7 | 1.832 | 0
1098 | 2022-12-24 18:19 | 8 | 20.6 | 38.9 | 36.6 | 1.833 | 0
1099 | 2022-12-24 18:20 | 8 | 20.8 | 38.8 | 36.4 | 1.833 | 0
1100 | 2022-12-24 18:21 | 8.5 | 20.9 | 38.6 | 34.9 | 1.997 | 0
1101 | 2022-12-24 18:22 | 8.3 | 21 | 38.4 | 35.6 | 1.994 | 0
1102 | 2022-12-24 18:23 | 8.6 | 21.2 | 38.1 | 35.4 | 1.993 | 0
1103 | 2022-12-24 18:24 | 8.4 | 21.4 | 37.9 | 35.8 | 1.994 | 0
1104 | 2022-12-24 18:25 | 8.7 | 21.6 | 37.7 | 35.7 | 1.993 | 0
1105 | 2022-12-24 18:26 | 8.6 | 21.7 | 37.6 | 35.6 | 1.991 | 0
1106 | 2022-12-24 18:27 | 8.5 | 21.8 | 37.5 | 35.3 | 1.951 | 0
1107 | 2022-12-24 18:28 | 8.3 | 21.8 | 37.3 | 35.1 | 1.829 | 0
1108 | 2022-12-24 18:29 | 8.4 | 21.9 | 37.1 | 35 | 1.824 | 0
1109 | 2022-12-24 18:30 | 8.5 | 21.7 | 37 | 35.6 | 1.824 | 0
1110 | 2022-12-24 18:31 | 8.1 | 21.4 | 36.9 | 35.5 | 1.823 | 0
1111 | 2022-12-24 18:32 | 8.2 | 21.1 | 36.8 | 35.4 | 1.82 | 0
1112 | 2022-12-24 18:33 | 8.4 | 21 | 36.9 | 35.4 | 1.748 | 0
1113 | 2022-12-24 18:34 | 8.7 | 20.8 | 37.3 | 35.3 | 1.499 | 0
1114 | 2022-12-24 18:35 | 8.6 | 20.8 | 37.7 | 35.7 | 1.509 | 0
1115 | 2022-12-24 18:36 | 8.7 | 20.7 | 38.1 | 36.1 | 1.499 | 0
1116 | 2022-12-24 18:37 | 8.6 | 20.6 | 38.3 | 36.4 | 1.502 | 0
1117 | 2022-12-24 18:38 | 8.9 | 20.6 | 38.8 | 36.7 | 1.502 | 0
1118 | 2022-12-24 18:39 | 9.1 | 20.6 | 39.1 | 37 | 1.504 | 0
1119 | 2022-12-24 18:40 | 8.6 | 20.6 | 39.5 | 37.4 | 1.502 | 0
1120 | 2022-12-24 18:41 | 8.6 | 20.4 | 39.8 | 37.9 | 1.504 | 0
1121 | 2022-12-24 18:42 | 8.3 | 20.5 | 40.2 | 38.7 | 1.508 | 0
1122 | 2022-12-24 18:43 | 8.3 | 20.4 | 40 | 38.8 | 1.502 | 0
1123 | 2022-12-24 18:44 | 8.3 | 20.5 | 40 | 38.7 | 1.503 | 0
1124 | 2022-12-24 18:45 | 8.4 | 20.4 | 40 | 38.8 | 1.386 | 0
1125 | 2022-12-24 18:46 | 8.2 | 20.5 | 40 | 38.4 | 1.089 | 0
1126 | 2022-12-24 18:47 | 8.5 | 20.6 | 39.9 | 37.5 | 1.425 | 0
1127 | 2022-12-24 18:48 | 8.7 | 20.5 | 39.8 | 37.4 | 1.615 | 0
1128 | 2022-12-24 18:49 | 8.8 | 20.7 | 39.6 | 37.1 | 1.661 | 0
1129 | 2022-12-24 18:50 | 8.9 | 20.9 | 39.2 | 36.5 | 1.88 | 0
1130 | 2022-12-24 18:51 | 8.7 | 21.2 | 39 | 36.6 | 1.886 | 0
1131 | 2022-12-24 18:52 | 9 | 21.4 | 38.7 | 36.8 | 1.882 | 0
1132 | 2022-12-24 18:53 | 8.9 | 21.6 | 38.6 | 36.6 | 1.889 | 0
1133 | 2022-12-24 18:54 | 8.6 | 21.6 | 38.5 | 36.5 | 1.889 | 0
1134 | 2022-12-24 18:55 | 8.6 | 21.8 | 38.3 | 36.5 | 1.889 | 0
1135 | 2022-12-24 18:56 | 8.5 | 21.9 | 38.2 | 35.7 | 1.979 | 0
1136 | 2022-12-24 18:57 | 9 | 21.9 | 38 | 36.4 | 1.925 | 0
1137 | 2022-12-24 18:58 | 9 | 21.9 | 37.8 | 36.4 | 1.849 | 0
1138 | 2022-12-24 18:59 | 8.7 | 21.7 | 37.8 | 36.9 | 1.86 | 0
1139 | 2022-12-24 19:00 | 8.5 | 21.4 | 37.7 | 36.9 | 1.827 | 0
1140 | 2022-12-24 19:01 | 8.7 | 21.1 | 37.7 | 36.8 | 1.545 | 0
1141 | 2022-12-24 19:02 | 8.6 | 20.9 | 37.7 | 36.7 | 1.42 | 0
1142 | 2022-12-24 19:03 | 8.3 | 20.7 | 37.6 | 36.4 | 0.974 | 0
1143 | 2022-12-24 19:04 | 8.9 | 20.6 | 37.7 | 36.3 | 0.968 | 0
1144 | 2022-12-24 19:05 | 8.7 | 20.5 | 37.9 | 36.4 | 0.969 | 0
1145 | 2022-12-24 19:06 | 8.6 | 20.3 | 38.4 | 36.6 | 0.97 | 0
1146 | 2022-12-24 19:07 | 8.8 | 20.2 | 38.9 | 35.5 | 1.474 | 0
1147 | 2022-12-24 19:08 | 8.6 | 20.3 | 39.1 | 37 | 1.505 | 0
1148 | 2022-12-24 19:09 | 8.7 | 20.2 | 39.4 | 37.3 | 1.501 | 0
1149 | 2022-12-24 19:10 | 9 | 20.2 | 39.8 | 37.6 | 1.501 | 0
1150 | 2022-12-24 19:11 | 9.5 | 20.2 | 40.2 | 38 | 1.507 | 0
1151 | 2022-12-24 19:12 | 8.8 | 20.3 | 40.8 | 38.3 | 1.509 | 0
1152 | 2022-12-24 19:13 | 8.8 | 20.4 | 40.5 | 38.8 | 1.504 | 0
1153 | 2022-12-24 19:14 | 8.7 | 20.4 | 40.5 | 37.3 | 1.821 | 0
1154 | 2022-12-24 19:15 | 8.8 | 20.5 | 40.3 | 37.7 | 1.827 | 0
1155 | 2022-12-24 19:16 | 9.4 | 20.8 | 39.9 | 37.5 | 1.827 | 0
1156 | 2022-12-24 19:17 | 9.4 | 21.1 | 39.8 | 37.3 | 1.832 | 0
1157 | 2022-12-24 19:18 | 9.8 | 21.3 | 39.6 | 37.7 | 1.824 | 0
1158 | 2022-12-24 19:19 | 9.4 | 21.5 | 39.5 | 37.5 | 1.822 | 0
1159 | 2022-12-24 19:20 | 9.5 | 21.6 | 39.4 | 37.4 | 1.826 | 0
1160 | 2022-12-24 19:21 | 9.9 | 21.8 | 39.2 | 37.3 | 1.825 | 0
1161 | 2022-12-24 19:22 | 9.9 | 21.8 | 39.1 | 37 | 1.613 | 0
1162 | 2022-12-24 19:23 | 9.9 | 21.9 | 39 | 36.9 | 1.617 | 0
1163 | 2022-12-24 19:24 | 10.2 | 21.9 | 38.8 | 36.8 | 1.614 | 0
1164 | 2022-12-24 19:25 | 9.8 | 21.9 | 38.7 | 37.2 | 1.62 | 0
1165 | 2022-12-24 19:26 | 10 | 21.7 | 38.5 | 37.5 | 1.621 | 0
1166 | 2022-12-24 19:27 | 10 | 21.4 | 38.4 | 37.4 | 1.62 | 0
1167 | 2022-12-24 19:28 | 10.7 | 21.2 | 38.5 | 37.3 | 1.606 | 0
1168 | 2022-12-24 19:29 | 10.5 | 21 | 38.4 | 37.3 | 1.48 | 0
1169 | 2022-12-24 19:30 | 10.1 | 20.9 | 38.4 | 36.9 | 1.087 | 0
1170 | 2022-12-24 19:31 | 10.1 | 20.8 | 38.3 | 36.8 | 1.417 | 0
1171 | 2022-12-24 19:32 | 9.8 | 20.7 | 38.2 | 36.4 | 1.501 | 0
1172 | 2022-12-24 19:33 | 9.4 | 20.6 | 38 | 34 | 1.604 | 0
1173 | 2022-12-24 19:34 | 9.4 | 20.6 | 38 | 35.5 | 1.83 | 0
1174 | 2022-12-24 19:35 | 10.1 | 20.6 | 38.2 | 35.7 | 1.829 | 0
1175 | 2022-12-24 19:36 | 9.9 | 20.5 | 38.5 | 35.8 | 1.833 | 0
1176 | 2022-12-24 19:37 | 10.2 | 20.6 | 38.8 | 36.1 | 1.838 | 0
1177 | 2022-12-24 19:38 | 10 | 20.6 | 39.1 | 36.4 | 1.833 | 0
1178 | 2022-12-24 19:39 | 9.7 | 20.6 | 39.4 | 36.7 | 1.827 | 0
1179 | 2022-12-24 19:40 | 9.7 | 20.6 | 39.7 | 36.9 | 1.835 | 0
1180 | 2022-12-24 19:41 | 9.6 | 20.8 | 40 | 37.2 | 1.837 | 0
1181 | 2022-12-24 19:42 | 9.2 | 20.7 | 40.4 | 38.4 | 1.837 | 0
1182 | 2022-12-24 19:43 | 9.1 | 20.6 | 40.3 | 38.7 | 1.839 | 0
1183 | 2022-12-24 19:44 | 9.3 | 20.7 | 40.3 | 38.7 | 1.837 | 0
1184 | 2022-12-24 19:45 | 9.2 | 20.6 | 40.3 | 38.6 | 1.79 | 0
1185 | 2022-12-24 19:46 | 9 | 20.7 | 40.2 | 38.9 | 1.512 | 0
1186 | 2022-12-24 19:47 | 9.1 | 20.6 | 40.1 | 39.1 | 1.507 | 0
1187 | 2022-12-24 19:48 | 9 | 20.5 | 40 | 39 | 1.503 | 0
1188 | 2022-12-24 19:49 | 8.7 | 20.4 | 40.1 | 39 | 1.506 | 0
1189 | 2022-12-24 19:50 | 8.9 | 20.4 | 40 | 39 | 1.495 | 0
1190 | 2022-12-24 19:51 | 8.8 | 20.5 | 39.9 | 38.8 | 1.499 | 0
1191 | 2022-12-24 19:52 | 8.8 | 20.4 | 39.8 | 37.9 | 1.691 | 0
1192 | 2022-12-24 19:53 | 8.8 | 20.5 | 39.7 | 38.3 | 1.556 | 0
1193 | 2022-12-24 19:54 | 8.6 | 20.6 | 39.4 | 38.1 | 1.563 | 0
1194 | 2022-12-24 19:55 | 8.7 | 20.8 | 39.4 | 37.8 | 1.549 | 0
1195 | 2022-12-24 19:56 | 8.6 | 21 | 39.3 | 37.4 | 0.962 | 0
1196 | 2022-12-24 19:57 | 8.6 | 21.2 | 39.3 | 37.1 | 0.948 | 0
1197 | 2022-12-24 19:58 | 8.7 | 21.3 | 39.2 | 37.1 | 0.945 | 0
1198 | 2022-12-24 19:59 | 8.8 | 21.4 | 39 | 37 | 0.948 | 0
1199 | 2022-12-24 20:00 | 8.9 | 21.4 | 39 | 37.2 | 1.392 | 0
1200 | 2022-12-24 20:01 | 8.8 | 21.5 | 38.7 | 36.6 | 1.614 | 0
1201 | 2022-12-24 20:02 | 8.7 | 21.6 | 38.6 | 36.5 | 1.62 | 0
1202 | 2022-12-24 20:03 | 8.8 | 21.7 | 38.5 | 36.4 | 1.614 | 0
1203 | 2022-12-24 20:04 | 8.9 | 21.7 | 38.8 | 36.4 | 1.613 | 0
1204 | 2022-12-24 20:05 | 9 | 21.8 | 38.9 | 36.6 | 1.617 | 0
1205 | 2022-12-24 20:06 | 9.2 | 21.8 | 39.3 | 36 | 1.823 | 0
1206 | 2022-12-24 20:07 | 9 | 21.9 | 39.5 | 36.7 | 1.824 | 0
1207 | 2022-12-24 20:08 | 9.3 | 21.8 | 39.7 | 37.7 | 1.829 | 0
1208 | 2022-12-24 20:09 | 9.6 | 21.7 | 40.1 | 38.1 | 1.831 | 0
1209 | 2022-12-24 20:10 | 10 | 21.4 | 40.5 | 38.4 | 1.829 | 0
1210 | 2022-12-24 20:11 | 10.5 | 21.3 | 40.9 | 38.8 | 1.822 | 0
1211 | 2022-12-24 20:12 | 10.5 | 21 | 41.2 | 39 | 1.718 | 0
1212 | 2022-12-24 20:13 | 10.4 | 20.9 | 41.4 | 39.2 | 1.51 | 0
1213 | 2022-12-24 20:14 | 10 | 20.8 | 41.7 | 39.4 | 1.501 | 0
1214 | 2022-12-24 20:15 | 9.5 | 20.7 | 42 | 39.7 | 1.508 | 0
1215 | 2022-12-24 20:16 | 9.6 | 20.6 | 41.7 | 39.8 | 1.509 | 0
1216 | 2022-12-24 20:17 | 10.1 | 20.6 | 41.6 | 39.6 | 1.513 | 0
1217 | 2022-12-24 20:18 | 10.4 | 20.5 | 41.5 | 35.8 | 1.8 | 0
1218 | 2022-12-24 20:19 | 10.2 | 20.6 | 41.4 | 38.6 | 1.828 | 0
1219 | 2022-12-24 20:20 | 9.6 | 20.6 | 40.9 | 38.6 | 1.834 | 0
1220 | 2022-12-24 20:21 | 9.8 | 20.5 | 40.7 | 38.1 | 1.836 | 0
1221 | 2022-12-24 20:22 | 9.6 | 20.6 | 40.6 | 38 | 1.834 | 0
1222 | 2022-12-24 20:23 | 9.8 | 20.6 | 40.3 | 38.4 | 1.84 | 0
1223 | 2022-12-24 20:24 | 9.7 | 20.7 | 40.2 | 38.2 | 1.833 | 0
1224 | 2022-12-24 20:25 | 9.5 | 20.8 | 40.1 | 38.1 | 1.837 | 0
1225 | 2022-12-24 20:26 | 9.6 | 20.7 | 40 | 38.8 | 1.838 | 0
1226 | 2022-12-24 20:27 | 10.1 | 20.7 | 39.9 | 38.8 | 1.652 | 0
1227 | 2022-12-24 20:28 | 10.2 | 20.7 | 39.8 | 38.7 | 0 | 0
1228 | 2022-12-24 20:29 | 10.2 | 20.7 | 39.6 | 38.2 | 0 | 0
1229 | 2022-12-24 20:30 | 10 | 20.6 | 39.4 | 37.7 | 0 | 0
1230 | 2022-12-24 20:31 | 9.7 | 20.6 | 39.1 | 37.2 | 0 | 0
1231 | 2022-12-24 20:32 | 10.1 | 20.4 | 39.1 | 37.3 | 0 | 0
1232 | 2022-12-24 20:33 | 10.2 | 20.3 | 39.5 | 38.5 | 0.926 | 0
1233 | 2022-12-24 20:34 | 10.4 | 20.4 | 39.4 | 39.1 | 0.451 | 0
1234 | 2022-12-24 20:35 | 10.4 | 20.4 | 39.6 | 33.1 | 0.849 | 0
1235 | 2022-12-24 20:36 | 10.8 | 20.4 | 40.1 | 37.4 | 0.944 | 0
1236 | 2022-12-24 20:37 | 11 | 20.5 | 40.5 | 38 | 1.424 | 0
1237 | 2022-12-24 20:38 | 11 | 20.7 | 40.8 | 38 | 1.564 | 0
1238 | 2022-12-24 20:39 | 11.3 | 21 | 41.2 | 38.5 | 1.557 | 0
1239 | 2022-12-24 20:40 | 11.3 | 21.1 | 41.5 | 38.9 | 1.567 | 0
1240 | 2022-12-24 20:41 | 10.9 | 21.2 | 41.9 | 37.6 | 1.825 | 0
1241 | 2022-12-24 20:42 | 10.9 | 21.4 | 42.2 | 39.1 | 1.837 | 0
1242 | 2022-12-24 20:43 | 10.9 | 21.5 | 42.1 | 39.3 | 1.829 | 0
1243 | 2022-12-24 20:44 | 11 | 21.6 | 42 | 39.2 | 1.838 | 0
1244 | 2022-12-24 20:45 | 10.9 | 21.7 | 41.8 | 39.1 | 1.833 | 0
1245 | 2022-12-24 20:46 | 10.7 | 21.8 | 41.6 | 39 | 1.828 | 0
1246 | 2022-12-24 20:47 | 10.3 | 21.9 | 41.4 | 38.7 | 1.831 | 0
1247 | 2022-12-24 20:48 | 10.5 | 22 | 41.2 | 38.6 | 1.832 | 0
1248 | 2022-12-24 20:49 | 11.1 | 22 | 40.9 | 39 | 1.833 | 0
1249 | 2022-12-24 20:50 | 11.5 | 21.8 | 40.8 | 39.1 | 1.832 | 0
1250 | 2022-12-24 20:51 | 10.8 | 21.4 | 40.7 | 39 | 1.837 | 0
1251 | 2022-12-24 20:52 | 10.3 | 21.3 | 40.7 | 39 | 1.825 | 0
1252 | 2022-12-24 20:53 | 10.1 | 21.1 | 40.6 | 38.9 | 1.77 | 0
1253 | 2022-12-24 20:54 | 10.2 | 21 | 40.5 | 39.2 | 1.509 | 0
1254 | 2022-12-24 20:55 | 10 | 20.9 | 40.4 | 39.2 | 1.508 | 0
1255 | 2022-12-24 20:56 | 9.6 | 20.8 | 40.3 | 39.1 | 1.509 | 0
1256 | 2022-12-24 20:57 | 9.2 | 20.7 | 40.2 | 39 | 1.497 | 0
1257 | 2022-12-24 20:58 | 9 | 20.6 | 40.2 | 38.9 | 1.129 | 0
1258 | 2022-12-24 20:59 | 9 | 20.6 | 40.1 | 38.6 | 1.1 | 0
1259 | 2022-12-24 21:00 | 8.8 | 20.6 | 40.1 | 38.5 | 0 | 0
1260 | 2022-12-24 21:01 | 8.6 | 20.5 | 39.9 | 38.2 | 0 | 0
1261 | 2022-12-24 21:02 | 8.9 | 20.5 | 39.7 | 37.8 | 0 | 0
1262 | 2022-12-24 21:03 | 9.1 | 20.4 | 39.4 | 37.3 | 0 | 0
1263 | 2022-12-24 21:04 | 9.1 | 20.4 | 39.2 | 36.8 | 0 | 0
1264 | 2022-12-24 21:05 | 9 | 20.3 | 38.9 | 36.3 | 0 | 0
1265 | 2022-12-24 21:06 | 8.7 | 20.3 | 38.7 | 35.9 | 0 | 0
1266 | 2022-12-24 21:07 | 9.5 | 20.3 | 38.5 | 35.5 | 0 | 0
1267 | 2022-12-24 21:08 | 9.8 | 20.3 | 38.2 | 35.1 | 0 | 0
1268 | 2022-12-24 21:09 | 10.3 | 20.1 | 38 | 34.7 | 0 | 0
1269 | 2022-12-24 21:10 | 10.4 | 20.1 | 37.7 | 34.3 | 0 | 0
1270 | 2022-12-24 21:11 | 10.6 | 20.1 | 37.5 | 34 | 0 | 0
1271 | 2022-12-24 21:12 | 10.1 | 20.1 | 37.2 | 33.6 | 0 | 0
1272 | 2022-12-24 21:13 | 10 | 20.1 | 37 | 33.3 | 0 | 0
1273 | 2022-12-24 21:14 | 10.2 | 20.1 | 36.8 | 32.9 | 0 | 0
1274 | 2022-12-24 21:15 | 10 | 20 | 36.5 | 32.6 | 0 | 0
1275 | 2022-12-24 21:16 | 9.9 | 20 | 36.3 | 32.3 | 0 | 0
1276 | 2022-12-24 21:17 | 10 | 20 | 36.1 | 32 | 0 | 0
1277 | 2022-12-24 21:18 | 9.7 | 20 | 35.9 | 31.7 | 0 | 0
1278 | 2022-12-24 21:19 | 9.5 | 20 | 35.7 | 31.5 | 0 | 0
1279 | 2022-12-24 21:20 | 9.5 | 19.9 | 35.5 | 31.2 | 0 | 0
1280 | 2022-12-24 21:21 | 9.3 | 19.9 | 35.2 | 30.9 | 0 | 0
1281 | 2022-12-24 21:22 | 9.2 | 19.9 | 35 | 30.7 | 0 | 0
1282 | 2022-12-24 21:23 | 9 | 19.9 | 34.8 | 30.4 | 0 | 0
1283 | 2022-12-24 21:24 | 8.8 | 19.8 | 34.6 | 30.2 | 0 | 0
1284 | 2022-12-24 21:25 | 8.6 | 19.8 | 34.4 | 29.9 | 0 | 0
1285 | 2022-12-24 21:26 | 8.5 | 19.8 | 34.2 | 29.7 | 0 | 0
1286 | 2022-12-24 21:27 | 8.5 | 19.8 | 34 | 29.5 | 0 | 0
1287 | 2022-12-24 21:28 | 9.1 | 19.8 | 33.8 | 29.3 | 0 | 0
1288 | 2022-12-24 21:29 | 9.4 | 19.7 | 33.6 | 29 | 0 | 0
1289 | 2022-12-24 21:30 | 9.6 | 19.8 | 33.4 | 28.8 | 0 | 0
1290 | 2022-12-24 21:31 | 9.2 | 19.8 | 33.2 | 28.6 | 0 | 0
1291 | 2022-12-24 21:32 | 9.1 | 19.7 | 33 | 28.4 | 0 | 0
1292 | 2022-12-24 21:33 | 9.4 | 19.7 | 32.8 | 28.2 | 0 | 0
1293 | 2022-12-24 21:34 | 10 | 19.7 | 32.6 | 28 | 0 | 0
1294 | 2022-12-24 21:35 | 10.1 | 19.7 | 32.4 | 27.8 | 0 | 0
1295 | 2022-12-24 21:36 | 10.1 | 19.7 | 32.2 | 27.5 | 0 | 0
1296 | 2022-12-24 21:37 | 9.7 | 19.7 | 32 | 27.4 | 0 | 0
1297 | 2022-12-24 21:38 | 9.7 | 19.7 | 31.8 | 27.2 | 0 | 0
1298 | 2022-12-24 21:39 | 9.8 | 19.6 | 31.7 | 27 | 0 | 0
1299 | 2022-12-24 21:40 | 9.9 | 19.7 | 31.5 | 26.8 | 0 | 0
1300 | 2022-12-24 21:41 | 10.2 | 19.6 | 31.3 | 26.6 | 0 | 0
1301 | 2022-12-24 21:42 | 9.9 | 19.6 | 31.1 | 26.4 | 0 | 0
1302 | 2022-12-24 21:43 | 9.9 | 19.6 | 30.9 | 26.3 | 0 | 0
1303 | 2022-12-24 21:44 | 9.6 | 19.6 | 30.7 | 26.1 | 0 | 0
1304 | 2022-12-24 21:45 | 9.5 | 19.6 | 30.6 | 25.9 | 0 | 0
1305 | 2022-12-24 21:46 | 9.5 | 19.6 | 30.4 | 25.8 | 0 | 0
1306 | 2022-12-24 21:47 | 9.1 | 19.7 | 30.2 | 25.6 | 0 | 0
1307 | 2022-12-24 21:48 | 9.4 | 19.6 | 30.1 | 25.4 | 0 | 0
1308 | 2022-12-24 21:49 | 9.4 | 19.6 | 29.9 | 25.3 | 0 | 0
1309 | 2022-12-24 21:50 | 9.9 | 19.6 | 29.7 | 25.1 | 0 | 0
1310 | 2022-12-24 21:51 | 9.5 | 19.6 | 29.5 | 25 | 0 | 0
1311 | 2022-12-24 21:52 | 9.3 | 19.6 | 29.4 | 24.8 | 0 | 0
1312 | 2022-12-24 21:53 | 8.9 | 19.6 | 29.2 | 24.7 | 0 | 0
1313 | 2022-12-24 21:54 | 9.6 | 19.5 | 29 | 24.5 | 0 | 0
1314 | 2022-12-24 21:55 | 9.9 | 19.6 | 28.9 | 24.4 | 0 | 0
1315 | 2022-12-24 21:56 | 9.6 | 19.5 | 28.7 | 24.2 | 0 | 0
1316 | 2022-12-24 21:57 | 10.1 | 19.5 | 28.5 | 24.1 | 0 | 0
1317 | 2022-12-24 21:58 | 10.1 | 19.5 | 28.4 | 23.9 | 0 | 0
1318 | 2022-12-24 21:59 | 10.2 | 19.5 | 28.2 | 23.8 | 0 | 0
1319 | 2022-12-24 22:00 | 10.9 | 19.6 | 28.1 | 23.6 | 0 | 0
1320 | 2022-12-24 22:01 | 10.3 | 19.5 | 27.9 | 23.5 | 0 | 0
1321 | 2022-12-24 22:02 | 9.9 | 19.5 | 27.8 | 23.4 | 0 | 0
1322 | 2022-12-24 22:03 | 10.4 | 19.5 | 27.6 | 23.3 | 0 | 0
1323 | 2022-12-24 22:04 | 10.7 | 19.5 | 27.5 | 23.1 | 0 | 0
1324 | 2022-12-24 22:05 | 11.4 | 19.5 | 27.3 | 23 | 0 | 0
1325 | 2022-12-24 22:06 | 11.5 | 19.5 | 27.2 | 22.9 | 0 | 0
1326 | 2022-12-24 22:07 | 11.4 | 19.5 | 27 | 22.8 | 0 | 0
1327 | 2022-12-24 22:08 | 11.2 | 19.5 | 26.9 | 22.7 | 0 | 0
1328 | 2022-12-24 22:09 | 11.3 | 19.6 | 26.7 | 22.6 | 0 | 0
1329 | 2022-12-24 22:10 | 11.1 | 19.6 | 26.6 | 22.4 | 0 | 0
1330 | 2022-12-24 22:11 | 11.1 | 19.6 | 26.5 | 22.3 | 0 | 0
1331 | 2022-12-24 22:12 | 11.4 | 19.5 | 26.3 | 22.2 | 0 | 0
1332 | 2022-12-24 22:13 | 11.5 | 19.4 | 26.2 | 22.1 | 0 | 0
1333 | 2022-12-24 22:14 | 11.9 | 19.4 | 26.1 | 22 | 0 | 0
1334 | 2022-12-24 22:15 | 11.7 | 19.4 | 25.9 | 21.9 | 0 | 0
1335 | 2022-12-24 22:16 | 11.2 | 19.4 | 25.8 | 21.8 | 0 | 0
1336 | 2022-12-24 22:17 | 11.2 | 19.4 | 25.7 | 21.7 | 0 | 0
1337 | 2022-12-24 22:18 | 11.3 | 19.4 | 25.5 | 21.6 | 0 | 0
1338 | 2022-12-24 22:19 | 11.6 | 19.5 | 25.4 | 21.5 | 0 | 0
1339 | 2022-12-24 22:20 | 11.7 | 19.4 | 25.3 | 21.4 | 0 | 0
1340 | 2022-12-24 22:21 | 11.6 | 19.4 | 25.2 | 21.3 | 0 | 0
1341 | 2022-12-24 22:22 | 11.7 | 19.4 | 25.1 | 21.2 | 0 | 0
1342 | 2022-12-24 22:23 | 11.5 | 19.4 | 24.9 | 21.1 | 0 | 0
1343 | 2022-12-24 22:24 | 11.8 | 19.4 | 24.8 | 21 | 0 | 0
1344 | 2022-12-24 22:25 | 11.9 | 19.4 | 24.7 | 20.9 | 0 | 0
1345 | 2022-12-24 22:26 | 11.6 | 19.4 | 24.6 | 20.8 | 0 | 0
1346 | 2022-12-24 22:27 | 11.7 | 19.4 | 24.5 | 20.7 | 0 | 0
1347 | 2022-12-24 22:28 | 12 | 19.4 | 24.4 | 20.6 | 0 | 0
1348 | 2022-12-24 22:29 | 11.9 | 19.4 | 24.3 | 20.5 | 0 | 0
1349 | 2022-12-24 22:30 | 11.9 | 19.4 | 24.2 | 20.5 | 0 | 0
1350 | 2022-12-24 22:31 | 11.5 | 19.4 | 24.1 | 20.4 | 0 | 0
1351 | 2022-12-24 22:32 | 11.4 | 19.5 | 24 | 20.3 | 0 | 0
1352 | 2022-12-24 22:33 | 11.7 | 19.4 | 23.9 | 20.2 | 0 | 0
1353 | 2022-12-24 22:34 | 11.7 | 19.3 | 23.8 | 20.1 | 0 | 0
1354 | 2022-12-24 22:35 | 11.6 | 19.4 | 23.7 | 20 | 0 | 0
1355 | 2022-12-24 22:36 | 11.7 | 19.3 | 23.6 | 20 | 0 | 0
1356 | 2022-12-24 22:37 | 11.7 | 19.4 | 23.5 | 19.9 | 0 | 0
1357 | 2022-12-24 22:38 | 11.7 | 19.3 | 23.4 | 19.8 | 0 | 0
1358 | 2022-12-24 22:39 | 11.6 | 19.3 | 23.3 | 19.7 | 0 | 0
1359 | 2022-12-24 22:40 | 11.3 | 19.3 | 23.2 | 19.7 | 0 | 0
1360 | 2022-12-24 22:41 | 11.4 | 19.3 | 23.1 | 19.6 | 0 | 0
1361 | 2022-12-24 22:42 | 11.2 | 19.3 | 23 | 19.5 | 0 | 0
1362 | 2022-12-24 22:43 | 11.1 | 19.4 | 22.9 | 19.5 | 0 | 0
1363 | 2022-12-24 22:44 | 11.5 | 19.3 | 22.8 | 19.4 | 0 | 0
1364 | 2022-12-24 22:45 | 11.6 | 19.3 | 22.7 | 19.3 | 0 | 0
1365 | 2022-12-24 22:46 | 12 | 19.3 | 22.6 | 19.3 | 0 | 0
1366 | 2022-12-24 22:47 | 11.8 | 19.3 | 22.6 | 19.2 | 0 | 0
1367 | 2022-12-24 22:48 | 11.6 | 19.3 | 22.5 | 19.1 | 0 | 0
1368 | 2022-12-24 22:49 | 11.7 | 19.3 | 22.4 | 19.1 | 0 | 0
1369 | 2022-12-24 22:50 | 11.9 | 19.3 | 22.3 | 19 | 0 | 0
1370 | 2022-12-24 22:51 | 11.8 | 19.3 | 22.2 | 18.9 | 0 | 0
1371 | 2022-12-24 22:52 | 11.9 | 19.3 | 22.2 | 18.9 | 0 | 0
1372 | 2022-12-24 22:53 | 11.8 | 19.2 | 22.1 | 18.8 | 0 | 0
1373 | 2022-12-24 22:54 | 12.1 | 19.3 | 22 | 18.7 | 0 | 0
1374 | 2022-12-24 22:55 | 11.7 | 19.2 | 21.9 | 18.7 | 0 | 0
1375 | 2022-12-24 22:56 | 11.6 | 19.3 | 21.9 | 18.6 | 0 | 0
1376 | 2022-12-24 22:57 | 11.6 | 19.2 | 21.8 | 18.6 | 0 | 0
1377 | 2022-12-24 22:58 | 11.8 | 19.2 | 21.7 | 18.5 | 0 | 0
1378 | 2022-12-24 22:59 | 11.6 | 19.2 | 21.6 | 18.4 | 0 | 0
1379 | 2022-12-24 23:00 | 11.7 | 19.3 | 21.6 | 18.4 | 0 | 0
1380 | 2022-12-24 23:01 | 11.3 | 19.2 | 21.5 | 18.3 | 0 | 0
1381 | 2022-12-24 23:02 | 11.4 | 19.2 | 21.4 | 18.3 | 0 | 0
1382 | 2022-12-24 23:03 | 11.3 | 19.2 | 21.3 | 18.2 | 0 | 0
1383 | 2022-12-24 23:04 | 11.2 | 19.2 | 21.3 | 18.2 | 0 | 0
1384 | 2022-12-24 23:05 | 11.5 | 19.2 | 21.2 | 18.1 | 0 | 0
1385 | 2022-12-24 23:06 | 11.7 | 19.1 | 21.2 | 18.1 | 0 | 0
1386 | 2022-12-24 23:07 | 11.4 | 19.2 | 21.1 | 18 | 0 | 0
1387 | 2022-12-24 23:08 | 11.3 | 19.2 | 21 | 18 | 0 | 0
1388 | 2022-12-24 23:09 | 11.4 | 19.1 | 21 | 17.9 | 0 | 0
1389 | 2022-12-24 23:10 | 11.3 | 19.2 | 20.9 | 17.9 | 0 | 0
1390 | 2022-12-24 23:11 | 11.4 | 19.2 | 20.8 | 17.8 | 0 | 0
1391 | 2022-12-24 23:12 | 11.4 | 19.2 | 20.8 | 17.8 | 0 | 0
1392 | 2022-12-24 23:13 | 11.4 | 19.1 | 20.7 | 17.7 | 0 | 0
1393 | 2022-12-24 23:14 | 11.5 | 19.1 | 20.6 | 17.7 | 0 | 0
1394 | 2022-12-24 23:15 | 11.5 | 19.2 | 20.6 | 17.6 | 0 | 0
1395 | 2022-12-24 23:16 | 11.3 | 19.1 | 20.5 | 17.6 | 0 | 0
1396 | 2022-12-24 23:17 | 11.3 | 19.1 | 20.4 | 17.5 | 0 | 0
1397 | 2022-12-24 23:18 | 11.2 | 19.1 | 20.4 | 17.5 | 0 | 0
1398 | 2022-12-24 23:19 | 10.8 | 19.1 | 20.3 | 17.4 | 0 | 0
1399 | 2022-12-24 23:20 | 10.9 | 19.1 | 20.3 | 17.4 | 0 | 0
1400 | 2022-12-24 23:21 | 10.9 | 19.1 | 20.2 | 17.3 | 0 | 0
1401 | 2022-12-24 23:22 | 10.7 | 19.1 | 20.2 | 17.3 | 0 | 0
1402 | 2022-12-24 23:23 | 10.9 | 19.1 | 20.1 | 17.2 | 0 | 0
1403 | 2022-12-24 23:24 | 10.9 | 19.2 | 20 | 17.2 | 0 | 0
1404 | 2022-12-24 23:25 | 10.8 | 19.2 | 20 | 17.1 | 0 | 0
1405 | 2022-12-24 23:26 | 10.9 | 19.1 | 19.9 | 17.1 | 0 | 0
1406 | 2022-12-24 23:27 | 10.7 | 19.1 | 19.9 | 17.1 | 0 | 0
1407 | 2022-12-24 23:28 | 10.8 | 19.2 | 19.8 | 17 | 0 | 0
1408 | 2022-12-24 23:29 | 11 | 19.2 | 19.7 | 17 | 0 | 0
1409 | 2022-12-24 23:30 | 10.8 | 19.2 | 19.7 | 16.9 | 0 | 0
1410 | 2022-12-24 23:31 | 10.5 | 19.1 | 19.6 | 16.9 | 0 | 0
1411 | 2022-12-24 23:32 | 10.7 | 19.1 | 19.6 | 16.8 | 0 | 0
1412 | 2022-12-24 23:33 | 10.7 | 19.1 | 19.5 | 16.8 | 0 | 0
1413 | 2022-12-24 23:34 | 11 | 19.1 | 19.5 | 16.7 | 0 | 0
1414 | 2022-12-24 23:35 | 10.3 | 19.1 | 19.4 | 16.7 | 0 | 0
1415 | 2022-12-24 23:36 | 10.6 | 19 | 19.4 | 16.7 | 0 | 0
1416 | 2022-12-24 23:37 | 10.5 | 19 | 19.4 | 16.6 | 0 | 0
1417 | 2022-12-24 23:38 | 10.9 | 19 | 19.3 | 16.6 | 0 | 0
1418 | 2022-12-24 23:39 | 10.7 | 19 | 19.2 | 16.5 | 0 | 0
1419 | 2022-12-24 23:40 | 10.9 | 19.1 | 19.2 | 16.5 | 0 | 0
1420 | 2022-12-24 23:41 | 10.8 | 19.1 | 19.1 | 16.5 | 0 | 0
1421 | 2022-12-24 23:42 | 10.9 | 19 | 19.1 | 16.4 | 0 | 0
1422 | 2022-12-24 23:43 | 10.3 | 19.1 | 19 | 16.4 | 0 | 0
1423 | 2022-12-24 23:44 | 10 | 19 | 19 | 16.3 | 0 | 0
1424 | 2022-12-24 23:45 | 10 | 19.1 | 19 | 16.3 | 0 | 0
1425 | 2022-12-24 23:46 | 9.9 | 19.1 | 18.9 | 16.3 | 0 | 0
1426 | 2022-12-24 23:47 | 10.1 | 19 | 18.9 | 16.2 | 0 | 0
1427 | 2022-12-24 23:48 | 10.6 | 19 | 18.8 | 16.2 | 0 | 0
1428 | 2022-12-24 23:49 | 10.6 | 19 | 18.8 | 16.1 | 0 | 0
1429 | 2022-12-24 23:50 | 10.3 | 19 | 18.7 | 16.1 | 0 | 0
1430 | 2022-12-24 23:51 | 9.9 | 19 | 18.7 | 16.1 | 0 | 0
1431 | 2022-12-24 23:52 | 9.5 | 19 | 18.6 | 16 | 0 | 0
1432 | 2022-12-24 23:53 | 9.9 | 18.9 | 18.6 | 16 | 0 | 0
1433 | 2022-12-24 23:54 | 9.9 | 19 | 18.5 | 15.9 | 0 | 0
1434 | 2022-12-24 23:55 | 9.4 | 19 | 18.5 | 15.9 | 0 | 0
1435 | 2022-12-24 23:56 | 9.2 | 19 | 18.4 | 15.9 | 0 | 0
1436 | 2022-12-24 23:57 | 8.8 | 19 | 18.4 | 15.8 | 0 | 0
1437 | 2022-12-24 23:58 | 8.7 | 18.9 | 18.3 | 15.8 | 0 | 0
1438 | 2022-12-24 23:59 | 8.6 | 18.9 | 18.3 | 15.8 | 0 | 0

## 25-12-2022_WITH HEAT
| Date&time_x | OUTDOOR_TEMP | INDOOR_TEMP | SH_INLET | SH_RETURN | FLOW_FAN_COILS_INDOOR | PYRANOMETER
0 | 2022-12-25 | 8.5 | 18.9 | 18.3 | 15.7 | 0 | 0
1 | 2022-12-25 00:01 | 8.6 | 19 | 18.2 | 15.7 | 0 | 0
2 | 2022-12-25 00:02 | 8.3 | 18.9 | 18.2 | 15.7 | 0 | 0
3 | 2022-12-25 00:03 | 8.5 | 19 | 18.1 | 15.6 | 0 | 0
4 | 2022-12-25 00:04 | 8.6 | 18.9 | 18.1 | 15.6 | 0 | 0
5 | 2022-12-25 00:05 | 8.9 | 18.9 | 18 | 15.5 | 0 | 0
6 | 2022-12-25 00:06 | 8.7 | 18.9 | 18 | 15.5 | 0 | 0
7 | 2022-12-25 00:07 | 8.8 | 19 | 17.9 | 15.5 | 0 | 0
8 | 2022-12-25 00:08 | 8.7 | 18.9 | 17.9 | 15.4 | 0 | 0
9 | 2022-12-25 00:09 | 8.4 | 18.9 | 17.8 | 15.4 | 0 | 0
10 | 2022-12-25 00:10 | 8.8 | 18.9 | 17.8 | 15.4 | 0 | 0
11 | 2022-12-25 00:11 | 8.7 | 18.9 | 17.7 | 15.3 | 0 | 0
12 | 2022-12-25 00:12 | 8.6 | 18.9 | 17.7 | 15.3 | 0 | 0
13 | 2022-12-25 00:13 | 9.1 | 18.9 | 17.6 | 15.2 | 0 | 0
14 | 2022-12-25 00:14 | 9.3 | 18.9 | 17.6 | 15.2 | 0 | 0
15 | 2022-12-25 00:15 | 9.3 | 18.8 | 17.6 | 15.2 | 0 | 0
16 | 2022-12-25 00:16 | 9.5 | 18.9 | 17.5 | 15.1 | 0 | 0
17 | 2022-12-25 00:17 | 9 | 18.9 | 17.5 | 15.1 | 0 | 0
18 | 2022-12-25 00:18 | 8.7 | 18.9 | 17.4 | 15 | 0 | 0
19 | 2022-12-25 00:19 | 8.5 | 18.9 | 17.4 | 15 | 0 | 0
20 | 2022-12-25 00:20 | 8.4 | 18.9 | 17.4 | 15 | 0 | 0
21 | 2022-12-25 00:21 | 8.2 | 18.8 | 17.3 | 14.9 | 0 | 0
22 | 2022-12-25 00:22 | 8.2 | 18.8 | 17.3 | 14.9 | 0 | 0
23 | 2022-12-25 00:23 | 8.2 | 18.9 | 17.2 | 14.9 | 0 | 0
24 | 2022-12-25 00:24 | 8.2 | 18.9 | 17.2 | 14.8 | 0 | 0
25 | 2022-12-25 00:25 | 8.5 | 18.8 | 17.1 | 14.8 | 0 | 0
26 | 2022-12-25 00:26 | 8.2 | 18.9 | 17.1 | 14.8 | 0 | 0
27 | 2022-12-25 00:27 | 8 | 18.9 | 17.1 | 14.7 | 0 | 0
28 | 2022-12-25 00:28 | 8.5 | 18.8 | 17 | 14.7 | 0 | 0
29 | 2022-12-25 00:29 | 8.2 | 18.9 | 17 | 14.7 | 0 | 0
30 | 2022-12-25 00:30 | 8 | 18.8 | 16.9 | 14.6 | 0 | 0
31 | 2022-12-25 00:31 | 8 | 18.9 | 16.9 | 14.6 | 0 | 0
32 | 2022-12-25 00:32 | 8 | 18.9 | 16.9 | 14.6 | 0 | 0
33 | 2022-12-25 00:33 | 7.9 | 18.9 | 16.8 | 14.5 | 0 | 0
34 | 2022-12-25 00:34 | 8.1 | 18.8 | 16.8 | 14.5 | 0 | 0
35 | 2022-12-25 00:35 | 8.5 | 18.8 | 16.8 | 14.5 | 0 | 0
36 | 2022-12-25 00:36 | 8.2 | 18.8 | 16.8 | 14.4 | 0 | 0
37 | 2022-12-25 00:37 | 8 | 18.9 | 16.7 | 14.4 | 0 | 0
38 | 2022-12-25 00:38 | 8.1 | 18.9 | 16.7 | 14.4 | 0 | 0
39 | 2022-12-25 00:39 | 8.8 | 18.9 | 16.7 | 14.3 | 0 | 0
40 | 2022-12-25 00:40 | 8.6 | 18.8 | 16.6 | 14.3 | 0 | 0
41 | 2022-12-25 00:41 | 8.3 | 18.8 | 16.6 | 14.3 | 0 | 0
42 | 2022-12-25 00:42 | 8.1 | 18.8 | 16.5 | 14.2 | 0 | 0
43 | 2022-12-25 00:43 | 7.9 | 18.8 | 16.5 | 14.2 | 0 | 0
44 | 2022-12-25 00:44 | 8.1 | 18.8 | 16.5 | 14.2 | 0 | 0
45 | 2022-12-25 00:45 | 8 | 18.8 | 16.4 | 14.1 | 0 | 0
46 | 2022-12-25 00:46 | 7.8 | 18.8 | 16.4 | 14.1 | 0 | 0
47 | 2022-12-25 00:47 | 7.9 | 18.8 | 16.4 | 14.1 | 0 | 0
48 | 2022-12-25 00:48 | 8 | 18.8 | 16.3 | 14 | 0 | 0
49 | 2022-12-25 00:49 | 7.8 | 18.8 | 16.3 | 14 | 0 | 0
50 | 2022-12-25 00:50 | 7.8 | 18.8 | 16.3 | 14 | 0 | 0
51 | 2022-12-25 00:51 | 7.8 | 18.7 | 16.2 | 14 | 0 | 0
52 | 2022-12-25 00:52 | 7.9 | 18.7 | 16.2 | 13.9 | 0 | 0
53 | 2022-12-25 00:53 | 7.8 | 18.7 | 16.2 | 13.9 | 0 | 0
54 | 2022-12-25 00:54 | 7.9 | 18.7 | 16.1 | 13.9 | 0 | 0
55 | 2022-12-25 00:55 | 7.7 | 18.7 | 16.1 | 13.8 | 0 | 0
56 | 2022-12-25 00:56 | 8.7 | 18.8 | 16.1 | 13.8 | 0 | 0
57 | 2022-12-25 00:57 | 8.1 | 18.7 | 16 | 13.8 | 0 | 0
58 | 2022-12-25 00:58 | 7.9 | 18.7 | 16 | 13.7 | 0 | 0
59 | 2022-12-25 00:59 | 7.7 | 18.7 | 15.9 | 13.7 | 0 | 0
60 | 2022-12-25 01:00 | 7.8 | 18.7 | 15.9 | 13.7 | 0 | 0
61 | 2022-12-25 01:01 | 7.7 | 18.7 | 15.9 | 13.7 | 0 | 0
62 | 2022-12-25 01:02 | 7.9 | 18.6 | 15.8 | 13.6 | 0 | 0
63 | 2022-12-25 01:03 | 7.7 | 18.6 | 15.8 | 13.6 | 0 | 0
64 | 2022-12-25 01:04 | 8 | 18.6 | 15.8 | 13.6 | 0 | 0
65 | 2022-12-25 01:05 | 7.9 | 18.7 | 15.8 | 13.5 | 0 | 0
66 | 2022-12-25 01:06 | 8 | 18.7 | 15.7 | 13.5 | 0 | 0
67 | 2022-12-25 01:07 | 7.9 | 18.7 | 15.7 | 13.5 | 0 | 0
68 | 2022-12-25 01:08 | 7.8 | 18.6 | 15.7 | 13.4 | 0 | 0
69 | 2022-12-25 01:09 | 7.7 | 18.6 | 15.7 | 14.1 | 0 | 0
70 | 2022-12-25 01:10 | 7.6 | 18.6 | 15.7 | 14.1 | 0 | 0
71 | 2022-12-25 01:11 | 7.8 | 18.6 | 16.4 | 14.9 | 0.408 | 0
72 | 2022-12-25 01:12 | 7.7 | 18.6 | 37.9 | 17.5 | 0.918 | 0
73 | 2022-12-25 01:13 | 7.6 | 18.6 | 37.7 | 33.9 | 0.948 | 0
74 | 2022-12-25 01:14 | 7.6 | 18.6 | 37 | 34.8 | 0.92 | 0
75 | 2022-12-25 01:15 | 7.6 | 18.6 | 36.8 | 34.6 | 0.977 | 0
76 | 2022-12-25 01:16 | 7.4 | 18.7 | 36.8 | 34.6 | 0.979 | 0
77 | 2022-12-25 01:17 | 7.5 | 18.7 | 35.3 | 34.9 | 0.974 | 0
78 | 2022-12-25 01:18 | 7.5 | 18.7 | 36.7 | 33.7 | 0 | 0
79 | 2022-12-25 01:19 | 7.6 | 18.8 | 37.2 | 34.3 | 0 | 0
80 | 2022-12-25 01:20 | 7.4 | 18.8 | 36.8 | 33.9 | 0 | 0
81 | 2022-12-25 01:21 | 7.6 | 18.9 | 36.5 | 33.2 | 0 | 0
82 | 2022-12-25 01:22 | 7.4 | 18.9 | 36.2 | 32.7 | 0 | 0
83 | 2022-12-25 01:23 | 7.6 | 18.8 | 35.8 | 32.1 | 0 | 0
84 | 2022-12-25 01:24 | 7.5 | 18.8 | 35.5 | 31.6 | 0 | 0
85 | 2022-12-25 01:25 | 7.4 | 18.8 | 35.2 | 31.1 | 0 | 0
86 | 2022-12-25 01:26 | 7.4 | 18.7 | 35 | 30.7 | 0 | 0
87 | 2022-12-25 01:27 | 7.4 | 18.7 | 34.7 | 30.2 | 0 | 0
88 | 2022-12-25 01:28 | 7.4 | 18.7 | 34.4 | 29.8 | 0 | 0
89 | 2022-12-25 01:29 | 7.5 | 18.7 | 34.2 | 29.4 | 0 | 0
90 | 2022-12-25 01:30 | 7.5 | 18.7 | 33.9 | 29.1 | 0 | 0
91 | 2022-12-25 01:31 | 7.3 | 18.7 | 33.7 | 28.7 | 0 | 0
92 | 2022-12-25 01:32 | 7.3 | 18.7 | 33.5 | 28.4 | 0 | 0
93 | 2022-12-25 01:33 | 7.4 | 18.7 | 33.2 | 28.1 | 0 | 0
94 | 2022-12-25 01:34 | 7.5 | 18.7 | 33 | 27.8 | 0 | 0
95 | 2022-12-25 01:35 | 7.4 | 18.6 | 32.8 | 27.5 | 0 | 0
96 | 2022-12-25 01:36 | 7.4 | 18.6 | 32.6 | 27.2 | 0 | 0
97 | 2022-12-25 01:37 | 7.4 | 18.6 | 32.4 | 26.9 | 0 | 0
98 | 2022-12-25 01:38 | 7.4 | 18.6 | 32.2 | 26.7 | 0 | 0
99 | 2022-12-25 01:39 | 7.2 | 18.6 | 31.9 | 26.4 | 0 | 0
100 | 2022-12-25 01:40 | 7.4 | 18.6 | 31.7 | 26.2 | 0 | 0
101 | 2022-12-25 01:41 | 7.3 | 18.6 | 31.5 | 25.9 | 0 | 0
102 | 2022-12-25 01:42 | 7.2 | 18.6 | 31.3 | 25.7 | 0 | 0
103 | 2022-12-25 01:43 | 7.2 | 18.6 | 31.1 | 25.5 | 0 | 0
104 | 2022-12-25 01:44 | 7.1 | 18.6 | 30.9 | 25.2 | 0 | 0
105 | 2022-12-25 01:45 | 7.1 | 18.6 | 30.7 | 25 | 0 | 0
106 | 2022-12-25 01:46 | 7 | 18.6 | 30.5 | 24.8 | 0 | 0
107 | 2022-12-25 01:47 | 7.1 | 18.6 | 30.3 | 24.6 | 0 | 0
108 | 2022-12-25 01:48 | 7 | 18.6 | 30.1 | 24.4 | 0 | 0
109 | 2022-12-25 01:49 | 7.1 | 18.6 | 29.9 | 24.2 | 0 | 0
110 | 2022-12-25 01:50 | 7.2 | 18.6 | 29.7 | 24 | 0 | 0
111 | 2022-12-25 01:51 | 7.2 | 18.6 | 29.6 | 23.8 | 0 | 0
112 | 2022-12-25 01:52 | 7 | 18.6 | 29.4 | 23.6 | 0 | 0
113 | 2022-12-25 01:53 | 7.1 | 18.6 | 29.2 | 23.5 | 0 | 0
114 | 2022-12-25 01:54 | 7.2 | 18.6 | 29 | 23.3 | 0 | 0
115 | 2022-12-25 01:55 | 7.2 | 18.5 | 28.8 | 23.1 | 0 | 0
116 | 2022-12-25 01:56 | 6.9 | 18.5 | 28.7 | 22.9 | 0 | 0
117 | 2022-12-25 01:57 | 7 | 18.5 | 28.5 | 22.8 | 0 | 0
118 | 2022-12-25 01:58 | 7 | 18.5 | 28.3 | 22.6 | 0 | 0
119 | 2022-12-25 01:59 | 6.9 | 18.5 | 28.1 | 22.4 | 0 | 0
120 | 2022-12-25 02:00 | 7.2 | 18.5 | 27.9 | 22.3 | 0 | 0
121 | 2022-12-25 02:01 | 7.1 | 18.6 | 27.8 | 22.1 | 0 | 0
122 | 2022-12-25 02:02 | 7 | 18.6 | 27.6 | 22 | 0 | 0
123 | 2022-12-25 02:03 | 7 | 18.5 | 27.5 | 21.8 | 0.098 | 0
124 | 2022-12-25 02:04 | 7.1 | 18.5 | 27.3 | 25.1 | 0 | 0
125 | 2022-12-25 02:05 | 7 | 18.5 | 27.1 | 25.4 | 0 | 0
126 | 2022-12-25 02:06 | 7 | 18.6 | 27 | 25.2 | 0.823 | 0
127 | 2022-12-25 02:07 | 7 | 18.5 | 36.1 | 24.5 | 0.917 | 0
128 | 2022-12-25 02:08 | 7.2 | 18.5 | 36.5 | 32.1 | 0.936 | 0
129 | 2022-12-25 02:09 | 7.2 | 18.5 | 35.9 | 33.9 | 0.938 | 0
130 | 2022-12-25 02:10 | 7.1 | 18.5 | 34.7 | 33.7 | 0.973 | 0
131 | 2022-12-25 02:11 | 7.1 | 18.6 | 35.1 | 32.9 | 0.974 | 0
132 | 2022-12-25 02:12 | 7.1 | 18.6 | 35.9 | 33.5 | 0.98 | 0
133 | 2022-12-25 02:13 | 7 | 18.6 | 36.7 | 34.3 | 0.174 | 0
134 | 2022-12-25 02:14 | 7 | 18.7 | 36.4 | 34.6 | 0 | 0
135 | 2022-12-25 02:15 | 7.2 | 18.7 | 36.2 | 34.5 | 0 | 0
136 | 2022-12-25 02:16 | 6.9 | 18.8 | 35.9 | 34 | 0 | 0
137 | 2022-12-25 02:17 | 7.2 | 18.7 | 35.6 | 33.4 | 0 | 0
138 | 2022-12-25 02:18 | 7 | 18.7 | 35.3 | 32.9 | 0 | 0
139 | 2022-12-25 02:19 | 7 | 18.6 | 35.1 | 32.4 | 0 | 0
140 | 2022-12-25 02:20 | 6.9 | 18.6 | 34.8 | 31.9 | 0 | 0
141 | 2022-12-25 02:21 | 7.1 | 18.6 | 34.5 | 31.5 | 0 | 0
142 | 2022-12-25 02:22 | 7.1 | 18.6 | 34.3 | 31.1 | 0 | 0
143 | 2022-12-25 02:23 | 7.1 | 18.6 | 34.1 | 30.7 | 0 | 0
144 | 2022-12-25 02:24 | 7.1 | 18.5 | 33.8 | 30.3 | 0 | 0
145 | 2022-12-25 02:25 | 7.1 | 18.5 | 33.6 | 29.9 | 0 | 0
146 | 2022-12-25 02:26 | 7.1 | 18.5 | 33.4 | 29.6 | 0 | 0
147 | 2022-12-25 02:27 | 7.1 | 18.5 | 33.1 | 29.2 | 0 | 0
148 | 2022-12-25 02:28 | 7.1 | 18.5 | 32.9 | 28.9 | 0 | 0
149 | 2022-12-25 02:29 | 7 | 18.5 | 32.7 | 28.6 | 0 | 0
150 | 2022-12-25 02:30 | 6.9 | 18.5 | 32.5 | 28.3 | 0 | 0
151 | 2022-12-25 02:31 | 7.1 | 18.5 | 32.3 | 28 | 0 | 0
152 | 2022-12-25 02:32 | 6.9 | 18.5 | 32 | 27.7 | 0 | 0
153 | 2022-12-25 02:33 | 7.2 | 18.5 | 31.8 | 27.4 | 0 | 0
154 | 2022-12-25 02:34 | 7.1 | 18.5 | 31.6 | 27.2 | 0 | 0
155 | 2022-12-25 02:35 | 7 | 18.5 | 31.4 | 26.9 | 0 | 0
156 | 2022-12-25 02:36 | 7.1 | 18.5 | 31.2 | 26.6 | 0 | 0
157 | 2022-12-25 02:37 | 6.9 | 18.5 | 31 | 26.4 | 0 | 0
158 | 2022-12-25 02:38 | 7.2 | 18.5 | 30.8 | 26.1 | 0 | 0
159 | 2022-12-25 02:39 | 7.1 | 18.4 | 30.6 | 25.9 | 0 | 0
160 | 2022-12-25 02:40 | 6.9 | 18.4 | 30.4 | 25.7 | 0 | 0
161 | 2022-12-25 02:41 | 7.2 | 18.5 | 30.2 | 25.5 | 0 | 0
162 | 2022-12-25 02:42 | 7.1 | 18.4 | 30 | 25.3 | 0 | 0
163 | 2022-12-25 02:43 | 7.2 | 18.4 | 29.8 | 25.1 | 0 | 0
164 | 2022-12-25 02:44 | 7.2 | 18.4 | 29.7 | 24.9 | 0 | 0
165 | 2022-12-25 02:45 | 6.9 | 18.5 | 29.5 | 24.7 | 0 | 0
166 | 2022-12-25 02:46 | 6.8 | 18.4 | 29.3 | 24.5 | 0 | 0
167 | 2022-12-25 02:47 | 6.8 | 18.4 | 29.1 | 24.3 | 0 | 0
168 | 2022-12-25 02:48 | 6.8 | 18.4 | 28.9 | 27.7 | 0 | 0
169 | 2022-12-25 02:49 | 6.9 | 18.4 | 28.7 | 27.4 | 0.713 | 0
170 | 2022-12-25 02:50 | 6.9 | 18.4 | 36.6 | 27.3 | 0.924 | 0
171 | 2022-12-25 02:51 | 6.7 | 18.4 | 37.6 | 34.4 | 0.935 | 0
172 | 2022-12-25 02:52 | 6.7 | 18.5 | 36.9 | 34.9 | 0.95 | 0
173 | 2022-12-25 02:53 | 6.6 | 18.4 | 37.1 | 34.7 | 0.977 | 0
174 | 2022-12-25 02:54 | 6.8 | 18.5 | 37.3 | 35.1 | 0.971 | 0
175 | 2022-12-25 02:55 | 6.6 | 18.4 | 37.4 | 35.2 | 0.975 | 0
176 | 2022-12-25 02:56 | 6.5 | 18.6 | 37.4 | 35.3 | 0 | 0
177 | 2022-12-25 02:57 | 6.6 | 18.7 | 36.7 | 35.2 | 0 | 0
178 | 2022-12-25 02:58 | 6.5 | 18.7 | 36.6 | 35 | 0 | 0
179 | 2022-12-25 02:59 | 6.5 | 18.7 | 36.3 | 34.4 | 0 | 0
180 | 2022-12-25 03:00 | 6.5 | 18.6 | 36 | 33.9 | 0 | 0
181 | 2022-12-25 03:01 | 6.5 | 18.6 | 35.8 | 33.4 | 0 | 0
182 | 2022-12-25 03:02 | 6.6 | 18.5 | 35.5 | 32.9 | 0 | 0
183 | 2022-12-25 03:03 | 6.6 | 18.5 | 35.3 | 32.4 | 0 | 0
184 | 2022-12-25 03:04 | 6.4 | 18.6 | 35 | 31.9 | 0 | 0
185 | 2022-12-25 03:05 | 6.3 | 18.5 | 34.7 | 31.5 | 0 | 0
186 | 2022-12-25 03:06 | 6.5 | 18.5 | 34.5 | 31.1 | 0 | 0
187 | 2022-12-25 03:07 | 6.3 | 18.5 | 34.3 | 30.7 | 0 | 0
188 | 2022-12-25 03:08 | 6.2 | 18.4 | 34 | 30.3 | 0 | 0
189 | 2022-12-25 03:09 | 6.3 | 18.4 | 33.8 | 30 | 0 | 0
190 | 2022-12-25 03:10 | 6.1 | 18.4 | 33.6 | 29.7 | 0 | 0
191 | 2022-12-25 03:11 | 6.2 | 18.4 | 33.3 | 29.3 | 0 | 0
192 | 2022-12-25 03:12 | 6.1 | 18.4 | 33.1 | 29 | 0 | 0
193 | 2022-12-25 03:13 | 6.1 | 18.4 | 32.9 | 28.7 | 0 | 0
194 | 2022-12-25 03:14 | 6.2 | 18.4 | 32.7 | 28.4 | 0 | 0
195 | 2022-12-25 03:15 | 6.4 | 18.4 | 32.4 | 28.2 | 0 | 0
196 | 2022-12-25 03:16 | 6.1 | 18.4 | 32.2 | 27.9 | 0 | 0
197 | 2022-12-25 03:17 | 6.1 | 18.4 | 32 | 27.6 | 0 | 0
198 | 2022-12-25 03:18 | 6.2 | 18.4 | 31.8 | 27.4 | 0 | 0
199 | 2022-12-25 03:19 | 6.2 | 18.4 | 31.6 | 27.1 | 0 | 0
200 | 2022-12-25 03:20 | 6.1 | 18.4 | 31.4 | 26.9 | 0 | 0
201 | 2022-12-25 03:21 | 6.3 | 18.3 | 31.2 | 26.6 | 0 | 0
202 | 2022-12-25 03:22 | 6.1 | 18.4 | 31 | 26.4 | 0 | 0
203 | 2022-12-25 03:23 | 6.1 | 18.4 | 30.8 | 26.2 | 0 | 0
204 | 2022-12-25 03:24 | 6 | 18.3 | 30.6 | 25.9 | 0 | 0
205 | 2022-12-25 03:25 | 6.2 | 18.3 | 30.4 | 25.7 | 0 | 0
206 | 2022-12-25 03:26 | 6 | 18.4 | 30.2 | 28.7 | 0 | 0
207 | 2022-12-25 03:27 | 6 | 18.3 | 30 | 28.4 | 0.716 | 0
208 | 2022-12-25 03:28 | 6 | 18.3 | 40.8 | 27.4 | 0.975 | 0
209 | 2022-12-25 03:29 | 6 | 18.3 | 41.5 | 38.2 | 0.985 | 0
210 | 2022-12-25 03:30 | 5.9 | 18.3 | 40.8 | 38.4 | 0.982 | 0
211 | 2022-12-25 03:31 | 6.1 | 18.4 | 41.2 | 38.3 | 0.981 | 0
212 | 2022-12-25 03:32 | 6.1 | 18.4 | 41.4 | 38.7 | 0.978 | 0
213 | 2022-12-25 03:33 | 6.1 | 18.5 | 41.6 | 39 | 0 | 0
214 | 2022-12-25 03:34 | 5.9 | 18.6 | 41.6 | 38.9 | 0 | 0
215 | 2022-12-25 03:35 | 6 | 18.6 | 41.2 | 38.2 | 0 | 0
216 | 2022-12-25 03:36 | 5.9 | 18.6 | 40.8 | 37.5 | 0 | 0
217 | 2022-12-25 03:37 | 5.8 | 18.5 | 40.5 | 36.9 | 0 | 0
218 | 2022-12-25 03:38 | 5.9 | 18.5 | 40.1 | 36.2 | 0 | 0
219 | 2022-12-25 03:39 | 5.9 | 18.4 | 39.8 | 35.7 | 0 | 0
220 | 2022-12-25 03:40 | 6 | 18.4 | 39.5 | 35.1 | 0 | 0
221 | 2022-12-25 03:41 | 5.9 | 18.4 | 39.2 | 34.6 | 0 | 0
222 | 2022-12-25 03:42 | 5.9 | 18.4 | 38.9 | 34.1 | 0 | 0
223 | 2022-12-25 03:43 | 6.1 | 18.3 | 38.6 | 33.6 | 0 | 0
224 | 2022-12-25 03:44 | 6.1 | 18.3 | 38.3 | 33.2 | 0 | 0
225 | 2022-12-25 03:45 | 6.1 | 18.3 | 38 | 32.8 | 0 | 0
226 | 2022-12-25 03:46 | 6 | 18.4 | 37.7 | 32.3 | 0 | 0
227 | 2022-12-25 03:47 | 6 | 18.3 | 37.4 | 32 | 0 | 0
228 | 2022-12-25 03:48 | 6.1 | 18.3 | 37.2 | 31.6 | 0 | 0
229 | 2022-12-25 03:49 | 6.3 | 18.3 | 36.9 | 31.2 | 0 | 0
230 | 2022-12-25 03:50 | 6.3 | 18.3 | 36.6 | 30.9 | 0 | 0
231 | 2022-12-25 03:51 | 6.2 | 18.3 | 36.4 | 30.5 | 0 | 0
232 | 2022-12-25 03:52 | 6.3 | 18.3 | 36.2 | 30.2 | 0 | 0
233 | 2022-12-25 03:53 | 6.5 | 18.3 | 35.9 | 29.9 | 0 | 0
234 | 2022-12-25 03:54 | 6.4 | 18.3 | 35.7 | 29.6 | 0 | 0
235 | 2022-12-25 03:55 | 6.5 | 18.3 | 35.4 | 29.3 | 0 | 0
236 | 2022-12-25 03:56 | 6.3 | 18.3 | 35.2 | 29 | 0 | 0
237 | 2022-12-25 03:57 | 6.6 | 18.2 | 35 | 28.7 | 0 | 0
238 | 2022-12-25 03:58 | 6.8 | 18.3 | 34.7 | 28.4 | 0.022 | 0
239 | 2022-12-25 03:59 | 6.8 | 18.3 | 34.5 | 31.8 | 0 | 0
240 | 2022-12-25 04:00 | 6.9 | 18.2 | 34.3 | 32 | 0.422 | 0
241 | 2022-12-25 04:01 | 6.6 | 18.2 | 39.7 | 32.3 | 0.976 | 0
242 | 2022-12-25 04:02 | 6.7 | 18.3 | 40.5 | 37.2 | 0.983 | 0
243 | 2022-12-25 04:03 | 6.7 | 18.3 | 39.7 | 37.6 | 0.98 | 0
244 | 2022-12-25 04:04 | 6.6 | 18.2 | 39.7 | 37.3 | 0.98 | 0
245 | 2022-12-25 04:05 | 6.6 | 18.3 | 39.7 | 37.4 | 0.981 | 0
246 | 2022-12-25 04:06 | 6.8 | 18.4 | 39.6 | 37.3 | 0 | 0
247 | 2022-12-25 04:07 | 6.6 | 18.5 | 39.5 | 37.3 | 0 | 0
248 | 2022-12-25 04:08 | 6.7 | 18.5 | 39.3 | 36.9 | 0.982 | 0
249 | 2022-12-25 04:09 | 6.6 | 18.6 | 39.3 | 37.1 | 0.948 | 0
250 | 2022-12-25 04:10 | 6.8 | 18.5 | 39.2 | 38.7 | 0.11 | 0
251 | 2022-12-25 04:11 | 6.8 | 18.4 | 39 | 38.9 | 0.891 | 0
252 | 2022-12-25 04:12 | 6.6 | 18.5 | 39 | 22.2 | 1.086 | 0
253 | 2022-12-25 04:13 | 6.5 | 18.4 | 38.9 | 36.2 | 1.095 | 0
254 | 2022-12-25 04:14 | 6.7 | 18.4 | 38.8 | 37 | 1.093 | 0
255 | 2022-12-25 04:15 | 6.6 | 18.3 | 38.4 | 37.1 | 1.095 | 0
256 | 2022-12-25 04:16 | 6.6 | 18.4 | 37.7 | 36.6 | 1.093 | 0
257 | 2022-12-25 04:17 | 6.4 | 18.4 | 37.8 | 36.2 | 1.091 | 0
258 | 2022-12-25 04:18 | 6.5 | 18.3 | 37.9 | 36.3 | 1.086 | 0
259 | 2022-12-25 04:19 | 6.6 | 18.3 | 37.9 | 36.3 | 1.088 | 0
260 | 2022-12-25 04:20 | 6.4 | 18.3 | 37.7 | 36.3 | 1.09 | 0
261 | 2022-12-25 04:21 | 6.3 | 18.3 | 37.7 | 36.2 | 1.091 | 0
262 | 2022-12-25 04:22 | 6.4 | 18.4 | 37.6 | 36.1 | 1.086 | 0
263 | 2022-12-25 04:23 | 6.3 | 18.4 | 37.6 | 36.1 | 1.096 | 0
264 | 2022-12-25 04:24 | 6.3 | 18.4 | 37.5 | 36 | 1.09 | 0
265 | 2022-12-25 04:25 | 6.2 | 18.3 | 37.4 | 36 | 1.085 | 0
266 | 2022-12-25 04:26 | 6.3 | 18.3 | 37.4 | 35.9 | 1.091 | 0
267 | 2022-12-25 04:27 | 6.1 | 18.4 | 37.3 | 35.9 | 1.088 | 0
268 | 2022-12-25 04:28 | 6.1 | 18.3 | 37.3 | 35.8 | 1.093 | 0
269 | 2022-12-25 04:29 | 6.1 | 18.4 | 37.2 | 35.8 | 1.089 | 0
270 | 2022-12-25 04:30 | 6.1 | 18.4 | 37.1 | 35.7 | 1.086 | 0
271 | 2022-12-25 04:31 | 6.3 | 18.4 | 37.9 | 35.6 | 1.09 | 0
272 | 2022-12-25 04:32 | 6.3 | 18.4 | 38.6 | 36.4 | 1.092 | 0
273 | 2022-12-25 04:33 | 6.1 | 18.3 | 38.9 | 36.9 | 1.092 | 0
274 | 2022-12-25 04:34 | 6 | 18.3 | 39 | 37.3 | 1.101 | 0
275 | 2022-12-25 04:35 | 6.3 | 18.4 | 39.3 | 37.3 | 1.635 | 0
276 | 2022-12-25 04:36 | 6.3 | 18.4 | 39.7 | 36.4 | 1.644 | 0
277 | 2022-12-25 04:37 | 6.3 | 18.4 | 40 | 37.3 | 1.641 | 0
278 | 2022-12-25 04:38 | 6.1 | 18.4 | 40.1 | 37.6 | 1.639 | 0
279 | 2022-12-25 04:39 | 6.1 | 18.5 | 40.6 | 37.8 | 1.642 | 0
280 | 2022-12-25 04:40 | 6.2 | 18.6 | 40.9 | 38.2 | 1.639 | 0
281 | 2022-12-25 04:41 | 6.2 | 18.7 | 40.6 | 38.5 | 0 | 0
282 | 2022-12-25 04:42 | 6.2 | 18.8 | 40.5 | 38.4 | 0 | 0
283 | 2022-12-25 04:43 | 6.1 | 18.8 | 40.2 | 37.9 | 0 | 0
284 | 2022-12-25 04:44 | 5.9 | 18.8 | 39.9 | 37.3 | 0 | 0
285 | 2022-12-25 04:45 | 5.9 | 18.7 | 39.6 | 36.7 | 0 | 0
286 | 2022-12-25 04:46 | 6.1 | 18.6 | 39.3 | 36.2 | 0 | 0
287 | 2022-12-25 04:47 | 5.9 | 18.6 | 39 | 35.7 | 0 | 0
288 | 2022-12-25 04:48 | 5.8 | 18.5 | 38.7 | 35.2 | 0 | 0
289 | 2022-12-25 04:49 | 5.8 | 18.5 | 38.5 | 34.7 | 0 | 0
290 | 2022-12-25 04:50 | 5.7 | 18.5 | 38.2 | 34.3 | 0 | 0
291 | 2022-12-25 04:51 | 5.9 | 18.5 | 37.9 | 33.8 | 0 | 0
292 | 2022-12-25 04:52 | 5.6 | 18.4 | 37.6 | 33.4 | 0 | 0
293 | 2022-12-25 04:53 | 5.7 | 18.4 | 37.4 | 33 | 0 | 0
294 | 2022-12-25 04:54 | 5.6 | 18.3 | 37.1 | 32.6 | 0 | 0
295 | 2022-12-25 04:55 | 5.6 | 18.3 | 36.9 | 32.2 | 0 | 0
296 | 2022-12-25 04:56 | 5.6 | 18.3 | 36.6 | 31.8 | 0 | 0
297 | 2022-12-25 04:57 | 5.6 | 18.3 | 36.4 | 31.4 | 0 | 0
298 | 2022-12-25 04:58 | 5.6 | 18.3 | 36.1 | 31.1 | 0 | 0
299 | 2022-12-25 04:59 | 5.9 | 18.4 | 35.9 | 30.8 | 0 | 0
300 | 2022-12-25 05:00 | 5.6 | 18.3 | 35.6 | 30.4 | 0 | 0
301 | 2022-12-25 05:01 | 5.8 | 18.4 | 35.4 | 30.1 | 0 | 0
302 | 2022-12-25 05:02 | 5.8 | 18.4 | 35.1 | 29.8 | 0 | 0
303 | 2022-12-25 05:03 | 5.8 | 18.4 | 34.9 | 29.5 | 0 | 0
304 | 2022-12-25 05:04 | 5.6 | 18.3 | 34.7 | 29.2 | 0 | 0
305 | 2022-12-25 05:05 | 5.5 | 18.2 | 34.5 | 28.9 | 0 | 0
306 | 2022-12-25 05:06 | 5.7 | 18.3 | 34.2 | 28.7 | 0 | 0
307 | 2022-12-25 05:07 | 5.6 | 18.2 | 34 | 32.1 | 0 | 0
308 | 2022-12-25 05:08 | 5.8 | 18.3 | 33.8 | 31.6 | 0.908 | 0
309 | 2022-12-25 05:09 | 5.6 | 18.3 | 41 | 29.9 | 0.958 | 0
310 | 2022-12-25 05:10 | 5.8 | 18.3 | 40.7 | 38.2 | 0.968 | 0
311 | 2022-12-25 05:11 | 5.7 | 18.3 | 40.4 | 37.8 | 0.978 | 0
312 | 2022-12-25 05:12 | 5.5 | 18.3 | 40.7 | 38.1 | 0.98 | 0
313 | 2022-12-25 05:13 | 5.7 | 18.4 | 40.7 | 38.4 | 0.98 | 0
314 | 2022-12-25 05:14 | 5.7 | 18.4 | 40.7 | 38.2 | 0 | 0
315 | 2022-12-25 05:15 | 5.6 | 18.5 | 40.6 | 38 | 0 | 0
316 | 2022-12-25 05:16 | 5.7 | 18.5 | 40.3 | 37.4 | 0 | 0
317 | 2022-12-25 05:17 | 5.6 | 18.5 | 40 | 36.8 | 0 | 0
318 | 2022-12-25 05:18 | 5.7 | 18.4 | 39.6 | 36.2 | 0 | 0
319 | 2022-12-25 05:19 | 5.5 | 18.4 | 39.3 | 35.6 | 0 | 0
320 | 2022-12-25 05:20 | 5.6 | 18.4 | 39 | 35 | 0 | 0
321 | 2022-12-25 05:21 | 5.7 | 18.3 | 38.7 | 34.5 | 0 | 0
322 | 2022-12-25 05:22 | 5.7 | 18.3 | 38.4 | 34 | 0 | 0
323 | 2022-12-25 05:23 | 5.7 | 18.3 | 38.1 | 33.6 | 0 | 0
324 | 2022-12-25 05:24 | 5.7 | 18.3 | 37.9 | 33.1 | 0 | 0
325 | 2022-12-25 05:25 | 5.7 | 18.2 | 37.6 | 32.7 | 0 | 0
326 | 2022-12-25 05:26 | 5.6 | 18.3 | 37.3 | 32.3 | 0.01 | 0
327 | 2022-12-25 05:27 | 5.8 | 18.2 | 37.1 | 34.8 | 0 | 0
328 | 2022-12-25 05:28 | 5.7 | 18.2 | 36.8 | 34.9 | 0 | 0
329 | 2022-12-25 05:29 | 5.6 | 18.2 | 36.5 | 34.6 | 0.136 | 0
330 | 2022-12-25 05:30 | 5.7 | 18.2 | 38.8 | 35.1 | 0.954 | 0
331 | 2022-12-25 05:31 | 5.7 | 18.2 | 40 | 33.3 | 0.977 | 0
332 | 2022-12-25 05:32 | 5.7 | 18.2 | 39.3 | 38 | 0.978 | 0
333 | 2022-12-25 05:33 | 5.8 | 18.1 | 39.2 | 37.5 | 0.975 | 0
334 | 2022-12-25 05:34 | 5.7 | 18.2 | 39.6 | 37.6 | 0.979 | 0
335 | 2022-12-25 05:35 | 5.6 | 18.2 | 40.1 | 38 | 0.976 | 0
336 | 2022-12-25 05:36 | 5.6 | 18.2 | 40.8 | 38.4 | 0.977 | 0
337 | 2022-12-25 05:37 | 5.9 | 18.2 | 41.2 | 39.1 | 1.551 | 0
338 | 2022-12-25 05:38 | 5.9 | 18.1 | 41.6 | 36.1 | 1.583 | 0
339 | 2022-12-25 05:39 | 5.8 | 18.1 | 42 | 39.1 | 1.581 | 0
340 | 2022-12-25 05:40 | 6 | 18.1 | 41.3 | 39.2 | 1.583 | 0
341 | 2022-12-25 05:41 | 5.9 | 18.1 | 41.3 | 38.8 | 1.587 | 0
342 | 2022-12-25 05:42 | 5.9 | 18.3 | 41.3 | 38.9 | 1.578 | 0
343 | 2022-12-25 05:43 | 5.9 | 18.4 | 41.2 | 38.8 | 1.584 | 0
344 | 2022-12-25 05:44 | 6 | 18.5 | 41 | 39.9 | 1.583 | 0
345 | 2022-12-25 05:45 | 6.1 | 18.5 | 41 | 39.8 | 1.579 | 0
346 | 2022-12-25 05:46 | 6.3 | 18.5 | 41 | 39.8 | 1.486 | 0
347 | 2022-12-25 05:47 | 6.2 | 18.5 | 40.9 | 39.7 | 0.982 | 0
348 | 2022-12-25 05:48 | 6.1 | 18.3 | 40.9 | 39.3 | 0.974 | 0
349 | 2022-12-25 05:49 | 6.1 | 18.3 | 40.9 | 39.3 | 0 | 0
350 | 2022-12-25 05:50 | 6.2 | 18.2 | 40.9 | 39.2 | 0 | 0
351 | 2022-12-25 05:51 | 6.1 | 18.2 | 40.6 | 38.7 | 0 | 0
352 | 2022-12-25 05:52 | 6.1 | 18.2 | 40.4 | 38.1 | 0 | 0
353 | 2022-12-25 05:53 | 6.2 | 18.1 | 40.1 | 37.5 | 0 | 0
354 | 2022-12-25 05:54 | 6.2 | 18.2 | 39.8 | 36.9 | 0 | 0
355 | 2022-12-25 05:55 | 6.1 | 18.2 | 39.5 | 36.4 | 0 | 0
356 | 2022-12-25 05:56 | 6.3 | 18.1 | 39.3 | 35.9 | 0 | 0
357 | 2022-12-25 05:57 | 6.4 | 18.1 | 39 | 35.4 | 0 | 0
358 | 2022-12-25 05:58 | 6.4 | 18.1 | 38.7 | 34.9 | 0 | 0
359 | 2022-12-25 05:59 | 6.4 | 18.1 | 38.4 | 34.5 | 0 | 0
360 | 2022-12-25 06:00 | 6.6 | 18.1 | 38.2 | 34 | 0 | 0
361 | 2022-12-25 06:01 | 6.3 | 18.1 | 37.9 | 33.6 | 0 | 0
362 | 2022-12-25 06:02 | 6.3 | 18.1 | 37.7 | 33.2 | 0 | 0
363 | 2022-12-25 06:03 | 6.5 | 18.1 | 37.4 | 32.8 | 0 | 0
364 | 2022-12-25 06:04 | 6.6 | 18 | 37.2 | 32.7 | 0.008 | 0
365 | 2022-12-25 06:05 | 6.5 | 18.1 | 36.9 | 35.4 | 0 | 0
366 | 2022-12-25 06:06 | 6.6 | 18 | 36.8 | 36.3 | 0.962 | 0
367 | 2022-12-25 06:07 | 6.6 | 18.1 | 40 | 35.3 | 0.978 | 0
368 | 2022-12-25 06:08 | 6.5 | 18.1 | 39.4 | 37.5 | 0.978 | 0
369 | 2022-12-25 06:09 | 6.6 | 18.1 | 39.4 | 37 | 0.979 | 0
370 | 2022-12-25 06:10 | 6.5 | 18.1 | 39.5 | 37.2 | 0.982 | 0
371 | 2022-12-25 06:11 | 6.7 | 18.2 | 39.4 | 37.1 | 0.976 | 0
372 | 2022-12-25 06:12 | 6.8 | 18.4 | 39.3 | 37.1 | 0.981 | 0
373 | 2022-12-25 06:13 | 6.9 | 18.5 | 39.1 | 38.4 | 1.616 | 0
374 | 2022-12-25 06:14 | 6.7 | 18.5 | 39 | 35 | 1.641 | 0
375 | 2022-12-25 06:15 | 6.7 | 18.5 | 38.9 | 37.7 | 1.61 | 0
376 | 2022-12-25 06:16 | 6.7 | 18.4 | 38.8 | 37.7 | 1.106 | 0
377 | 2022-12-25 06:17 | 6.5 | 18.4 | 38.9 | 37.2 | 1.089 | 0
378 | 2022-12-25 06:18 | 6.6 | 18.4 | 38.9 | 37.3 | 1.088 | 0
379 | 2022-12-25 06:19 | 6.6 | 18.3 | 38.9 | 37.3 | 1.092 | 0
380 | 2022-12-25 06:20 | 6.6 | 18.3 | 38.8 | 37.2 | 1.092 | 0
381 | 2022-12-25 06:21 | 6.7 | 18.3 | 38.6 | 37.1 | 1.096 | 0
382 | 2022-12-25 06:22 | 6.6 | 18.3 | 38.5 | 37 | 1.089 | 0
383 | 2022-12-25 06:23 | 6.8 | 18.3 | 38.5 | 36.9 | 1.085 | 0
384 | 2022-12-25 06:24 | 6.7 | 18.2 | 38.4 | 36.9 | 1.089 | 0
385 | 2022-12-25 06:25 | 6.6 | 18.2 | 38.3 | 36.8 | 1.089 | 0
386 | 2022-12-25 06:26 | 6.7 | 18.2 | 38.2 | 36.7 | 1.089 | 0
387 | 2022-12-25 06:27 | 6.9 | 18.2 | 38.1 | 36.6 | 1.082 | 0
388 | 2022-12-25 06:28 | 6.7 | 18.2 | 38 | 36.5 | 1.089 | 0
389 | 2022-12-25 06:29 | 6.9 | 18.2 | 37.9 | 36.5 | 1.086 | 0
390 | 2022-12-25 06:30 | 6.9 | 18.3 | 37.9 | 36.4 | 1.085 | 0
391 | 2022-12-25 06:31 | 6.9 | 18.3 | 37.7 | 36.3 | 1.087 | 0
392 | 2022-12-25 06:32 | 7.5 | 18.2 | 37.6 | 36.2 | 1.086 | 0
393 | 2022-12-25 06:33 | 7.2 | 18.1 | 37.6 | 36.1 | 1.088 | 0
394 | 2022-12-25 06:34 | 7.8 | 18.2 | 37.7 | 36.1 | 1.091 | 0
395 | 2022-12-25 06:35 | 7.8 | 18.2 | 38.1 | 36.2 | 1.09 | 0
396 | 2022-12-25 06:36 | 7.8 | 18.2 | 38.6 | 36.6 | 1.487 | 0
397 | 2022-12-25 06:37 | 7.9 | 18.1 | 38.9 | 35.2 | 1.636 | 0
398 | 2022-12-25 06:38 | 8.2 | 18.2 | 39.2 | 36.5 | 1.634 | 0
399 | 2022-12-25 06:39 | 8.2 | 18.2 | 39.5 | 36.9 | 1.639 | 0
400 | 2022-12-25 06:40 | 8.4 | 18.3 | 39.9 | 37.1 | 1.64 | 0
401 | 2022-12-25 06:41 | 8.4 | 18.4 | 39.7 | 37.5 | 1.638 | 0
402 | 2022-12-25 06:42 | 8.2 | 18.5 | 39.6 | 37.3 | 1.632 | 0
403 | 2022-12-25 06:43 | 8 | 18.6 | 39.5 | 37.3 | 1.636 | 0
404 | 2022-12-25 06:44 | 8.5 | 18.7 | 39.4 | 38.2 | 1.643 | 0
405 | 2022-12-25 06:45 | 8.3 | 18.6 | 39.3 | 38.1 | 0 | 0
406 | 2022-12-25 06:46 | 8.7 | 18.7 | 39.2 | 38 | 0 | 0
407 | 2022-12-25 06:47 | 8.5 | 18.6 | 38.9 | 37.5 | 0 | 0
408 | 2022-12-25 06:48 | 8.4 | 18.5 | 38.7 | 36.9 | 0 | 0
409 | 2022-12-25 06:49 | 8.3 | 18.6 | 38.4 | 36.4 | 0 | 0
410 | 2022-12-25 06:50 | 8.2 | 18.4 | 38.2 | 35.9 | 0 | 0
411 | 2022-12-25 06:51 | 8.4 | 18.4 | 37.9 | 35.4 | 0 | 0
412 | 2022-12-25 06:52 | 8.3 | 18.3 | 37.7 | 34.9 | 0 | 0
413 | 2022-12-25 06:53 | 8.1 | 18.3 | 37.4 | 34.5 | 0 | 0
414 | 2022-12-25 06:54 | 8 | 18.3 | 37.2 | 34.1 | 0 | 0
415 | 2022-12-25 06:55 | 7.9 | 18.3 | 37 | 33.6 | 0 | 0
416 | 2022-12-25 06:56 | 7.7 | 18.3 | 36.7 | 33.2 | 0 | 0
417 | 2022-12-25 06:57 | 7.8 | 18.2 | 36.5 | 32.9 | 0 | 0
418 | 2022-12-25 06:58 | 7.5 | 18.2 | 36.2 | 32.5 | 0 | 0
419 | 2022-12-25 06:59 | 7.8 | 18.2 | 36 | 32.1 | 0 | 0
420 | 2022-12-25 07:00 | 7.9 | 18.1 | 35.8 | 31.8 | 0 | 0
421 | 2022-12-25 07:01 | 8 | 18.1 | 35.6 | 31.4 | 0 | 0
422 | 2022-12-25 07:02 | 8.2 | 18.2 | 35.3 | 31.1 | 0 | 0
423 | 2022-12-25 07:03 | 8.3 | 18.1 | 35.1 | 30.8 | 0.081 | 0
424 | 2022-12-25 07:04 | 8.1 | 18.1 | 34.9 | 33.5 | 0 | 0
425 | 2022-12-25 07:05 | 8.3 | 18.1 | 34.7 | 33.7 | 0.718 | 0
426 | 2022-12-25 07:06 | 9.2 | 18.1 | 38.5 | 33.5 | 0.922 | 0
427 | 2022-12-25 07:07 | 9.2 | 18.2 | 39.7 | 36.3 | 0.955 | 0
428 | 2022-12-25 07:08 | 9 | 18.1 | 39.5 | 37.2 | 0.971 | 0
429 | 2022-12-25 07:09 | 8.6 | 18.2 | 39.9 | 37.1 | 0.979 | 0
430 | 2022-12-25 07:10 | 9 | 18.2 | 40.4 | 37.8 | 0.979 | 0
431 | 2022-12-25 07:11 | 9.1 | 18.3 | 41 | 38.2 | 0.983 | 0
432 | 2022-12-25 07:12 | 8.8 | 18.4 | 41.5 | 38.7 | 0.983 | 0
433 | 2022-12-25 07:13 | 9.1 | 18.4 | 42 | 41.2 | 0.981 | 0
434 | 2022-12-25 07:14 | 9.1 | 18.4 | 42.4 | 41.6 | 1.154 | 0
435 | 2022-12-25 07:15 | 9.9 | 18.4 | 42.9 | 41.8 | 0.988 | 0
436 | 2022-12-25 07:16 | 9.7 | 18.3 | 43.3 | 35.6 | 0.981 | 0
437 | 2022-12-25 07:17 | 9.8 | 18.3 | 44 | 41.1 | 0.981 | 0
438 | 2022-12-25 07:18 | 10 | 18.2 | 44.4 | 42 | 0.977 | 0
439 | 2022-12-25 07:19 | 9.6 | 18.2 | 44.4 | 42.4 | 0.979 | 0
440 | 2022-12-25 07:20 | 10 | 18.1 | 44.5 | 42.4 | 0.984 | 0
441 | 2022-12-25 07:21 | 10.1 | 18.1 | 45 | 42.6 | 0.98 | 0
442 | 2022-12-25 07:22 | 10.6 | 18.1 | 45.3 | 43.1 | 0.977 | 0
443 | 2022-12-25 07:23 | 10.8 | 18.1 | 45.7 | 43.3 | 0.979 | 0
444 | 2022-12-25 07:24 | 10.9 | 18.1 | 46.2 | 43.7 | 0.975 | 0
445 | 2022-12-25 07:25 | 11.1 | 18.1 | 46.5 | 44.1 | 0.972 | 0
446 | 2022-12-25 07:26 | 11.2 | 18 | 46.8 | 44.4 | 0.981 | 0
447 | 2022-12-25 07:27 | 11.1 | 18.1 | 47.2 | 44.8 | 0.98 | 0
448 | 2022-12-25 07:28 | 11 | 18 | 47.7 | 45.1 | 0.983 | 0
449 | 2022-12-25 07:29 | 11 | 18.1 | 47.5 | 45.5 | 0 | 0
450 | 2022-12-25 07:30 | 10.6 | 18 | 47.3 | 45.3 | 0 | 0
451 | 2022-12-25 07:31 | 10.8 | 18 | 47 | 44.8 | 0 | 0
452 | 2022-12-25 07:32 | 10.8 | 18 | 46.8 | 44.3 | 0.959 | 0
453 | 2022-12-25 07:33 | 10.6 | 18.1 | 47.4 | 45.7 | 0.071 | 0
454 | 2022-12-25 07:34 | 10.8 | 17.9 | 47.1 | 46.6 | 0.971 | 0
455 | 2022-12-25 07:35 | 10.8 | 18 | 47.1 | 42.2 | 0.988 | 0
456 | 2022-12-25 07:36 | 10.3 | 18.1 | 47.1 | 43.9 | 0.989 | 0
457 | 2022-12-25 07:37 | 10.3 | 18.1 | 47 | 43.9 | 0.984 | 0
458 | 2022-12-25 07:38 | 10.3 | 18.1 | 46.8 | 44 | 0 | 0
459 | 2022-12-25 07:39 | 11 | 18.4 | 46.6 | 43.8 | 0 | 1
460 | 2022-12-25 07:40 | 11 | 18.4 | 46.3 | 43.2 | 0 | 1
461 | 2022-12-25 07:41 | 10.8 | 18.3 | 46 | 42.6 | 0 | 1
462 | 2022-12-25 07:42 | 10.4 | 18.3 | 45.7 | 42 | 0 | 2
463 | 2022-12-25 07:43 | 10.1 | 18.2 | 45.4 | 41.4 | 0 | 2
464 | 2022-12-25 07:44 | 9.7 | 18.2 | 45.1 | 40.8 | 0 | 3
465 | 2022-12-25 07:45 | 10.5 | 18.2 | 44.8 | 40.2 | 0 | 3
466 | 2022-12-25 07:46 | 10.7 | 18.2 | 44.5 | 39.7 | 0 | 4
467 | 2022-12-25 07:47 | 10.7 | 18.1 | 44.2 | 39.2 | 0 | 4
468 | 2022-12-25 07:48 | 10.5 | 18 | 43.9 | 38.7 | 0 | 5
469 | 2022-12-25 07:49 | 9.8 | 18 | 43.6 | 38.2 | 0 | 5
470 | 2022-12-25 07:50 | 9.7 | 18 | 43.3 | 37.8 | 0 | 5
471 | 2022-12-25 07:51 | 9.4 | 18.1 | 43 | 37.6 | 0 | 6
472 | 2022-12-25 07:52 | 10 | 18 | 42.7 | 37.1 | 0.569 | 6
473 | 2022-12-25 07:53 | 10.2 | 18 | 45.4 | 39.8 | 1.085 | 7
474 | 2022-12-25 07:54 | 9.8 | 18 | 45.6 | 41.9 | 1.099 | 8
475 | 2022-12-25 07:55 | 9.8 | 18 | 44.7 | 43.1 | 1.097 | 8
476 | 2022-12-25 07:56 | 9.6 | 18.1 | 44.9 | 42.7 | 1.094 | 9
477 | 2022-12-25 07:57 | 9.5 | 18 | 44.7 | 42.8 | 1.097 | 9
478 | 2022-12-25 07:58 | 9.3 | 18.1 | 44.6 | 42.6 | 1.095 | 10
479 | 2022-12-25 07:59 | 9.1 | 18 | 44.5 | 42.6 | 1.096 | 10
480 | 2022-12-25 08:00 | 9 | 18 | 44.4 | 42.5 | 1.13 | 10
481 | 2022-12-25 08:01 | 8.8 | 18.2 | 44.3 | 42.3 | 1.639 | 10
482 | 2022-12-25 08:02 | 8.6 | 18.1 | 44.2 | 40.9 | 1.951 | 11
483 | 2022-12-25 08:03 | 8.5 | 18.2 | 44.5 | 37.9 | 2.017 | 11
484 | 2022-12-25 08:04 | 8.3 | 18.3 | 44.5 | 39.5 | 2.013 | 11
485 | 2022-12-25 08:05 | 8.2 | 18.6 | 44.3 | 40.2 | 2.016 | 12
486 | 2022-12-25 08:06 | 8.2 | 19.3 | 44.4 | 40.1 | 2.018 | 12
487 | 2022-12-25 08:07 | 8.2 | 19.7 | 44.5 | 40.3 | 2.018 | 12
488 | 2022-12-25 08:08 | 8.4 | 20.1 | 44.6 | 40.3 | 2.018 | 13
489 | 2022-12-25 08:09 | 8.2 | 20.2 | 44.9 | 40.4 | 2.016 | 13
490 | 2022-12-25 08:10 | 8 | 20.5 | 44.8 | 40.7 | 2.015 | 14
491 | 2022-12-25 08:11 | 8.4 | 20.7 | 44.9 | 40.6 | 2.02 | 14
492 | 2022-12-25 08:12 | 8.2 | 20.8 | 44.5 | 40.6 | 2.019 | 15
493 | 2022-12-25 08:13 | 7.9 | 20.9 | 44.2 | 40.4 | 2.019 | 15
494 | 2022-12-25 08:14 | 7.7 | 21.1 | 44 | 40.1 | 2.017 | 16
495 | 2022-12-25 08:15 | 7.7 | 21.2 | 43.6 | 39.9 | 2.005 | 16
496 | 2022-12-25 08:16 | 7.8 | 21.1 | 43.3 | 39.6 | 2.007 | 17
497 | 2022-12-25 08:17 | 8 | 21.3 | 43 | 39.4 | 2.01 | 17
498 | 2022-12-25 08:18 | 7.9 | 21.2 | 42.6 | 39.1 | 2.014 | 17
499 | 2022-12-25 08:19 | 7.9 | 21.2 | 42.3 | 38.8 | 2.011 | 18
500 | 2022-12-25 08:20 | 8 | 21.2 | 42.1 | 38.6 | 2.015 | 18
501 | 2022-12-25 08:21 | 7.9 | 21.2 | 41.7 | 38.3 | 2.013 | 19
502 | 2022-12-25 08:22 | 7.9 | 21.2 | 41.4 | 38.9 | 2.011 | 19
503 | 2022-12-25 08:23 | 7.9 | 21.2 | 41.3 | 38.7 | 2.011 | 20
504 | 2022-12-25 08:24 | 7.8 | 21.1 | 41.1 | 38.6 | 2.012 | 20
505 | 2022-12-25 08:25 | 7.6 | 21 | 41 | 38.4 | 1.889 | 20
506 | 2022-12-25 08:26 | 7.8 | 21 | 40.8 | 37.9 | 1.834 | 21
507 | 2022-12-25 08:27 | 7.8 | 21 | 40.5 | 37.9 | 1.837 | 21
508 | 2022-12-25 08:28 | 7.8 | 20.8 | 40.3 | 37.7 | 1.837 | 22
509 | 2022-12-25 08:29 | 7.6 | 20.9 | 40.1 | 37.5 | 1.828 | 22
510 | 2022-12-25 08:30 | 7.5 | 21 | 39.9 | 37.3 | 1.837 | 23
511 | 2022-12-25 08:31 | 7.4 | 20.9 | 39.7 | 37.1 | 1.946 | 23
512 | 2022-12-25 08:32 | 7.5 | 20.9 | 39.5 | 37.1 | 2.005 | 23
513 | 2022-12-25 08:33 | 7.3 | 20.8 | 39.4 | 36.1 | 2.009 | 23
514 | 2022-12-25 08:34 | 7.3 | 20.8 | 39.2 | 36.1 | 2.005 | 24
515 | 2022-12-25 08:35 | 7.4 | 20.9 | 39.4 | 35.9 | 2.008 | 24
516 | 2022-12-25 08:36 | 7.5 | 20.9 | 39.5 | 36.1 | 2.006 | 25
517 | 2022-12-25 08:37 | 7.4 | 21 | 39.9 | 36.2 | 2.007 | 26
518 | 2022-12-25 08:38 | 7.2 | 21 | 40.1 | 36.6 | 2.007 | 26
519 | 2022-12-25 08:39 | 7.4 | 21.1 | 40.3 | 36.7 | 2.004 | 27
520 | 2022-12-25 08:40 | 7.1 | 21 | 40.4 | 36.8 | 2.008 | 27
521 | 2022-12-25 08:41 | 7.1 | 21.1 | 40.7 | 37 | 2.003 | 27
522 | 2022-12-25 08:42 | 7.4 | 21.2 | 40.9 | 37.2 | 2.005 | 27
523 | 2022-12-25 08:43 | 7.4 | 21.3 | 41.1 | 37.4 | 2.007 | 28
524 | 2022-12-25 08:44 | 7.1 | 21.3 | 41.2 | 37.6 | 2.011 | 28
525 | 2022-12-25 08:45 | 7.3 | 21.3 | 41.5 | 38.6 | 2.005 | 29
526 | 2022-12-25 08:46 | 7.2 | 21.3 | 41.6 | 38.8 | 2.01 | 29
527 | 2022-12-25 08:47 | 7.1 | 21.3 | 41.6 | 38.9 | 2.011 | 29
528 | 2022-12-25 08:48 | 7.1 | 21.3 | 41.4 | 38.8 | 1.87 | 30
529 | 2022-12-25 08:49 | 7.3 | 21.3 | 41.2 | 38.3 | 1.835 | 30
530 | 2022-12-25 08:50 | 7.2 | 21.2 | 41 | 38.2 | 1.835 | 31
531 | 2022-12-25 08:51 | 7.3 | 21.2 | 40.7 | 38.1 | 1.838 | 31
532 | 2022-12-25 08:52 | 7.2 | 21.2 | 40.5 | 37.9 | 1.836 | 31
533 | 2022-12-25 08:53 | 7.3 | 21.3 | 40.3 | 37.7 | 1.833 | 32
534 | 2022-12-25 08:54 | 7.3 | 21.3 | 40.1 | 37.6 | 1.833 | 32
535 | 2022-12-25 08:55 | 7.2 | 21.2 | 40 | 37.4 | 1.835 | 32
536 | 2022-12-25 08:56 | 7.2 | 21.2 | 39.8 | 37.2 | 1.83 | 32
537 | 2022-12-25 08:57 | 7.2 | 21.2 | 39.5 | 37 | 1.833 | 33
538 | 2022-12-25 08:58 | 7 | 21.3 | 39.4 | 36.8 | 2.009 | 33
539 | 2022-12-25 08:59 | 7 | 21.2 | 39.3 | 35.9 | 1.998 | 33
540 | 2022-12-25 09:00 | 7 | 21.2 | 39.1 | 36 | 2.006 | 33
541 | 2022-12-25 09:01 | 7 | 21.3 | 38.6 | 35.8 | 2.007 | 34
542 | 2022-12-25 09:02 | 7.2 | 21.2 | 38.4 | 35.4 | 2 | 34
543 | 2022-12-25 09:03 | 7 | 21.3 | 38.2 | 35.3 | 2.005 | 34
544 | 2022-12-25 09:04 | 7.2 | 21.3 | 38.1 | 35.1 | 2.005 | 35
545 | 2022-12-25 09:05 | 7 | 21.3 | 38.3 | 35.1 | 2.01 | 35
546 | 2022-12-25 09:06 | 7 | 21.3 | 38.8 | 35.3 | 2.01 | 36
547 | 2022-12-25 09:07 | 7 | 21.3 | 38.9 | 35.6 | 2.005 | 36
548 | 2022-12-25 09:08 | 7.2 | 21.3 | 39.1 | 35.7 | 2.011 | 37
549 | 2022-12-25 09:09 | 7.1 | 21.3 | 39.3 | 35.9 | 2.006 | 37
550 | 2022-12-25 09:10 | 7 | 21.4 | 39.5 | 36.8 | 2.01 | 38
551 | 2022-12-25 09:11 | 7.2 | 21.4 | 39.8 | 37.1 | 2.008 | 38
552 | 2022-12-25 09:12 | 7.1 | 21.5 | 40.1 | 37.4 | 2.009 | 38
553 | 2022-12-25 09:13 | 7.2 | 21.4 | 40.5 | 37.6 | 1.932 | 39
554 | 2022-12-25 09:14 | 7.1 | 21.4 | 40.7 | 37.8 | 1.834 | 40
555 | 2022-12-25 09:15 | 7.2 | 21.4 | 41 | 37.9 | 1.83 | 40
556 | 2022-12-25 09:16 | 7.2 | 21.4 | 41.2 | 38.2 | 1.837 | 41
557 | 2022-12-25 09:17 | 7.1 | 21.5 | 41.4 | 38.4 | 1.833 | 41
558 | 2022-12-25 09:18 | 7.2 | 21.5 | 41.7 | 38.6 | 1.834 | 41
559 | 2022-12-25 09:19 | 7.1 | 21.5 | 42 | 38.9 | 1.837 | 41
560 | 2022-12-25 09:20 | 7 | 21.5 | 42.2 | 39.1 | 1.834 | 42
561 | 2022-12-25 09:21 | 7.3 | 21.4 | 42.5 | 39.3 | 1.832 | 43
562 | 2022-12-25 09:22 | 7.1 | 21.5 | 42.7 | 39.5 | 1.841 | 43
563 | 2022-12-25 09:23 | 7.1 | 21.5 | 42.9 | 39.7 | 1.834 | 43
564 | 2022-12-25 09:24 | 7.1 | 21.5 | 43.2 | 39.9 | 1.831 | 44
565 | 2022-12-25 09:25 | 7.1 | 21.5 | 43.5 | 40.2 | 1.835 | 44
566 | 2022-12-25 09:26 | 7.3 | 21.5 | 43.6 | 40.4 | 1.997 | 44
567 | 2022-12-25 09:27 | 7.3 | 21.7 | 43.9 | 37.8 | 2.006 | 45
568 | 2022-12-25 09:28 | 7.2 | 21.7 | 44.1 | 39.9 | 2.012 | 45
569 | 2022-12-25 09:29 | 7.2 | 21.7 | 44 | 40.1 | 2.004 | 85
570 | 2022-12-25 09:30 | 7.3 | 21.8 | 44.2 | 40.1 | 2.016 | 240
571 | 2022-12-25 09:31 | 7.1 | 21.9 | 44.4 | 40.3 | 2.012 | 414
572 | 2022-12-25 09:32 | 7.4 | 21.9 | 44.5 | 40.4 | 2.009 | 504
573 | 2022-12-25 09:33 | 7.9 | 22 | 44.7 | 40.5 | 2.016 | 508
574 | 2022-12-25 09:34 | 7.9 | 22.1 | 44.9 | 41.7 | 2.015 | 512
575 | 2022-12-25 09:35 | 8 | 22.1 | 45 | 42.1 | 2.022 | 516
576 | 2022-12-25 09:36 | 8.3 | 21.8 | 45.4 | 43 | 2.008 | 520
577 | 2022-12-25 09:37 | 8.5 | 21.3 | 45.7 | 43.4 | 1.844 | 523
578 | 2022-12-25 09:38 | 8.6 | 21 | 46.1 | 43.5 | 1.813 | 527
579 | 2022-12-25 09:39 | 8.8 | 20.7 | 46.3 | 43.9 | 1.552 | 531
580 | 2022-12-25 09:40 | 9.1 | 20.5 | 46.4 | 43.7 | 1.519 | 534
581 | 2022-12-25 09:41 | 8.8 | 20.4 | 46.4 | 43.8 | 1.516 | 536
582 | 2022-12-25 09:42 | 9.3 | 20.3 | 46.2 | 43.9 | 1.514 | 542
583 | 2022-12-25 09:43 | 9.9 | 20.2 | 46 | 43.6 | 1.829 | 546
584 | 2022-12-25 09:44 | 10.1 | 20.3 | 45.8 | 41.5 | 1.844 | 550
585 | 2022-12-25 09:45 | 10.5 | 20.5 | 45.7 | 42.4 | 1.845 | 552
586 | 2022-12-25 09:46 | 10.9 | 20.8 | 45.3 | 42.3 | 1.843 | 555
587 | 2022-12-25 09:47 | 11 | 21.1 | 45.1 | 41.9 | 1.907 | 559
588 | 2022-12-25 09:48 | 11.1 | 21.4 | 44.8 | 41.8 | 2.01 | 562
589 | 2022-12-25 09:49 | 11.8 | 21.5 | 44.6 | 40.6 | 2.011 | 566
590 | 2022-12-25 09:50 | 11.2 | 21.7 | 44.2 | 40.5 | 2.01 | 569
591 | 2022-12-25 09:51 | 11.2 | 21.7 | 43.8 | 40.2 | 2.009 | 571
592 | 2022-12-25 09:52 | 11.1 | 21.9 | 43.5 | 39.9 | 2.007 | 574
593 | 2022-12-25 09:53 | 11.2 | 22.1 | 43.1 | 39.6 | 2.01 | 576
594 | 2022-12-25 09:54 | 11.7 | 22.2 | 42.9 | 39.4 | 2.017 | 582
595 | 2022-12-25 09:55 | 12.3 | 22.2 | 42.5 | 40.6 | 2.01 | 584
596 | 2022-12-25 09:56 | 13 | 22 | 42.3 | 40.7 | 2.007 | 588
597 | 2022-12-25 09:57 | 12.8 | 21.5 | 42.4 | 40.6 | 1.984 | 591
598 | 2022-12-25 09:58 | 12.4 | 21.2 | 42.3 | 40.6 | 1.772 | 591
599 | 2022-12-25 09:59 | 12.4 | 20.9 | 42.2 | 40.3 | 1.507 | 595
600 | 2022-12-25 10:00 | 12.7 | 20.7 | 42.1 | 39.9 | 1.516 | 597
601 | 2022-12-25 10:01 | 13.3 | 20.5 | 41.9 | 39.9 | 1.506 | 601
602 | 2022-12-25 10:02 | 13.2 | 20.4 | 41.7 | 39.8 | 1.508 | 605
603 | 2022-12-25 10:03 | 13.3 | 20.3 | 41.6 | 39.7 | 1.514 | 608
604 | 2022-12-25 10:04 | 13.7 | 20.3 | 41.6 | 39.5 | 1.509 | 612
605 | 2022-12-25 10:05 | 13.6 | 20.1 | 41.5 | 39.5 | 1.742 | 614
606 | 2022-12-25 10:06 | 14 | 20.3 | 41.2 | 39.4 | 1.835 | 617
607 | 2022-12-25 10:07 | 14.2 | 20.5 | 41 | 38.4 | 1.832 | 620
608 | 2022-12-25 10:08 | 13.6 | 20.7 | 40.9 | 38.2 | 1.835 | 607
609 | 2022-12-25 10:09 | 13.8 | 20.9 | 40.5 | 38 | 1.957 | 624
610 | 2022-12-25 10:10 | 13.9 | 21.2 | 40.2 | 36.4 | 2.004 | 628
611 | 2022-12-25 10:11 | 13.8 | 21.4 | 40.1 | 36.9 | 2.002 | 630
612 | 2022-12-25 10:12 | 13.9 | 21.6 | 39.7 | 36.8 | 2.005 | 634
613 | 2022-12-25 10:13 | 14 | 21.7 | 39.5 | 36.4 | 1.998 | 637
614 | 2022-12-25 10:14 | 13.9 | 21.8 | 39.3 | 36.3 | 1.998 | 638
615 | 2022-12-25 10:15 | 13.7 | 21.8 | 39 | 36.1 | 2.003 | 641
616 | 2022-12-25 10:16 | 13.9 | 21.9 | 38.8 | 35.9 | 2.006 | 644
617 | 2022-12-25 10:17 | 13.6 | 22 | 38.6 | 35.7 | 2 | 648
618 | 2022-12-25 10:18 | 13.7 | 22 | 38.3 | 35.6 | 1.995 | 649
619 | 2022-12-25 10:19 | 14 | 22 | 38.1 | 36.6 | 2.003 | 652
620 | 2022-12-25 10:20 | 14.1 | 21.7 | 38 | 36.7 | 1.994 | 655
621 | 2022-12-25 10:21 | 14.2 | 21.3 | 38 | 36.6 | 1.991 | 654
622 | 2022-12-25 10:22 | 14.4 | 21.1 | 37.9 | 36.5 | 1.706 | 659
623 | 2022-12-25 10:23 | 14.2 | 20.9 | 37.8 | 36.2 | 1.499 | 661
624 | 2022-12-25 10:24 | 14.5 | 20.6 | 37.7 | 36 | 1.503 | 662
625 | 2022-12-25 10:25 | 14.5 | 20.5 | 37.6 | 36 | 1.503 | 665
626 | 2022-12-25 10:26 | 14.7 | 20.4 | 37.4 | 35.8 | 1.505 | 669
627 | 2022-12-25 10:27 | 14.6 | 20.3 | 37.3 | 35.7 | 1.498 | 671
628 | 2022-12-25 10:28 | 14.7 | 20.3 | 37.2 | 35.6 | 1.499 | 672
629 | 2022-12-25 10:29 | 14.8 | 20.3 | 37.1 | 35.5 | 1.726 | 676
630 | 2022-12-25 10:30 | 14.6 | 20.4 | 37 | 35.5 | 1.825 | 678
631 | 2022-12-25 10:31 | 14.6 | 20.5 | 37.1 | 34.6 | 1.823 | 681
632 | 2022-12-25 10:32 | 14.7 | 20.6 | 37.2 | 34.8 | 1.824 | 683
633 | 2022-12-25 10:33 | 14.7 | 20.7 | 37.4 | 35 | 1.823 | 687
634 | 2022-12-25 10:34 | 14.8 | 21.1 | 37.8 | 35.2 | 1.828 | 691
635 | 2022-12-25 10:35 | 14.7 | 21.2 | 38.2 | 35.5 | 1.827 | 695
636 | 2022-12-25 10:36 | 14.9 | 21.3 | 38.5 | 35.8 | 1.83 | 696
637 | 2022-12-25 10:37 | 15 | 21.5 | 38.9 | 36.2 | 1.83 | 698
638 | 2022-12-25 10:38 | 15.1 | 21.6 | 39.2 | 36.4 | 1.822 | 699
639 | 2022-12-25 10:39 | 15 | 21.7 | 39.4 | 36.8 | 1.822 | 703
640 | 2022-12-25 10:40 | 14.8 | 21.7 | 39.8 | 36.9 | 1.826 | 703
641 | 2022-12-25 10:41 | 15 | 21.7 | 40 | 37.2 | 1.829 | 707
642 | 2022-12-25 10:42 | 15.5 | 21.8 | 40.4 | 37.5 | 1.831 | 710
643 | 2022-12-25 10:43 | 15.8 | 21.9 | 40.6 | 37.8 | 1.834 | 711
644 | 2022-12-25 10:44 | 16 | 21.9 | 40.6 | 37.9 | 1.829 | 714
645 | 2022-12-25 10:45 | 16.3 | 22 | 40.4 | 37.9 | 1.832 | 716
646 | 2022-12-25 10:46 | 16.8 | 21.9 | 40.2 | 38.5 | 1.834 | 719
647 | 2022-12-25 10:47 | 16.8 | 21.5 | 40.1 | 38.5 | 1.833 | 718
648 | 2022-12-25 10:48 | 16.8 | 21.2 | 40.1 | 38.4 | 1.824 | 719
649 | 2022-12-25 10:49 | 17.4 | 20.9 | 40 | 38.4 | 1.721 | 721
650 | 2022-12-25 10:50 | 17.3 | 20.8 | 39.9 | 38.2 | 1.508 | 724
651 | 2022-12-25 10:51 | 17.1 | 20.6 | 39.8 | 38.3 | 1.657 | 721
652 | 2022-12-25 10:52 | 17 | 20.5 | 39.7 | 37.9 | 1.827 | 721
653 | 2022-12-25 10:53 | 16.8 | 20.5 | 39.6 | 37.5 | 1.834 | 726
654 | 2022-12-25 10:54 | 16.6 | 20.4 | 39.4 | 37.5 | 1.784 | 725
655 | 2022-12-25 10:55 | 16.8 | 20.4 | 39.2 | 37.3 | 1.633 | 723
656 | 2022-12-25 10:56 | 17 | 20.5 | 39.1 | 37 | 1.624 | 727
657 | 2022-12-25 10:57 | 17.1 | 20.6 | 39 | 36.9 | 1.625 | 732
658 | 2022-12-25 10:58 | 17.3 | 20.6 | 38.8 | 36.8 | 1.863 | 742
659 | 2022-12-25 10:59 | 17 | 20.9 | 38.6 | 35.8 | 1.877 | 743
660 | 2022-12-25 11:00 | 16.9 | 21 | 38.5 | 35.9 | 1.901 | 748
661 | 2022-12-25 11:01 | 16.9 | 21.3 | 38.3 | 35.8 | 2.004 | 748
662 | 2022-12-25 11:02 | 17.2 | 21.5 | 38.1 | 35.8 | 1.996 | 750
663 | 2022-12-25 11:03 | 17.1 | 21.6 | 37.9 | 35.9 | 2.003 | 750
664 | 2022-12-25 11:04 | 17 | 21.7 | 38 | 35.7 | 1.934 | 748
665 | 2022-12-25 11:05 | 16.7 | 21.8 | 38.4 | 35.7 | 1.823 | 751
666 | 2022-12-25 11:06 | 16.6 | 21.8 | 38.7 | 36 | 1.833 | 755
667 | 2022-12-25 11:07 | 16.6 | 21.8 | 39.1 | 36.3 | 1.82 | 758
668 | 2022-12-25 11:08 | 17.3 | 21.8 | 39.3 | 36.6 | 1.823 | 756
669 | 2022-12-25 11:09 | 17.1 | 21.9 | 39.6 | 36.8 | 1.829 | 758
670 | 2022-12-25 11:10 | 16.5 | 21.8 | 39.9 | 38 | 1.828 | 757
671 | 2022-12-25 11:11 | 17 | 21.4 | 40.2 | 38.3 | 1.829 | 763
672 | 2022-12-25 11:12 | 17 | 21.1 | 40.7 | 38.6 | 1.789 | 764
673 | 2022-12-25 11:13 | 17.6 | 21 | 40.8 | 39 | 1.507 | 764
674 | 2022-12-25 11:14 | 17.2 | 20.8 | 40.6 | 38.7 | 1.508 | 766
675 | 2022-12-25 11:15 | 16.9 | 20.6 | 40.5 | 38.6 | 1.5 | 771
676 | 2022-12-25 11:16 | 17.3 | 20.5 | 40.5 | 38.6 | 1.509 | 772
677 | 2022-12-25 11:17 | 17.7 | 20.5 | 40.4 | 38.5 | 1.507 | 776
678 | 2022-12-25 11:18 | 17.8 | 20.4 | 40.3 | 38.4 | 1.501 | 772
679 | 2022-12-25 11:19 | 18 | 20.4 | 40.2 | 38.3 | 1.507 | 774
680 | 2022-12-25 11:20 | 18.3 | 20.4 | 40 | 38.3 | 1.503 | 776
681 | 2022-12-25 11:21 | 18.5 | 20.3 | 39.9 | 38.1 | 1.507 | 777
682 | 2022-12-25 11:22 | 18.4 | 20.4 | 39.8 | 38 | 1.807 | 779
683 | 2022-12-25 11:23 | 17.8 | 20.6 | 39.7 | 35.8 | 1.826 | 784
684 | 2022-12-25 11:24 | 17.4 | 20.6 | 39.5 | 37.1 | 1.829 | 786
685 | 2022-12-25 11:25 | 16.9 | 20.9 | 39.2 | 37 | 1.829 | 789
686 | 2022-12-25 11:26 | 16 | 21.2 | 39.1 | 36.7 | 1.827 | 790
687 | 2022-12-25 11:27 | 16.6 | 21.4 | 38.9 | 36.6 | 1.83 | 791
688 | 2022-12-25 11:28 | 16.4 | 21.6 | 38.8 | 36.4 | 1.824 | 791
689 | 2022-12-25 11:29 | 16.5 | 21.7 | 38.6 | 36.3 | 1.825 | 794
690 | 2022-12-25 11:30 | 16.5 | 21.8 | 38.4 | 36.1 | 1.822 | 796
691 | 2022-12-25 11:31 | 16.9 | 21.9 | 38.2 | 36 | 1.82 | 799
692 | 2022-12-25 11:32 | 16.9 | 21.9 | 38.1 | 35.8 | 1.827 | 797
693 | 2022-12-25 11:33 | 16.5 | 21.9 | 37.9 | 35.7 | 1.826 | 795
694 | 2022-12-25 11:34 | 16.3 | 21.9 | 37.9 | 36 | 1.829 | 802
695 | 2022-12-25 11:35 | 16.1 | 21.7 | 38.4 | 36.5 | 1.831 | 805
696 | 2022-12-25 11:36 | 16.1 | 21.3 | 38.7 | 36.9 | 1.829 | 806
697 | 2022-12-25 11:37 | 16.1 | 21 | 39.1 | 37.3 | 1.729 | 806
698 | 2022-12-25 11:38 | 16.4 | 20.8 | 39.5 | 37.5 | 1.506 | 813
699 | 2022-12-25 11:39 | 16.4 | 20.7 | 39.8 | 38.3 | 1.501 | 815
700 | 2022-12-25 11:40 | 16.2 | 20.6 | 40.2 | 38.8 | 1.501 | 813
701 | 2022-12-25 11:41 | 16.2 | 20.6 | 40.5 | 39 | 1.411 | 812
702 | 2022-12-25 11:42 | 16.3 | 20.6 | 41.1 | 39.4 | 1.092 | 815
703 | 2022-12-25 11:43 | 16.8 | 20.4 | 41.4 | 39.5 | 1.093 | 818
704 | 2022-12-25 11:44 | 17.2 | 20.4 | 42.1 | 39.8 | 1.087 | 821
705 | 2022-12-25 11:45 | 17.3 | 20.3 | 41.4 | 40.3 | 1.095 | 820
706 | 2022-12-25 11:46 | 17.5 | 20.4 | 41.6 | 39.8 | 1.096 | 823
707 | 2022-12-25 11:47 | 17.8 | 20.4 | 41.3 | 39.9 | 1.611 | 819
708 | 2022-12-25 11:48 | 17.4 | 20.6 | 41.4 | 37.7 | 1.625 | 826
709 | 2022-12-25 11:49 | 17.2 | 20.8 | 41.3 | 38.9 | 1.833 | 826
710 | 2022-12-25 11:50 | 17.1 | 21 | 40.9 | 38 | 1.837 | 830
711 | 2022-12-25 11:51 | 16.4 | 21.2 | 40.9 | 38.2 | 1.834 | 827
712 | 2022-12-25 11:52 | 17 | 21.5 | 40.6 | 38.2 | 1.836 | 832
713 | 2022-12-25 11:53 | 17.6 | 21.8 | 40.5 | 37.9 | 1.826 | 831
714 | 2022-12-25 11:54 | 17.7 | 21.9 | 40.2 | 37.8 | 1.83 | 832
715 | 2022-12-25 11:55 | 16.7 | 22 | 40.1 | 37.6 | 1.826 | 834
716 | 2022-12-25 11:56 | 16.9 | 22.1 | 39.9 | 37.4 | 1.829 | 834
717 | 2022-12-25 11:57 | 17.1 | 22.1 | 39.7 | 38 | 1.832 | 838
718 | 2022-12-25 11:58 | 17.1 | 21.8 | 39.6 | 38.1 | 1.829 | 841
719 | 2022-12-25 11:59 | 17.3 | 21.5 | 39.5 | 38 | 1.818 | 840
720 | 2022-12-25 12:00 | 16.7 | 21.1 | 39.5 | 37.9 | 1.622 | 840
721 | 2022-12-25 12:01 | 16.9 | 21 | 39.4 | 37.7 | 1.504 | 842
722 | 2022-12-25 12:02 | 16.9 | 20.8 | 39.3 | 37.5 | 1.497 | 843
723 | 2022-12-25 12:03 | 17.1 | 20.6 | 39.2 | 37.4 | 1.501 | 843
724 | 2022-12-25 12:04 | 16.8 | 20.6 | 39.3 | 37.4 | 1.506 | 843
725 | 2022-12-25 12:05 | 16.9 | 20.6 | 39.4 | 37.5 | 1.498 | 844
726 | 2022-12-25 12:06 | 16.9 | 20.5 | 39.9 | 37.7 | 1.504 | 844
727 | 2022-12-25 12:07 | 17.3 | 20.5 | 40.3 | 38.1 | 1.505 | 846
728 | 2022-12-25 12:08 | 17.3 | 20.4 | 40.6 | 38.4 | 1.513 | 845
729 | 2022-12-25 12:09 | 17.5 | 20.5 | 41 | 38.7 | 1.507 | 844
730 | 2022-12-25 12:10 | 16.8 | 20.4 | 41.4 | 39.1 | 1.506 | 846
731 | 2022-12-25 12:11 | 16.7 | 20.4 | 41.8 | 39.5 | 1.719 | 847
732 | 2022-12-25 12:12 | 17.5 | 20.6 | 42.2 | 39.2 | 1.832 | 850
733 | 2022-12-25 12:13 | 18.2 | 20.7 | 41.8 | 39.2 | 1.838 | 849
734 | 2022-12-25 12:14 | 17.8 | 20.9 | 41.7 | 39.5 | 1.978 | 848
735 | 2022-12-25 12:15 | 17.4 | 21.1 | 41.3 | 36 | 1.99 | 848
736 | 2022-12-25 12:16 | 16.6 | 21.6 | 41.3 | 38.2 | 1.978 | 849
737 | 2022-12-25 12:17 | 16.8 | 21.8 | 40.6 | 38.3 | 1.89 | 850
738 | 2022-12-25 12:18 | 17.3 | 22 | 40.6 | 37.6 | 1.892 | 850
739 | 2022-12-25 12:19 | 17.5 | 22.1 | 40.4 | 37.6 | 1.884 | 850
740 | 2022-12-25 12:20 | 17.5 | 22.1 | 40.2 | 38.2 | 1.887 | 852
741 | 2022-12-25 12:21 | 17.3 | 22.1 | 40 | 38.2 | 1.889 | 855
742 | 2022-12-25 12:22 | 17.2 | 21.9 | 39.9 | 38.9 | 1.871 | 855
743 | 2022-12-25 12:23 | 16.6 | 21.6 | 39.9 | 38.9 | 1.661 | 855
744 | 2022-12-25 12:24 | 16.9 | 21.4 | 39.9 | 38.7 | 1.232 | 854
745 | 2022-12-25 12:25 | 16.4 | 21.2 | 39.9 | 38.5 | 1.508 | 855
746 | 2022-12-25 12:26 | 17.1 | 21 | 39.8 | 37.8 | 1.504 | 852
747 | 2022-12-25 12:27 | 17.1 | 21 | 39.6 | 37.9 | 1.505 | 855
748 | 2022-12-25 12:28 | 17.5 | 20.9 | 39.4 | 37.7 | 1.503 | 855
749 | 2022-12-25 12:29 | 17.5 | 20.8 | 39.3 | 37.6 | 1.506 | 855
750 | 2022-12-25 12:30 | 17.9 | 20.6 | 39.2 | 37.5 | 1.503 | 854
751 | 2022-12-25 12:31 | 17.4 | 20.6 | 39.1 | 37.4 | 1.502 | 854
752 | 2022-12-25 12:32 | 17.8 | 20.5 | 39 | 37.2 | 1.506 | 851
753 | 2022-12-25 12:33 | 17.7 | 20.5 | 38.9 | 37.2 | 1.5 | 854
754 | 2022-12-25 12:34 | 17.8 | 20.4 | 39 | 37.1 | 1.503 | 852
755 | 2022-12-25 12:35 | 18 | 20.4 | 39.5 | 37.4 | 1.507 | 852
756 | 2022-12-25 12:36 | 17.7 | 20.4 | 39.8 | 37.7 | 1.509 | 853
757 | 2022-12-25 12:37 | 17.2 | 20.5 | 40.1 | 38.1 | 1.656 | 855
758 | 2022-12-25 12:38 | 17.1 | 20.6 | 40.4 | 38.2 | 1.832 | 856
759 | 2022-12-25 12:39 | 17.4 | 20.6 | 40.8 | 37.5 | 1.83 | 855
760 | 2022-12-25 12:40 | 17.5 | 20.7 | 41.2 | 38.2 | 1.835 | 858
761 | 2022-12-25 12:41 | 17 | 21.1 | 41.3 | 38.4 | 1.834 | 856
762 | 2022-12-25 12:42 | 17.4 | 21.4 | 41.7 | 38.6 | 1.826 | 856
763 | 2022-12-25 12:43 | 17.7 | 21.8 | 41.7 | 38.9 | 1.83 | 855
764 | 2022-12-25 12:44 | 17.6 | 22 | 41.4 | 38.8 | 1.831 | 854
765 | 2022-12-25 12:45 | 17.7 | 22.1 | 41.3 | 38.6 | 1.836 | 852
766 | 2022-12-25 12:46 | 17.6 | 22.1 | 41.1 | 39.4 | 1.831 | 853
767 | 2022-12-25 12:47 | 17.9 | 21.8 | 41 | 39.9 | 1.829 | 852
768 | 2022-12-25 12:48 | 17.9 | 21.5 | 41 | 39.9 | 1.809 | 851
769 | 2022-12-25 12:49 | 18.2 | 21.2 | 41 | 39.8 | 1.518 | 850
770 | 2022-12-25 12:50 | 18 | 21.1 | 40.9 | 39.7 | 1.096 | 850
771 | 2022-12-25 12:51 | 18.4 | 21 | 40.9 | 39.4 | 1.092 | 852
772 | 2022-12-25 12:52 | 18.3 | 20.8 | 40.8 | 39.3 | 1.089 | 852
773 | 2022-12-25 12:53 | 18.4 | 20.8 | 40.7 | 39.2 | 1.091 | 853
774 | 2022-12-25 12:54 | 18.1 | 20.7 | 40.6 | 39.1 | 1.092 | 852
775 | 2022-12-25 12:55 | 17.7 | 20.6 | 40.6 | 39.1 | 1.088 | 853
776 | 2022-12-25 12:56 | 18.4 | 20.6 | 40.4 | 39 | 1.086 | 850
777 | 2022-12-25 12:57 | 18.4 | 20.5 | 40.4 | 38.9 | 1.092 | 847
778 | 2022-12-25 12:58 | 18.5 | 20.5 | 40.3 | 38.9 | 1.463 | 844
779 | 2022-12-25 12:59 | 18.5 | 20.5 | 40.2 | 38 | 1.504 | 843
780 | 2022-12-25 13:00 | 18.4 | 20.6 | 40.1 | 38.2 | 1.505 | 843
781 | 2022-12-25 13:01 | 18.9 | 20.4 | 40 | 38.2 | 1.499 | 843
782 | 2022-12-25 13:02 | 18.5 | 20.5 | 39.8 | 38.1 | 1.504 | 846
783 | 2022-12-25 13:03 | 18.6 | 20.4 | 39.8 | 38 | 1.502 | 847
784 | 2022-12-25 13:04 | 17.9 | 20.5 | 39.8 | 37.9 | 1.789 | 845
785 | 2022-12-25 13:05 | 17.9 | 20.7 | 40.2 | 36.3 | 1.832 | 844
786 | 2022-12-25 13:06 | 17.7 | 20.7 | 40.5 | 37.6 | 1.83 | 844
787 | 2022-12-25 13:07 | 17.8 | 20.9 | 40.8 | 37.9 | 1.831 | 844
788 | 2022-12-25 13:08 | 18.2 | 21.3 | 40.9 | 38.2 | 1.827 | 843
789 | 2022-12-25 13:09 | 18 | 21.6 | 40.7 | 38.2 | 1.836 | 841
790 | 2022-12-25 13:10 | 18 | 21.9 | 40.5 | 38 | 1.834 | 843
791 | 2022-12-25 13:11 | 17.8 | 22 | 40.3 | 37.9 | 1.832 | 841
792 | 2022-12-25 13:12 | 18 | 22.1 | 40.2 | 37.7 | 1.833 | 842
793 | 2022-12-25 13:13 | 18 | 22.2 | 40.1 | 37.7 | 1.828 | 839
794 | 2022-12-25 13:14 | 18.1 | 22 | 39.9 | 38.4 | 1.826 | 838
795 | 2022-12-25 13:15 | 18 | 21.7 | 39.9 | 38.3 | 1.821 | 836
796 | 2022-12-25 13:16 | 17.4 | 21.4 | 39.8 | 38.3 | 1.706 | 837
797 | 2022-12-25 13:17 | 17.8 | 21.2 | 39.7 | 38.4 | 1.501 | 834
798 | 2022-12-25 13:18 | 17.8 | 21 | 39.6 | 38.5 | 1.501 | 835
799 | 2022-12-25 13:19 | 17.7 | 20.9 | 39.5 | 38.5 | 1.494 | 834
800 | 2022-12-25 13:20 | 17.7 | 20.8 | 39.5 | 38.4 | 1.291 | 834
801 | 2022-12-25 13:21 | 17.9 | 20.7 | 39.4 | 38.3 | 1.09 | 832
802 | 2022-12-25 13:22 | 17.7 | 20.7 | 39.4 | 38 | 1.091 | 829
803 | 2022-12-25 13:23 | 17.1 | 20.6 | 39.3 | 37.9 | 1.093 | 827
804 | 2022-12-25 13:24 | 17.4 | 20.6 | 39.1 | 37.9 | 1.088 | 825
805 | 2022-12-25 13:25 | 17.7 | 20.6 | 39 | 37.6 | 1.091 | 825
806 | 2022-12-25 13:26 | 17.9 | 20.6 | 39.1 | 37.6 | 1.089 | 822
807 | 2022-12-25 13:27 | 17.5 | 20.5 | 39.1 | 37.6 | 1.088 | 820
808 | 2022-12-25 13:28 | 17.4 | 20.5 | 38.9 | 37.6 | 1.214 | 821
809 | 2022-12-25 13:29 | 17.1 | 20.5 | 38.9 | 37.5 | 1.504 | 820
810 | 2022-12-25 13:30 | 17.8 | 20.5 | 38.8 | 36.9 | 1.504 | 818
811 | 2022-12-25 13:31 | 17.9 | 20.5 | 38.7 | 36.9 | 1.5 | 818
812 | 2022-12-25 13:32 | 18 | 20.6 | 38.5 | 36.9 | 1.802 | 815
813 | 2022-12-25 13:33 | 17.8 | 20.7 | 38.4 | 34.3 | 1.824 | 814
814 | 2022-12-25 13:34 | 18.1 | 20.8 | 38.4 | 36 | 1.823 | 811
815 | 2022-12-25 13:35 | 18.2 | 20.9 | 38.7 | 36.1 | 1.823 | 806
816 | 2022-12-25 13:36 | 18.2 | 21.3 | 39.1 | 36.4 | 1.829 | 803
817 | 2022-12-25 13:37 | 18.6 | 21.6 | 39.3 | 36.7 | 1.828 | 800
818 | 2022-12-25 13:38 | 18.8 | 21.8 | 39.7 | 36.9 | 1.834 | 802
819 | 2022-12-25 13:39 | 18.3 | 21.9 | 40 | 37.3 | 1.829 | 802
820 | 2022-12-25 13:40 | 18.3 | 22 | 40.2 | 37.5 | 1.834 | 801
821 | 2022-12-25 13:41 | 18.3 | 22 | 40.5 | 39.4 | 1.834 | 800
822 | 2022-12-25 13:42 | 17.8 | 21.7 | 40.4 | 39.6 | 1.83 | 798
823 | 2022-12-25 13:43 | 17.4 | 21.4 | 40.5 | 39.4 | 1.791 | 792
824 | 2022-12-25 13:44 | 17.7 | 21.2 | 40.5 | 39.5 | 1.496 | 789
825 | 2022-12-25 13:45 | 17.8 | 21 | 40.5 | 39.5 | 1.43 | 789
826 | 2022-12-25 13:46 | 17.8 | 20.9 | 40.5 | 39.4 | 0 | 787
827 | 2022-12-25 13:47 | 17.8 | 20.7 | 40.4 | 39.3 | 0 | 785
828 | 2022-12-25 13:48 | 17.6 | 20.7 | 40.3 | 39.2 | 0 | 782
829 | 2022-12-25 13:49 | 17.7 | 20.6 | 40.2 | 38.8 | 0 | 779
830 | 2022-12-25 13:50 | 18 | 20.5 | 40 | 38.5 | 0 | 778
831 | 2022-12-25 13:51 | 18.1 | 20.5 | 39.9 | 38.2 | 0 | 783
832 | 2022-12-25 13:52 | 18.2 | 20.5 | 39.7 | 37.9 | 0 | 779
833 | 2022-12-25 13:53 | 17.6 | 20.4 | 39.6 | 37.8 | 0.917 | 776
834 | 2022-12-25 13:54 | 17.5 | 20.4 | 40.2 | 36 | 1.091 | 775
835 | 2022-12-25 13:55 | 17.8 | 20.4 | 40 | 38.5 | 1.092 | 773
836 | 2022-12-25 13:56 | 17.8 | 20.4 | 39.8 | 38.3 | 1.091 | 771
837 | 2022-12-25 13:57 | 18.1 | 20.4 | 39.9 | 38.3 | 1.088 | 772
838 | 2022-12-25 13:58 | 18.4 | 20.5 | 39.7 | 38.3 | 1.609 | 773
839 | 2022-12-25 13:59 | 18.5 | 20.6 | 39.7 | 37 | 1.823 | 771
840 | 2022-12-25 14:00 | 18.3 | 20.8 | 39.6 | 36.1 | 1.836 | 765
841 | 2022-12-25 14:01 | 17.9 | 21.1 | 39.3 | 37 | 1.836 | 766
842 | 2022-12-25 14:02 | 17.9 | 21.4 | 39 | 36.7 | 1.829 | 762
843 | 2022-12-25 14:03 | 17.8 | 21.7 | 39 | 36.5 | 1.834 | 763
844 | 2022-12-25 14:04 | 17.5 | 21.8 | 39 | 36.5 | 1.835 | 759
845 | 2022-12-25 14:05 | 17.8 | 22 | 39.5 | 36.6 | 1.833 | 759
846 | 2022-12-25 14:06 | 17.7 | 22.1 | 39.7 | 37.2 | 1.834 | 757
847 | 2022-12-25 14:07 | 17.9 | 21.9 | 40.1 | 38.1 | 1.829 | 750
848 | 2022-12-25 14:08 | 18 | 21.6 | 40.4 | 38.5 | 1.831 | 746
849 | 2022-12-25 14:09 | 17.8 | 21.3 | 40.9 | 38.8 | 1.763 | 742
850 | 2022-12-25 14:10 | 18 | 21.1 | 41.2 | 39.1 | 1.506 | 735
851 | 2022-12-25 14:11 | 17.9 | 21 | 41.5 | 39.3 | 1.512 | 729
852 | 2022-12-25 14:12 | 17.5 | 20.9 | 42.1 | 39.7 | 1.511 | 725
853 | 2022-12-25 14:13 | 17.6 | 20.8 | 42.4 | 40.2 | 1.506 | 720
854 | 2022-12-25 14:14 | 17.6 | 20.7 | 42.7 | 40.3 | 1.509 | 719
855 | 2022-12-25 14:15 | 17.8 | 20.7 | 43.1 | 40.7 | 1.511 | 717
856 | 2022-12-25 14:16 | 18 | 20.7 | 43.5 | 41.8 | 1.509 | 708
857 | 2022-12-25 14:17 | 18.3 | 20.6 | 43.9 | 42.2 | 1.515 | 702
858 | 2022-12-25 14:18 | 17.5 | 20.6 | 44.4 | 42.6 | 0.05 | 698
859 | 2022-12-25 14:19 | 16.9 | 20.6 | 44.7 | 42.8 | 0 | 695
860 | 2022-12-25 14:20 | 16.9 | 20.6 | 44.5 | 42.6 | 0 | 697
861 | 2022-12-25 14:21 | 16.9 | 20.6 | 44.3 | 42.1 | 0 | 695
862 | 2022-12-25 14:22 | 17.3 | 20.4 | 44.1 | 41.6 | 0 | 695
863 | 2022-12-25 14:23 | 16.9 | 20.4 | 43.8 | 41.2 | 0 | 693
864 | 2022-12-25 14:24 | 17 | 20.4 | 43.6 | 40.8 | 0 | 685
865 | 2022-12-25 14:25 | 17.2 | 20.4 | 43.4 | 40.4 | 0.316 | 678
866 | 2022-12-25 14:26 | 17.3 | 20.4 | 47 | 41.4 | 0 | 673
867 | 2022-12-25 14:27 | 17.3 | 20.4 | 47.5 | 41.4 | 0.542 | 668
868 | 2022-12-25 14:28 | 17.4 | 20.5 | 47.6 | 39.1 | 0.956 | 662
869 | 2022-12-25 14:29 | 17.1 | 20.6 | 47.3 | 43.5 | 0.963 | 667
870 | 2022-12-25 14:30 | 17.3 | 20.9 | 47 | 44 | 1.573 | 665
871 | 2022-12-25 14:31 | 16.9 | 21.3 | 46.9 | 41.3 | 1.606 | 660
872 | 2022-12-25 14:32 | 17.3 | 21.6 | 46.3 | 43.6 | 1.842 | 661
873 | 2022-12-25 14:33 | 17.4 | 21.9 | 46 | 42.8 | 1.842 | 658
874 | 2022-12-25 14:34 | 17.3 | 22.2 | 46 | 42.6 | 1.846 | 653
875 | 2022-12-25 14:35 | 17 | 22.3 | 45.8 | 42.7 | 1.848 | 649
876 | 2022-12-25 14:36 | 17 | 22.2 | 45.7 | 43.7 | 1.845 | 643
877 | 2022-12-25 14:37 | 16.7 | 21.9 | 45.6 | 43.6 | 1.839 | 640
878 | 2022-12-25 14:38 | 17 | 21.5 | 45.6 | 43.6 | 1.789 | 636
879 | 2022-12-25 14:39 | 17.2 | 21.4 | 45.5 | 43.4 | 1.517 | 631
880 | 2022-12-25 14:40 | 17.1 | 21.1 | 45.3 | 43.6 | 1.515 | 630
881 | 2022-12-25 14:41 | 16.9 | 21.1 | 45.2 | 43.8 | 1.519 | 635
882 | 2022-12-25 14:42 | 16.8 | 21 | 45 | 43.7 | 1.51 | 633
883 | 2022-12-25 14:43 | 17.1 | 20.8 | 45 | 43.6 | 1.481 | 628
884 | 2022-12-25 14:44 | 17.2 | 20.8 | 45 | 43.5 | 0 | 623
885 | 2022-12-25 14:45 | 17 | 20.8 | 45 | 43.1 | 0 | 618
886 | 2022-12-25 14:46 | 17.1 | 20.8 | 44.8 | 42.8 | 0 | 616
887 | 2022-12-25 14:47 | 17 | 20.7 | 44.6 | 42.4 | 0 | 615
888 | 2022-12-25 14:48 | 17 | 20.7 | 44.3 | 42 | 0 | 615
889 | 2022-12-25 14:49 | 17.2 | 20.6 | 44.1 | 41.6 | 0 | 613
890 | 2022-12-25 14:50 | 17.3 | 20.6 | 43.9 | 41.1 | 0 | 614
891 | 2022-12-25 14:51 | 17 | 20.6 | 43.7 | 40.8 | 0 | 608
892 | 2022-12-25 14:52 | 17.2 | 20.5 | 43.5 | 40.4 | 0 | 601
893 | 2022-12-25 14:53 | 17.1 | 20.5 | 43.2 | 40 | 0 | 599
894 | 2022-12-25 14:54 | 17.3 | 20.4 | 43 | 39.8 | 0 | 602
895 | 2022-12-25 14:55 | 17.5 | 20.4 | 42.8 | 41.3 | 0.974 | 596
896 | 2022-12-25 14:56 | 17.2 | 20.3 | 44.5 | 39.5 | 0.984 | 596
897 | 2022-12-25 14:57 | 17.1 | 20.3 | 44 | 42.6 | 1.507 | 595
898 | 2022-12-25 14:58 | 17.1 | 20.4 | 44.1 | 41.2 | 1.589 | 591
899 | 2022-12-25 14:59 | 17.2 | 20.5 | 43.8 | 41.5 | 1.833 | 587
900 | 2022-12-25 15:00 | 17.2 | 20.5 | 43.7 | 40.5 | 1.844 | 582
901 | 2022-12-25 15:01 | 17.3 | 20.6 | 43.5 | 40.6 | 1.839 | 583
902 | 2022-12-25 15:02 | 17.3 | 21 | 43.2 | 40.4 | 1.836 | 579
903 | 2022-12-25 15:03 | 17.2 | 21.4 | 43.1 | 40.2 | 1.841 | 577
904 | 2022-12-25 15:04 | 17.2 | 21.8 | 42.8 | 40.1 | 1.839 | 574
905 | 2022-12-25 15:05 | 17.3 | 22 | 42.6 | 39.9 | 1.838 | 570
906 | 2022-12-25 15:06 | 16.7 | 22.1 | 42.4 | 40.2 | 1.836 | 565
907 | 2022-12-25 15:07 | 16.6 | 22.2 | 42.2 | 41 | 1.84 | 561
908 | 2022-12-25 15:08 | 16.7 | 21.9 | 42.2 | 41 | 0.767 | 559
909 | 2022-12-25 15:09 | 16.7 | 21.6 | 42.1 | 41 | 0 | 555
910 | 2022-12-25 15:10 | 16.7 | 21.3 | 42.1 | 40.8 | 0 | 548
911 | 2022-12-25 15:11 | 16.2 | 21.2 | 41.9 | 40.4 | 0 | 543
912 | 2022-12-25 15:12 | 16.5 | 21 | 41.6 | 40 | 0 | 551
913 | 2022-12-25 15:13 | 16.6 | 20.9 | 41.4 | 39.6 | 0 | 546
914 | 2022-12-25 15:14 | 16.7 | 20.8 | 41.2 | 39.3 | 0 | 540
915 | 2022-12-25 15:15 | 16.9 | 20.7 | 41 | 38.9 | 0 | 534
916 | 2022-12-25 15:16 | 16.6 | 20.6 | 40.8 | 38.6 | 0 | 529
917 | 2022-12-25 15:17 | 16.9 | 20.6 | 40.6 | 38.3 | 0 | 527
918 | 2022-12-25 15:18 | 16.8 | 20.5 | 40.4 | 37.9 | 0 | 523
919 | 2022-12-25 15:19 | 17 | 20.5 | 40.2 | 37.6 | 0.006 | 518
920 | 2022-12-25 15:20 | 17.3 | 20.4 | 40 | 37.7 | 0 | 514
921 | 2022-12-25 15:21 | 16.9 | 20.3 | 39.8 | 37.3 | 0.651 | 509
922 | 2022-12-25 15:22 | 16.8 | 20.3 | 41.4 | 38 | 1.498 | 507
923 | 2022-12-25 15:23 | 16.8 | 20.3 | 41.4 | 38.8 | 1.511 | 501
924 | 2022-12-25 15:24 | 16.8 | 20.3 | 41.3 | 39.1 | 1.51 | 497
925 | 2022-12-25 15:25 | 16.5 | 20.3 | 41 | 39.3 | 1.779 | 497
926 | 2022-12-25 15:26 | 16.7 | 20.5 | 41.1 | 36.9 | 1.835 | 492
927 | 2022-12-25 15:27 | 16.9 | 20.5 | 41.1 | 38.4 | 1.839 | 483
928 | 2022-12-25 15:28 | 17 | 20.7 | 40.7 | 38.3 | 1.836 | 477
929 | 2022-12-25 15:29 | 17 | 21.1 | 40.4 | 38 | 1.838 | 475
930 | 2022-12-25 15:30 | 16.9 | 21.4 | 40.3 | 37.8 | 1.836 | 474
931 | 2022-12-25 15:31 | 17.1 | 21.7 | 40.1 | 37.6 | 1.834 | 471
932 | 2022-12-25 15:32 | 17.1 | 21.9 | 40 | 37.5 | 1.836 | 466
933 | 2022-12-25 15:33 | 16.6 | 22 | 39.8 | 37.4 | 1.838 | 458
934 | 2022-12-25 15:34 | 16.2 | 22 | 39.7 | 37.2 | 1.835 | 452
935 | 2022-12-25 15:35 | 16.5 | 22.1 | 40.1 | 38.6 | 1.844 | 453
936 | 2022-12-25 15:36 | 16.6 | 21.8 | 40.4 | 39.1 | 0 | 447
937 | 2022-12-25 15:37 | 16.6 | 21.6 | 40.6 | 39.2 | 0 | 436
938 | 2022-12-25 15:38 | 16.8 | 21.1 | 40.4 | 39 | 0 | 430
939 | 2022-12-25 15:39 | 16.5 | 21.1 | 40.2 | 38.7 | 0 | 425
940 | 2022-12-25 15:40 | 16.5 | 20.9 | 40 | 38.3 | 0 | 419
941 | 2022-12-25 15:41 | 16.4 | 20.8 | 39.8 | 38 | 0 | 410
942 | 2022-12-25 15:42 | 15.9 | 20.8 | 39.6 | 37.7 | 0 | 407
943 | 2022-12-25 15:43 | 15.8 | 20.7 | 39.4 | 37.4 | 0 | 406
944 | 2022-12-25 15:44 | 15.8 | 20.5 | 39.1 | 37.1 | 0 | 408
945 | 2022-12-25 15:45 | 15.8 | 20.5 | 38.9 | 36.8 | 0 | 406
946 | 2022-12-25 15:46 | 15.6 | 20.4 | 38.7 | 36.5 | 0 | 398
947 | 2022-12-25 15:47 | 15.8 | 20.4 | 38.5 | 36.3 | 0 | 397
948 | 2022-12-25 15:48 | 16.3 | 20.3 | 38.3 | 36.5 | 0 | 393
949 | 2022-12-25 15:49 | 16.3 | 20.3 | 38.1 | 36 | 0.889 | 389
950 | 2022-12-25 15:50 | 16 | 20.3 | 41.6 | 34.5 | 1.336 | 383
951 | 2022-12-25 15:51 | 16 | 20.3 | 41.4 | 37.5 | 1.806 | 376
952 | 2022-12-25 15:52 | 15.5 | 20.4 | 41.2 | 36.1 | 1.835 | 371
953 | 2022-12-25 15:53 | 15.6 | 20.6 | 41.1 | 38.4 | 1.84 | 369
954 | 2022-12-25 15:54 | 15.5 | 20.6 | 41 | 38.4 | 1.831 | 368
955 | 2022-12-25 15:55 | 15.8 | 21 | 41 | 38.2 | 1.833 | 365
956 | 2022-12-25 15:56 | 15.5 | 21.3 | 40.9 | 38.3 | 1.836 | 362
957 | 2022-12-25 15:57 | 15.6 | 21.4 | 40.7 | 38.2 | 1.835 | 354
958 | 2022-12-25 15:58 | 16 | 21.7 | 40.5 | 38 | 1.838 | 347
959 | 2022-12-25 15:59 | 15.7 | 21.8 | 40.2 | 37.8 | 1.835 | 344
960 | 2022-12-25 16:00 | 16.2 | 21.9 | 40.1 | 37.6 | 1.832 | 341
961 | 2022-12-25 16:01 | 16.1 | 22 | 40 | 37.5 | 1.832 | 338
962 | 2022-12-25 16:02 | 16.1 | 22.1 | 39.8 | 38.7 | 1.835 | 334
963 | 2022-12-25 16:03 | 16.1 | 21.8 | 39.7 | 38.7 | 1.833 | 331
964 | 2022-12-25 16:04 | 15.8 | 21.4 | 40 | 38.7 | 0 | 327
965 | 2022-12-25 16:05 | 15.8 | 21.2 | 40.1 | 38.7 | 0 | 324
966 | 2022-12-25 16:06 | 15.7 | 21 | 39.9 | 38.4 | 0 | 320
967 | 2022-12-25 16:07 | 15.9 | 20.9 | 39.7 | 37.9 | 0 | 316
968 | 2022-12-25 16:08 | 15.5 | 20.8 | 39.5 | 37.6 | 0 | 310
969 | 2022-12-25 16:09 | 15.5 | 20.8 | 39.3 | 37.3 | 0 | 306
970 | 2022-12-25 16:10 | 15.3 | 20.7 | 39.1 | 37 | 0 | 300
971 | 2022-12-25 16:11 | 15 | 20.6 | 38.9 | 36.7 | 0 | 295
972 | 2022-12-25 16:12 | 15 | 20.5 | 38.7 | 36.4 | 0 | 291
973 | 2022-12-25 16:13 | 15 | 20.5 | 38.5 | 36.1 | 0 | 289
974 | 2022-12-25 16:14 | 14.8 | 20.4 | 38.2 | 35.8 | 0 | 288
975 | 2022-12-25 16:15 | 14.6 | 20.3 | 38 | 35.5 | 0 | 287
976 | 2022-12-25 16:16 | 14.6 | 20.3 | 37.8 | 36.1 | 0 | 283
977 | 2022-12-25 16:17 | 14.7 | 20.3 | 37.7 | 35.6 | 0.918 | 277
978 | 2022-12-25 16:18 | 14.6 | 20.2 | 41.7 | 33.2 | 0.99 | 271
979 | 2022-12-25 16:19 | 14.8 | 20.4 | 41.4 | 39.6 | 1.773 | 265
980 | 2022-12-25 16:20 | 14.4 | 20.4 | 41.1 | 37.4 | 1.844 | 262
981 | 2022-12-25 16:21 | 14.5 | 20.5 | 41.1 | 38.2 | 1.995 | 243
982 | 2022-12-25 16:22 | 14.6 | 20.8 | 40.9 | 35.2 | 2.007 | 236
983 | 2022-12-25 16:23 | 14.5 | 21.1 | 40.7 | 37.3 | 2.01 | 248
984 | 2022-12-25 16:24 | 14.2 | 21.3 | 40.3 | 37.2 | 2.003 | 240
985 | 2022-12-25 16:25 | 14.2 | 21.6 | 40.2 | 37 | 2.014 | 236
986 | 2022-12-25 16:26 | 14.1 | 21.8 | 39.9 | 36.9 | 2.006 | 231
987 | 2022-12-25 16:27 | 14.3 | 22 | 39.6 | 36.7 | 2.006 | 226
988 | 2022-12-25 16:28 | 13.9 | 22 | 39.4 | 36.8 | 2.002 | 221
989 | 2022-12-25 16:29 | 13.6 | 22 | 39.2 | 37.8 | 2.01 | 217
990 | 2022-12-25 16:30 | 14 | 21.8 | 39.1 | 37.7 | 1.991 | 212
991 | 2022-12-25 16:31 | 14 | 21.5 | 39.1 | 38 | 1.81 | 207
992 | 2022-12-25 16:32 | 13.6 | 21.3 | 39.1 | 38.1 | 1.664 | 204
993 | 2022-12-25 16:33 | 13.6 | 21.2 | 39 | 37.9 | 1.495 | 199
994 | 2022-12-25 16:34 | 12.8 | 21 | 39.1 | 37.9 | 1.169 | 193
995 | 2022-12-25 16:35 | 12.8 | 21 | 39.6 | 37.9 | 1.088 | 188
996 | 2022-12-25 16:36 | 12.9 | 20.9 | 40.1 | 38.1 | 1.094 | 181
997 | 2022-12-25 16:37 | 12.9 | 20.7 | 40.4 | 38.6 | 0.826 | 147
998 | 2022-12-25 16:38 | 12.6 | 20.6 | 40.7 | 38.8 | 0 | 91
999 | 2022-12-25 16:39 | 12.7 | 20.6 | 40.7 | 38.7 | 0 | 50
1000 | 2022-12-25 16:40 | 13 | 20.6 | 40.4 | 38.2 | 0 | 34
1001 | 2022-12-25 16:41 | 12.8 | 20.6 | 40.1 | 37.8 | 0 | 18
1002 | 2022-12-25 16:42 | 12.4 | 20.5 | 39.9 | 37.3 | 0 | 16
1003 | 2022-12-25 16:43 | 12.2 | 20.6 | 39.6 | 37 | 0 | 15
1004 | 2022-12-25 16:44 | 12 | 20.5 | 39.9 | 37.3 | 0.301 | 13
1005 | 2022-12-25 16:45 | 11.9 | 20.5 | 41.5 | 37.1 | 0 | 11
1006 | 2022-12-25 16:46 | 11.6 | 20.4 | 41.5 | 36.7 | 0.971 | 11
1007 | 2022-12-25 16:47 | 11.6 | 20.4 | 41.2 | 38.7 | 0.978 | 10
1008 | 2022-12-25 16:48 | 11.5 | 20.3 | 41.1 | 39.5 | 0.974 | 9
1009 | 2022-12-25 16:49 | 11.2 | 20.3 | 40.9 | 39.5 | 0.974 | 9
1010 | 2022-12-25 16:50 | 11.2 | 20.3 | 40.8 | 39.4 | 1.465 | 8
1011 | 2022-12-25 16:51 | 10.9 | 20.4 | 40.8 | 35.4 | 1.556 | 8
1012 | 2022-12-25 16:52 | 10.9 | 20.4 | 40.7 | 38.4 | 1.803 | 7
1013 | 2022-12-25 16:53 | 10.9 | 20.6 | 40.5 | 37.6 | 1.828 | 7
1014 | 2022-12-25 16:54 | 10.8 | 20.8 | 40.5 | 37.8 | 1.826 | 7
1015 | 2022-12-25 16:55 | 10.9 | 21.2 | 40.3 | 37.8 | 1.826 | 7
1016 | 2022-12-25 16:56 | 10.7 | 21.4 | 40.1 | 37.6 | 1.825 | 6
1017 | 2022-12-25 16:57 | 10.4 | 21.6 | 39.9 | 37.5 | 1.816 | 5
1018 | 2022-12-25 16:58 | 10.4 | 21.8 | 39.7 | 37.3 | 1.824 | 5
1019 | 2022-12-25 16:59 | 10.5 | 21.9 | 39.5 | 37.1 | 1.82 | 4
1020 | 2022-12-25 17:00 | 10.4 | 21.9 | 39.4 | 37.3 | 1.828 | 4
1021 | 2022-12-25 17:01 | 10.3 | 22 | 39.2 | 37.4 | 1.831 | 3
1022 | 2022-12-25 17:02 | 10.3 | 21.9 | 39.1 | 38.1 | 1.827 | 3
1023 | 2022-12-25 17:03 | 10 | 21.5 | 39.1 | 38.1 | 1.749 | 2
1024 | 2022-12-25 17:04 | 10 | 21.2 | 39.1 | 38 | 1.554 | 2
1025 | 2022-12-25 17:05 | 9.9 | 21.1 | 39 | 37.9 | 1.153 | 2
1026 | 2022-12-25 17:06 | 9.9 | 20.9 | 38.9 | 37.5 | 1.086 | 1
1027 | 2022-12-25 17:07 | 9.9 | 20.8 | 38.9 | 37.5 | 1.089 | 0
1028 | 2022-12-25 17:08 | 9.8 | 20.8 | 38.7 | 37.4 | 1.088 | 0
1029 | 2022-12-25 17:09 | 9.9 | 20.7 | 38.7 | 37.3 | 1.09 | 0
1030 | 2022-12-25 17:10 | 9.9 | 20.6 | 38.6 | 37.2 | 1.094 | 0
1031 | 2022-12-25 17:11 | 9.7 | 20.6 | 38.6 | 37.2 | 1.091 | 0
1032 | 2022-12-25 17:12 | 9.7 | 20.6 | 38.4 | 37.1 | 1.085 | 0
1033 | 2022-12-25 17:13 | 9.6 | 20.5 | 38.3 | 37.7 | 1.088 | 0
1034 | 2022-12-25 17:14 | 9.4 | 20.5 | 38.3 | 38 | 1.498 | 0
1035 | 2022-12-25 17:15 | 9.7 | 20.4 | 38.2 | 37.1 | 1.499 | 0
1036 | 2022-12-25 17:16 | 9.5 | 20.4 | 38.3 | 37.2 | 1.783 | 0
1037 | 2022-12-25 17:17 | 9.3 | 20.4 | 38.1 | 34 | 1.783 | 0
1038 | 2022-12-25 17:18 | 9.5 | 20.5 | 38.2 | 36.3 | 1.679 | 0
1039 | 2022-12-25 17:19 | 9.6 | 20.4 | 38.3 | 36.3 | 1.566 | 0
1040 | 2022-12-25 17:20 | 9.5 | 20.6 | 38.4 | 36.3 | 1.82 | 0
1041 | 2022-12-25 17:21 | 9.5 | 20.6 | 38.8 | 35.1 | 1.851 | 0
1042 | 2022-12-25 17:22 | 9.2 | 20.9 | 39.1 | 36.2 | 1.851 | 0
1043 | 2022-12-25 17:23 | 9.4 | 20.9 | 39.2 | 36.4 | 1.85 | 0
1044 | 2022-12-25 17:24 | 9.7 | 21.2 | 39.6 | 36.6 | 1.848 | 0
1045 | 2022-12-25 17:25 | 9.5 | 21.5 | 39.9 | 37.3 | 1.85 | 0
1046 | 2022-12-25 17:26 | 9.6 | 21.7 | 40.1 | 38 | 1.854 | 0
1047 | 2022-12-25 17:27 | 9.4 | 21.9 | 40.6 | 38.3 | 1.847 | 0
1048 | 2022-12-25 17:28 | 9.6 | 22 | 40.9 | 38.6 | 1.731 | 0
1049 | 2022-12-25 17:29 | 9.4 | 22 | 41 | 38.5 | 1.56 | 0
1050 | 2022-12-25 17:30 | 9.1 | 21.9 | 41.1 | 39.1 | 1.693 | 0
1051 | 2022-12-25 17:31 | 9.2 | 21.8 | 40.9 | 40.2 | 1.826 | 0
1052 | 2022-12-25 17:32 | 9 | 21.4 | 40.9 | 39.7 | 1.826 | 0
1053 | 2022-12-25 17:33 | 8.8 | 21.1 | 40.9 | 39.7 | 1.75 | 0
1054 | 2022-12-25 17:34 | 8.8 | 21 | 41.1 | 39.7 | 1.091 | 0
1055 | 2022-12-25 17:35 | 9 | 20.9 | 41.5 | 39.6 | 1.09 | 0
1056 | 2022-12-25 17:36 | 8.9 | 20.8 | 42 | 39.9 | 1.088 | 0
1057 | 2022-12-25 17:37 | 8.8 | 20.8 | 42.4 | 40.3 | 1.092 | 0
1058 | 2022-12-25 17:38 | 8.8 | 20.6 | 42.9 | 40.6 | 1.088 | 0
1059 | 2022-12-25 17:39 | 9 | 20.7 | 43.3 | 41.1 | 1.091 | 0
1060 | 2022-12-25 17:40 | 9.1 | 20.6 | 43.6 | 41.5 | 1.09 | 0
1061 | 2022-12-25 17:41 | 8.7 | 20.7 | 44.1 | 41.8 | 1.091 | 0
1062 | 2022-12-25 17:42 | 8.8 | 20.5 | 44.4 | 42.2 | 1.091 | 0
1063 | 2022-12-25 17:43 | 8.6 | 20.5 | 44.8 | 42.5 | 1.092 | 0
1064 | 2022-12-25 17:44 | 8.8 | 20.5 | 45.1 | 42.9 | 1.093 | 0
1065 | 2022-12-25 17:45 | 9 | 20.6 | 45.6 | 43.2 | 1.477 | 0
1066 | 2022-12-25 17:46 | 8.9 | 20.6 | 46 | 40.1 | 1.509 | 0
1067 | 2022-12-25 17:47 | 8.6 | 20.5 | 45.5 | 43.5 | 1.508 | 0
1068 | 2022-12-25 17:48 | 8.6 | 20.5 | 45.3 | 42.9 | 1.508 | 0
1069 | 2022-12-25 17:49 | 8.8 | 20.5 | 45.1 | 43.7 | 1.514 | 0
1070 | 2022-12-25 17:50 | 8.8 | 20.4 | 45.1 | 43.8 | 1.512 | 0
1071 | 2022-12-25 17:51 | 8.6 | 20.4 | 45.1 | 43.8 | 1.513 | 0
1072 | 2022-12-25 17:52 | 8.5 | 20.5 | 45.1 | 43.8 | 1.816 | 0
1073 | 2022-12-25 17:53 | 8.5 | 20.6 | 45.1 | 41.5 | 1.836 | 0
1074 | 2022-12-25 17:54 | 8.6 | 20.6 | 44.9 | 42.2 | 1.937 | 0
1075 | 2022-12-25 17:55 | 8.5 | 20.8 | 44.4 | 41 | 1.852 | 0
1076 | 2022-12-25 17:56 | 8.6 | 21.1 | 44.2 | 40.9 | 1.859 | 0
1077 | 2022-12-25 17:57 | 8.5 | 21.4 | 43.8 | 41.2 | 1.854 | 0
1078 | 2022-12-25 17:58 | 8.4 | 21.6 | 43.6 | 41.1 | 1.855 | 0
1079 | 2022-12-25 17:59 | 8.6 | 22 | 43.5 | 40.9 | 1.844 | 0
1080 | 2022-12-25 18:00 | 8.4 | 22.1 | 43.2 | 41.8 | 0 | 0
1081 | 2022-12-25 18:01 | 8.7 | 22.2 | 43.2 | 41.7 | 0 | 0
1082 | 2022-12-25 18:02 | 8.5 | 21.9 | 42.9 | 41.2 | 0 | 0
1083 | 2022-12-25 18:03 | 8.7 | 21.6 | 42.6 | 40.6 | 0 | 0
1084 | 2022-12-25 18:04 | 8.7 | 21.3 | 42.4 | 40 | 0 | 0
1085 | 2022-12-25 18:05 | 8.6 | 21.1 | 42.1 | 39.5 | 0 | 0
1086 | 2022-12-25 18:06 | 8.7 | 20.9 | 41.8 | 39 | 0 | 0
1087 | 2022-12-25 18:07 | 8.4 | 20.7 | 41.6 | 39.5 | 0 | 0
1088 | 2022-12-25 18:08 | 8.5 | 20.5 | 41.3 | 39.3 | 0.472 | 0
1089 | 2022-12-25 18:09 | 8.5 | 20.4 | 42.8 | 39.4 | 1.087 | 0
1090 | 2022-12-25 18:10 | 8.5 | 20.4 | 42.7 | 40.7 | 1.093 | 0
1091 | 2022-12-25 18:11 | 8.7 | 20.4 | 42.5 | 40.7 | 1.251 | 0
1092 | 2022-12-25 18:12 | 8.5 | 20.3 | 42.5 | 40.8 | 1.505 | 0
1093 | 2022-12-25 18:13 | 8.7 | 20.4 | 42.3 | 40.2 | 1.512 | 0
1094 | 2022-12-25 18:14 | 8.8 | 20.4 | 42.3 | 40.1 | 1.506 | 0
1095 | 2022-12-25 18:15 | 8.7 | 20.4 | 42.1 | 40.1 | 1.503 | 0
1096 | 2022-12-25 18:16 | 8.6 | 20.4 | 42 | 40 | 1.502 | 0
1097 | 2022-12-25 18:17 | 8.6 | 20.3 | 42 | 39.9 | 1.506 | 0
1098 | 2022-12-25 18:18 | 8.5 | 20.4 | 41.9 | 39.8 | 1.503 | 0
1099 | 2022-12-25 18:19 | 8.6 | 20.4 | 41.7 | 39.7 | 1.639 | 0
1100 | 2022-12-25 18:20 | 8.7 | 20.4 | 41.6 | 38.9 | 1.823 | 0
1101 | 2022-12-25 18:21 | 8.4 | 20.4 | 41.5 | 38.6 | 1.826 | 0
1102 | 2022-12-25 18:22 | 8.7 | 20.7 | 41.1 | 38.6 | 1.821 | 0
1103 | 2022-12-25 18:23 | 8.4 | 21 | 40.8 | 38.3 | 1.822 | 0
1104 | 2022-12-25 18:24 | 8.5 | 21.4 | 40.6 | 38.1 | 1.823 | 0
1105 | 2022-12-25 18:25 | 8.6 | 21.5 | 40.4 | 37.9 | 1.83 | 0
1106 | 2022-12-25 18:26 | 8.5 | 21.7 | 40.2 | 38.2 | 1.833 | 0
1107 | 2022-12-25 18:27 | 8.7 | 21.7 | 40.1 | 38.1 | 1.829 | 0
1108 | 2022-12-25 18:28 | 8.5 | 20.2 | 40 | 38 | 1.821 | 0
1109 | 2022-12-25 18:29 | 8.4 | 21.9 | 39.9 | 38.5 | 0 | 0
1110 | 2022-12-25 18:30 | 8.3 | 22 | 39.8 | 38.4 | 0 | 0
1111 | 2022-12-25 18:31 | 8.3 | 21.6 | 39.6 | 38.2 | 0 | 0
1112 | 2022-12-25 18:32 | 8.5 | 21.5 | 39.4 | 37.7 | 0 | 0
1113 | 2022-12-25 18:33 | 8.4 | 21.2 | 39.1 | 37.2 | 0 | 0
1114 | 2022-12-25 18:34 | 8.3 | 21 | 38.9 | 36.7 | 0 | 0
1115 | 2022-12-25 18:35 | 8.4 | 20.7 | 38.6 | 36.3 | 0 | 0
1116 | 2022-12-25 18:36 | 8.4 | 20.6 | 38.4 | 35.9 | 0 | 0
1117 | 2022-12-25 18:37 | 8.1 | 20.6 | 38.1 | 35.5 | 0.08 | 0
1118 | 2022-12-25 18:38 | 8.3 | 20.5 | 37.9 | 36.9 | 0 | 0
1119 | 2022-12-25 18:39 | 8.3 | 20.3 | 37.7 | 37.1 | 0.855 | 0
1120 | 2022-12-25 18:40 | 8.3 | 20.2 | 42.1 | 36.2 | 0.948 | 0
1121 | 2022-12-25 18:41 | 8.1 | 20.3 | 42.8 | 39.9 | 1.64 | 0
1122 | 2022-12-25 18:42 | 8.2 | 20.3 | 42.8 | 39.6 | 1.839 | 0
1123 | 2022-12-25 18:43 | 8.1 | 20.3 | 43.4 | 39.7 | 1.844 | 0
1124 | 2022-12-25 18:44 | 8 | 20.3 | 43 | 40.4 | 1.835 | 0
1125 | 2022-12-25 18:45 | 8 | 20.4 | 42.8 | 39.9 | 1.898 | 0
1126 | 2022-12-25 18:46 | 8 | 20.7 | 42.8 | 39.4 | 2 | 0
1127 | 2022-12-25 18:47 | 7.8 | 20.8 | 42.6 | 38.8 | 2.005 | 0
1128 | 2022-12-25 18:48 | 7.8 | 21.1 | 42.3 | 39 | 2 | 0
1129 | 2022-12-25 18:49 | 8 | 21.4 | 41.9 | 39.5 | 1.99 | 0
1130 | 2022-12-25 18:50 | 7.9 | 21.7 | 41.8 | 39.2 | 1.997 | 0
1131 | 2022-12-25 18:51 | 7.9 | 21.9 | 41.6 | 39.1 | 1.893 | 0
1132 | 2022-12-25 18:52 | 7.9 | 22 | 41.4 | 38.8 | 1.829 | 0
1133 | 2022-12-25 18:53 | 7.8 | 22 | 41.2 | 40.1 | 1.827 | 0
1134 | 2022-12-25 18:54 | 7.8 | 21.8 | 41.1 | 40 | 1.821 | 0
1135 | 2022-12-25 18:55 | 8 | 21.4 | 41.2 | 39.9 | 1.764 | 0
1136 | 2022-12-25 18:56 | 7.9 | 21.1 | 41.1 | 40 | 1.211 | 0
1137 | 2022-12-25 18:57 | 8.3 | 21.1 | 41.1 | 39.5 | 1.091 | 0
1138 | 2022-12-25 18:58 | 8.2 | 20.9 | 41 | 39.4 | 0.051 | 0
1139 | 2022-12-25 18:59 | 8 | 20.8 | 40.9 | 39.3 | 0 | 0
1140 | 2022-12-25 19:00 | 7.9 | 20.7 | 40.8 | 39.1 | 0 | 0
1141 | 2022-12-25 19:01 | 7.9 | 20.7 | 40.5 | 38.6 | 0 | 0
1142 | 2022-12-25 19:02 | 7.8 | 20.6 | 40.2 | 38.1 | 0 | 0
1143 | 2022-12-25 19:03 | 7.7 | 20.6 | 40 | 37.6 | 0 | 0
1144 | 2022-12-25 19:04 | 7.8 | 20.5 | 39.7 | 37.1 | 0 | 0
1145 | 2022-12-25 19:05 | 7.7 | 20.4 | 39.5 | 36.7 | 0.255 | 0
1146 | 2022-12-25 19:06 | 7.8 | 20.4 | 40.5 | 37.8 | 0.019 | 0
1147 | 2022-12-25 19:07 | 7.7 | 20.3 | 40.4 | 38.5 | 0.923 | 0
1148 | 2022-12-25 19:08 | 7.8 | 20.3 | 40.5 | 36.6 | 0.974 | 0
1149 | 2022-12-25 19:09 | 7.8 | 20.2 | 40.1 | 38.9 | 0.976 | 0
1150 | 2022-12-25 19:10 | 7.7 | 20.2 | 40.1 | 38.5 | 1.017 | 0
1151 | 2022-12-25 19:11 | 7.7 | 20.3 | 40 | 38.5 | 1.59 | 0
1152 | 2022-12-25 19:12 | 7.6 | 20.3 | 39.9 | 37.6 | 1.826 | 0
1153 | 2022-12-25 19:13 | 7.4 | 20.5 | 39.9 | 37.1 | 1.824 | 0
1154 | 2022-12-25 19:14 | 7.5 | 20.6 | 39.6 | 37.2 | 1.828 | 0
1155 | 2022-12-25 19:15 | 7.7 | 21 | 39.4 | 37 | 1.824 | 0
1156 | 2022-12-25 19:16 | 7.6 | 21.3 | 39.2 | 36.8 | 1.916 | 0
1157 | 2022-12-25 19:17 | 7.5 | 20.4 | 39 | 36.3 | 1.988 | 0
1158 | 2022-12-25 19:18 | 7.4 | 20.6 | 38.8 | 35.8 | 1.989 | 0
1159 | 2022-12-25 19:19 | 7.4 | 21.8 | 38.4 | 35.6 | 1.991 | 0
1160 | 2022-12-25 19:20 | 7.2 | 21.9 | 38.2 | 35.3 | 1.993 | 0
1161 | 2022-12-25 19:21 | 7.5 | 21.9 | 38 | 35.2 | 1.99 | 0
1162 | 2022-12-25 19:22 | 7.4 | 22 | 37.8 | 35 | 1.989 | 0
1163 | 2022-12-25 19:23 | 7.5 | 22 | 37.5 | 35.5 | 1.989 | 0
1164 | 2022-12-25 19:24 | 7.3 | 21.8 | 37.3 | 35.4 | 1.988 | 0
1165 | 2022-12-25 19:25 | 7.4 | 21.6 | 37.2 | 35.8 | 1.987 | 0
1166 | 2022-12-25 19:26 | 7.5 | 21.4 | 37.1 | 36 | 1.912 | 0
1167 | 2022-12-25 19:27 | 7.5 | 21.3 | 37 | 36 | 1.82 | 0
1168 | 2022-12-25 19:28 | 7.5 | 21.1 | 36.9 | 36.1 | 1.515 | 0
1169 | 2022-12-25 19:29 | 8.2 | 20.9 | 37 | 35.9 | 1.272 | 0
1170 | 2022-12-25 19:30 | 8.4 | 20.8 | 37.3 | 35.9 | 1.096 | 0
1171 | 2022-12-25 19:31 | 8.2 | 20.8 | 37.5 | 35.9 | 1.086 | 0
1172 | 2022-12-25 19:32 | 7.9 | 20.8 | 37.5 | 36.1 | 1.087 | 0
1173 | 2022-12-25 19:33 | 7.7 | 20.8 | 37.3 | 36 | 1.089 | 0
1174 | 2022-12-25 19:34 | 7.9 | 20.6 | 37.5 | 36 | 1.086 | 0
1175 | 2022-12-25 19:35 | 7.9 | 20.5 | 37.8 | 36.1 | 1.087 | 0
1176 | 2022-12-25 19:36 | 7.7 | 20.5 | 38.4 | 36.4 | 1.085 | 0
1177 | 2022-12-25 19:37 | 7.6 | 20.5 | 38.9 | 37 | 1.082 | 0
1178 | 2022-12-25 19:38 | 7.8 | 20.5 | 39.2 | 37.4 | 1.096 | 0
1179 | 2022-12-25 19:39 | 7.6 | 20.4 | 39.5 | 37.7 | 1.152 | 0
1180 | 2022-12-25 19:40 | 7.5 | 20.4 | 39.9 | 38 | 1.498 | 0
1181 | 2022-12-25 19:41 | 7.5 | 20.4 | 40.5 | 37.9 | 1.507 | 0
1182 | 2022-12-25 19:42 | 7.7 | 20.4 | 40.5 | 38.7 | 1.505 | 0
1183 | 2022-12-25 19:43 | 7.7 | 20.4 | 40.1 | 38.3 | 1.499 | 0
1184 | 2022-12-25 19:44 | 7.7 | 20.4 | 40.2 | 38.2 | 1.503 | 0
1185 | 2022-12-25 19:45 | 7.6 | 20.5 | 40.2 | 39 | 1.798 | 0
1186 | 2022-12-25 19:46 | 7.6 | 20.5 | 40.1 | 35.7 | 1.832 | 0
1187 | 2022-12-25 19:47 | 7.5 | 20.5 | 40 | 38 | 1.821 | 0
1188 | 2022-12-25 19:48 | 7.5 | 20.7 | 39.6 | 38 | 1.818 | 0
1189 | 2022-12-25 19:49 | 7.7 | 20.9 | 39.5 | 37.6 | 1.787 | 0
1190 | 2022-12-25 19:50 | 7.6 | 21.1 | 39.5 | 37.6 | 1.664 | 0
1191 | 2022-12-25 19:51 | 7.7 | 21.3 | 39.3 | 37.4 | 1.8 | 0
1192 | 2022-12-25 19:52 | 7.7 | 21.4 | 39.2 | 34.2 | 1.855 | 0
1193 | 2022-12-25 19:53 | 7.7 | 21.5 | 39 | 36.4 | 1.848 | 0
1194 | 2022-12-25 19:54 | 7.6 | 21.5 | 38.6 | 36.3 | 1.847 | 0
1195 | 2022-12-25 19:55 | 7.9 | 21.6 | 38.5 | 35.9 | 1.852 | 0
1196 | 2022-12-25 19:56 | 7.8 | 21.8 | 38.3 | 35.8 | 1.848 | 0
1197 | 2022-12-25 19:57 | 7.9 | 21.9 | 38.1 | 35.6 | 1.856 | 0
1198 | 2022-12-25 19:58 | 7.8 | 21.9 | 37.9 | 36.5 | 0 | 0
1199 | 2022-12-25 19:59 | 7.9 | 21.8 | 37.8 | 36.6 | 0 | 0
1200 | 2022-12-25 20:00 | 7.9 | 21.6 | 37.6 | 36.1 | 1.808 | 0
1201 | 2022-12-25 20:01 | 7.7 | 21.3 | 37.7 | 36.4 | 1.256 | 0
1202 | 2022-12-25 20:02 | 7.9 | 21.1 | 37.5 | 37.2 | 1.06 | 0
1203 | 2022-12-25 20:03 | 7.6 | 20.9 | 37.6 | 35 | 1.09 | 0
1204 | 2022-12-25 20:04 | 7.7 | 20.7 | 37.7 | 36.2 | 1.081 | 0
1205 | 2022-12-25 20:05 | 7.7 | 20.6 | 38.1 | 36.3 | 1.084 | 0
1206 | 2022-12-25 20:06 | 7.6 | 20.6 | 38.6 | 36.7 | 1.082 | 0
1207 | 2022-12-25 20:07 | 8.2 | 20.5 | 39 | 37.1 | 1.085 | 0
1208 | 2022-12-25 20:08 | 10 | 20.5 | 39.3 | 37.5 | 1.085 | 0
1209 | 2022-12-25 20:09 | 10.2 | 20.5 | 39.6 | 37.8 | 1.083 | 0
1210 | 2022-12-25 20:10 | 9.8 | 20.5 | 40 | 38 | 1.087 | 0
1211 | 2022-12-25 20:11 | 9.5 | 20.5 | 40.5 | 38.4 | 1.431 | 0
1212 | 2022-12-25 20:12 | 8.9 | 20.4 | 40.9 | 38 | 1.501 | 0
1213 | 2022-12-25 20:13 | 8.3 | 20.4 | 41.3 | 38.8 | 1.507 | 0
1214 | 2022-12-25 20:14 | 8.3 | 20.4 | 41.7 | 39.2 | 1.505 | 0
1215 | 2022-12-25 20:15 | 8.3 | 20.4 | 42 | 39.6 | 1.508 | 0
1216 | 2022-12-25 20:16 | 9.4 | 20.4 | 41.9 | 40 | 1.513 | 0
1217 | 2022-12-25 20:17 | 9.9 | 20.4 | 41.6 | 39.6 | 1.507 | 0
1218 | 2022-12-25 20:18 | 11 | 20.6 | 41.6 | 39 | 1.83 | 0
1219 | 2022-12-25 20:19 | 10.6 | 20.6 | 41.6 | 38.5 | 1.825 | 0
1220 | 2022-12-25 20:20 | 10.2 | 20.7 | 41.3 | 38.7 | 1.826 | 0
1221 | 2022-12-25 20:21 | 10.1 | 21 | 41 | 38.4 | 1.833 | 0
1222 | 2022-12-25 20:22 | 9.9 | 21.3 | 40.8 | 38.2 | 1.828 | 0
1223 | 2022-12-25 20:23 | 10.5 | 21.5 | 40.6 | 38 | 1.828 | 0
1224 | 2022-12-25 20:24 | 11.5 | 21.7 | 40.4 | 37.8 | 1.822 | 0
1225 | 2022-12-25 20:25 | 11.7 | 21.9 | 40.1 | 37.7 | 1.83 | 0
1226 | 2022-12-25 20:26 | 11.4 | 21.9 | 40 | 38.1 | 1.829 | 0
1227 | 2022-12-25 20:27 | 11.4 | 22 | 39.9 | 38.6 | 0 | 0
1228 | 2022-12-25 20:28 | 10.6 | 21.9 | 39.9 | 38.5 | 0 | 0
1229 | 2022-12-25 20:29 | 10 | 21.7 | 39.7 | 38.1 | 0 | 0
1230 | 2022-12-25 20:30 | 9.6 | 21.4 | 39.4 | 37.6 | 0 | 0
1231 | 2022-12-25 20:31 | 9.3 | 21.2 | 39.2 | 37.1 | 0 | 0
1232 | 2022-12-25 20:32 | 9 | 20.9 | 38.9 | 36.6 | 0 | 0
1233 | 2022-12-25 20:33 | 8.9 | 20.7 | 38.7 | 36.2 | 0 | 0
1234 | 2022-12-25 20:34 | 8.7 | 20.6 | 38.4 | 35.7 | 0.158 | 0
1235 | 2022-12-25 20:35 | 9.1 | 20.4 | 38.2 | 37 | 0 | 0
1236 | 2022-12-25 20:36 | 9.6 | 20.4 | 38 | 37.2 | 0 | 0
1237 | 2022-12-25 20:37 | 9.2 | 20.3 | 37.7 | 37.8 | 0.859 | 0
1238 | 2022-12-25 20:38 | 9 | 20.3 | 41.3 | 34.6 | 0.977 | 0
1239 | 2022-12-25 20:39 | 8.9 | 20.3 | 41.5 | 38.8 | 1.607 | 0
1240 | 2022-12-25 20:40 | 8.7 | 20.3 | 42 | 36.3 | 1.636 | 0
1241 | 2022-12-25 20:41 | 8.7 | 20.3 | 42.1 | 39.4 | 1.832 | 0
1242 | 2022-12-25 20:42 | 8.8 | 20.4 | 42.6 | 38.8 | 1.842 | 0
1243 | 2022-12-25 20:43 | 8.6 | 20.5 | 42.7 | 39.8 | 1.845 | 0
1244 | 2022-12-25 20:44 | 8.2 | 20.7 | 42.3 | 39.6 | 1.999 | 0
1245 | 2022-12-25 20:45 | 8.4 | 20.9 | 42.3 | 38.8 | 2.006 | 0
1246 | 2022-12-25 20:46 | 8.1 | 21 | 42.1 | 39.5 | 2.009 | 0
1247 | 2022-12-25 20:47 | 8.2 | 21.2 | 41.7 | 39.3 | 1.926 | 0
1248 | 2022-12-25 20:48 | 7.9 | 21.5 | 41.6 | 38.8 | 1.828 | 0
1249 | 2022-12-25 20:49 | 8.1 | 21.7 | 41.5 | 38.7 | 1.823 | 0
1250 | 2022-12-25 20:50 | 8 | 21.8 | 41.2 | 38.6 | 1.831 | 0
1251 | 2022-12-25 20:51 | 7.9 | 22 | 41.1 | 38.4 | 1.825 | 0
1252 | 2022-12-25 20:52 | 8.2 | 22.1 | 40.8 | 38.9 | 1.836 | 0
1253 | 2022-12-25 20:53 | 8.6 | 21.9 | 40.7 | 39 | 1.835 | 0
1254 | 2022-12-25 20:54 | 8.2 | 21.6 | 40.6 | 38.9 | 1.827 | 0
1255 | 2022-12-25 20:55 | 8 | 21.3 | 40.5 | 38.8 | 1.695 | 0
1256 | 2022-12-25 20:56 | 8.1 | 21.1 | 40.4 | 38.6 | 1.506 | 0
1257 | 2022-12-25 20:57 | 8 | 21 | 40.3 | 39.1 | 0 | 0
1258 | 2022-12-25 20:58 | 7.9 | 20.9 | 40.2 | 38.9 | 0 | 0
1259 | 2022-12-25 20:59 | 8.1 | 20.8 | 39.9 | 38.4 | 0 | 0
1260 | 2022-12-25 21:00 | 8 | 20.7 | 39.7 | 37.9 | 0 | 0
1261 | 2022-12-25 21:01 | 7.8 | 20.6 | 39.4 | 37.3 | 0 | 0
1262 | 2022-12-25 21:02 | 9.1 | 20.5 | 39.2 | 36.8 | 0 | 0
1263 | 2022-12-25 21:03 | 9.3 | 20.4 | 38.9 | 36.3 | 0 | 0
1264 | 2022-12-25 21:04 | 9.6 | 20.4 | 38.7 | 35.9 | 0 | 0
1265 | 2022-12-25 21:05 | 9.2 | 20.4 | 38.4 | 35.4 | 0 | 0
1266 | 2022-12-25 21:06 | 8.9 | 20.3 | 38.2 | 35 | 0 | 0
1267 | 2022-12-25 21:07 | 8.8 | 20.2 | 37.9 | 34.6 | 0 | 0
1268 | 2022-12-25 21:08 | 8.6 | 20.2 | 37.7 | 34.2 | 0 | 0
1269 | 2022-12-25 21:09 | 8.3 | 20.2 | 37.5 | 33.8 | 0 | 0
1270 | 2022-12-25 21:10 | 8.4 | 20.1 | 37.2 | 33.5 | 0 | 0
1271 | 2022-12-25 21:11 | 8.4 | 20.1 | 37 | 33.1 | 0 | 0
1272 | 2022-12-25 21:12 | 8.3 | 20.1 | 36.7 | 32.8 | 0 | 0
1273 | 2022-12-25 21:13 | 8 | 20 | 36.5 | 32.5 | 0 | 0
1274 | 2022-12-25 21:14 | 8.1 | 20 | 36.3 | 32.2 | 0 | 0
1275 | 2022-12-25 21:15 | 8.2 | 20 | 36 | 31.8 | 0 | 0
1276 | 2022-12-25 21:16 | 8.1 | 20 | 35.8 | 31.6 | 0 | 0
1277 | 2022-12-25 21:17 | 8.1 | 20 | 35.6 | 31.3 | 0 | 0
1278 | 2022-12-25 21:18 | 8 | 20 | 35.4 | 31 | 0 | 0
1279 | 2022-12-25 21:19 | 8 | 20 | 35.1 | 30.7 | 0 | 0
1280 | 2022-12-25 21:20 | 8.2 | 19.9 | 34.9 | 30.4 | 0 | 0
1281 | 2022-12-25 21:21 | 8.3 | 20 | 34.7 | 30.2 | 0 | 0
1282 | 2022-12-25 21:22 | 9.9 | 19.9 | 34.4 | 29.9 | 0 | 0
1283 | 2022-12-25 21:23 | 10.5 | 19.9 | 34.2 | 29.6 | 0 | 0
1284 | 2022-12-25 21:24 | 9.3 | 19.9 | 34 | 29.4 | 0 | 0
1285 | 2022-12-25 21:25 | 9.2 | 19.9 | 33.8 | 29.1 | 0 | 0
1286 | 2022-12-25 21:26 | 9 | 19.9 | 33.6 | 28.9 | 0 | 0
1287 | 2022-12-25 21:27 | 8.7 | 19.9 | 33.4 | 28.7 | 0 | 0
1288 | 2022-12-25 21:28 | 8.6 | 19.9 | 33.2 | 28.5 | 0 | 0
1289 | 2022-12-25 21:29 | 8.8 | 19.9 | 33 | 28.2 | 0 | 0
1290 | 2022-12-25 21:30 | 8.3 | 19.9 | 32.8 | 28 | 0 | 0
1291 | 2022-12-25 21:31 | 8.1 | 19.8 | 32.6 | 27.8 | 0 | 0
1292 | 2022-12-25 21:32 | 8 | 19.8 | 32.3 | 27.6 | 0 | 0
1293 | 2022-12-25 21:33 | 7.9 | 19.9 | 32.2 | 27.4 | 0 | 0
1294 | 2022-12-25 21:34 | 7.6 | 19.9 | 31.9 | 27.2 | 0 | 0
1295 | 2022-12-25 21:35 | 7.6 | 19.8 | 31.8 | 27 | 0 | 0
1296 | 2022-12-25 21:36 | 7.7 | 19.8 | 31.6 | 26.8 | 0 | 0
1297 | 2022-12-25 21:37 | 7.8 | 19.8 | 31.4 | 26.6 | 0 | 0
1298 | 2022-12-25 21:38 | 7.6 | 19.8 | 31.2 | 26.5 | 0 | 0
1299 | 2022-12-25 21:39 | 7.7 | 19.8 | 31 | 26.3 | 0 | 0
1300 | 2022-12-25 21:40 | 7.6 | 19.7 | 30.8 | 26.1 | 0 | 0
1301 | 2022-12-25 21:41 | 7.4 | 19.8 | 30.6 | 25.9 | 0 | 0
1302 | 2022-12-25 21:42 | 7.7 | 19.7 | 30.4 | 25.7 | 0 | 0
1303 | 2022-12-25 21:43 | 7.4 | 19.8 | 30.2 | 25.5 | 0 | 0
1304 | 2022-12-25 21:44 | 7.3 | 19.8 | 30 | 25.4 | 0 | 0
1305 | 2022-12-25 21:45 | 7.4 | 19.7 | 29.9 | 25.2 | 0 | 0
1306 | 2022-12-25 21:46 | 7.5 | 19.8 | 29.7 | 25 | 0 | 0
1307 | 2022-12-25 21:47 | 7.5 | 19.8 | 29.5 | 24.8 | 0 | 0
1308 | 2022-12-25 21:48 | 7.7 | 19.6 | 29.3 | 24.6 | 0 | 0
1309 | 2022-12-25 21:49 | 7.4 | 19.7 | 29.1 | 24.5 | 0 | 0
1310 | 2022-12-25 21:50 | 7.5 | 19.6 | 28.9 | 24.3 | 0 | 0
1311 | 2022-12-25 21:51 | 7.3 | 19.7 | 28.8 | 24.2 | 0 | 0
1312 | 2022-12-25 21:52 | 7 | 19.6 | 28.6 | 24 | 0 | 0
1313 | 2022-12-25 21:53 | 7.4 | 19.6 | 28.4 | 23.8 | 0 | 0
1314 | 2022-12-25 21:54 | 7.5 | 19.6 | 28.2 | 23.7 | 0 | 0
1315 | 2022-12-25 21:55 | 7.3 | 19.6 | 28.1 | 23.5 | 0 | 0
1316 | 2022-12-25 21:56 | 7.4 | 19.6 | 27.9 | 23.4 | 0 | 0
1317 | 2022-12-25 21:57 | 7.2 | 19.6 | 27.7 | 23.3 | 0 | 0
1318 | 2022-12-25 21:58 | 7.4 | 19.7 | 27.5 | 23.1 | 0 | 0
1319 | 2022-12-25 21:59 | 7.6 | 19.6 | 27.4 | 23 | 0 | 0
1320 | 2022-12-25 22:00 | 7.6 | 19.6 | 27.2 | 22.8 | 0 | 0
1321 | 2022-12-25 22:01 | 7.7 | 19.5 | 27.1 | 22.7 | 0 | 0
1322 | 2022-12-25 22:02 | 7.4 | 19.5 | 26.9 | 22.6 | 0 | 0
1323 | 2022-12-25 22:03 | 7.3 | 19.5 | 26.7 | 22.5 | 0 | 0
1324 | 2022-12-25 22:04 | 7.1 | 19.5 | 26.6 | 22.3 | 0 | 0
1325 | 2022-12-25 22:05 | 7.2 | 19.5 | 26.4 | 22.2 | 0 | 0
1326 | 2022-12-25 22:06 | 7.4 | 19.5 | 26.2 | 22.1 | 0 | 0
1327 | 2022-12-25 22:07 | 7.7 | 19.5 | 26.1 | 21.9 | 0 | 0
1328 | 2022-12-25 22:08 | 7.4 | 19.5 | 25.9 | 21.8 | 0 | 0
1329 | 2022-12-25 22:09 | 7.4 | 19.5 | 25.8 | 21.7 | 0 | 0
1330 | 2022-12-25 22:10 | 7.2 | 19.5 | 25.6 | 21.5 | 0 | 0
1331 | 2022-12-25 22:11 | 7.1 | 19.5 | 25.5 | 21.4 | 0 | 0
1332 | 2022-12-25 22:12 | 7.2 | 19.5 | 25.3 | 21.3 | 0 | 0
1333 | 2022-12-25 22:13 | 7 | 19.5 | 25.2 | 21.2 | 0 | 0
1334 | 2022-12-25 22:14 | 7.3 | 19.5 | 25 | 21.1 | 0 | 0
1335 | 2022-12-25 22:15 | 7 | 19.5 | 24.9 | 20.9 | 0 | 0
1336 | 2022-12-25 22:16 | 7.2 | 19.5 | 24.8 | 20.8 | 0 | 0
1337 | 2022-12-25 22:17 | 7.2 | 19.5 | 24.6 | 20.7 | 0 | 0
1338 | 2022-12-25 22:18 | 7.3 | 19.4 | 24.5 | 20.6 | 0 | 0
1339 | 2022-12-25 22:19 | 7.2 | 19.4 | 24.3 | 20.5 | 0 | 0
1340 | 2022-12-25 22:20 | 7.2 | 19.4 | 24.2 | 20.4 | 0 | 0
1341 | 2022-12-25 22:21 | 7.3 | 19.5 | 24 | 20.3 | 0 | 0
1342 | 2022-12-25 22:22 | 7.1 | 19.4 | 23.9 | 20.1 | 0 | 0
1343 | 2022-12-25 22:23 | 7.3 | 19.5 | 23.8 | 20 | 0 | 0
1344 | 2022-12-25 22:24 | 7.2 | 19.5 | 23.6 | 19.9 | 0 | 0
1345 | 2022-12-25 22:25 | 7.2 | 19.5 | 23.5 | 19.8 | 0 | 0
1346 | 2022-12-25 22:26 | 7 | 19.4 | 23.4 | 19.7 | 0 | 0
1347 | 2022-12-25 22:27 | 7 | 19.5 | 23.2 | 19.6 | 0 | 0
1348 | 2022-12-25 22:28 | 7.1 | 19.4 | 23.1 | 19.5 | 0 | 0
1349 | 2022-12-25 22:29 | 7.1 | 19.4 | 23 | 19.4 | 0 | 0
1350 | 2022-12-25 22:30 | 6.9 | 19.5 | 22.9 | 19.3 | 0 | 0
1351 | 2022-12-25 22:31 | 6.9 | 19.5 | 22.7 | 19.2 | 0 | 0
1352 | 2022-12-25 22:32 | 7.1 | 19.4 | 22.6 | 19.1 | 0 | 0
1353 | 2022-12-25 22:33 | 7.1 | 19.3 | 22.5 | 19 | 0 | 0
1354 | 2022-12-25 22:34 | 7.1 | 19.3 | 22.3 | 18.9 | 0 | 0
1355 | 2022-12-25 22:35 | 6.9 | 19.4 | 22.2 | 18.9 | 0 | 0
1356 | 2022-12-25 22:36 | 6.9 | 19.3 | 22.1 | 18.8 | 0 | 0
1357 | 2022-12-25 22:37 | 7.1 | 19.4 | 22 | 18.7 | 0 | 0
1358 | 2022-12-25 22:38 | 7 | 19.4 | 21.9 | 18.6 | 0 | 0
1359 | 2022-12-25 22:39 | 7.1 | 19.3 | 21.8 | 18.5 | 0 | 0
1360 | 2022-12-25 22:40 | 7 | 19.3 | 21.7 | 18.4 | 0 | 0
1361 | 2022-12-25 22:41 | 7.1 | 19.3 | 21.6 | 18.3 | 0 | 0
1362 | 2022-12-25 22:42 | 6.9 | 19.4 | 21.4 | 18.3 | 0 | 0
1363 | 2022-12-25 22:43 | 7 | 19.4 | 21.3 | 18.2 | 0 | 0
1364 | 2022-12-25 22:44 | 6.8 | 19.3 | 21.2 | 18.1 | 0 | 0
1365 | 2022-12-25 22:45 | 6.8 | 19.4 | 21.1 | 18 | 0 | 0
1366 | 2022-12-25 22:46 | 6.8 | 19.3 | 21 | 17.9 | 0 | 0
1367 | 2022-12-25 22:47 | 6.8 | 19.3 | 20.9 | 17.9 | 0 | 0
1368 | 2022-12-25 22:48 | 7 | 19.3 | 20.8 | 17.8 | 0 | 0
1369 | 2022-12-25 22:49 | 6.9 | 19.3 | 20.7 | 17.7 | 0 | 0
1370 | 2022-12-25 22:50 | 6.8 | 19.3 | 20.6 | 17.6 | 0 | 0
1371 | 2022-12-25 22:51 | 6.7 | 19.3 | 20.5 | 17.6 | 0 | 0
1372 | 2022-12-25 22:52 | 6.8 | 19.3 | 20.4 | 17.5 | 0 | 0
1373 | 2022-12-25 22:53 | 7 | 19.3 | 20.3 | 17.4 | 0 | 0
1374 | 2022-12-25 22:54 | 7.1 | 19.3 | 20.3 | 17.3 | 0 | 0
1375 | 2022-12-25 22:55 | 6.9 | 19.3 | 20.2 | 17.2 | 0 | 0
1376 | 2022-12-25 22:56 | 6.8 | 19.3 | 20.1 | 17.2 | 0 | 0
1377 | 2022-12-25 22:57 | 6.7 | 19.3 | 20 | 17.1 | 0 | 0
1378 | 2022-12-25 22:58 | 6.6 | 19.2 | 19.9 | 17 | 0 | 0
1379 | 2022-12-25 22:59 | 6.6 | 19.2 | 19.8 | 17 | 0 | 0
1380 | 2022-12-25 23:00 | 6.8 | 19.2 | 19.7 | 16.9 | 0 | 0
1381 | 2022-12-25 23:01 | 6.7 | 19.3 | 19.6 | 16.8 | 0 | 0
1382 | 2022-12-25 23:02 | 6.6 | 19.2 | 19.6 | 16.7 | 0 | 0
1383 | 2022-12-25 23:03 | 6.9 | 19.2 | 19.4 | 16.7 | 0 | 0
1384 | 2022-12-25 23:04 | 7 | 19.2 | 19.4 | 16.6 | 0 | 0
1385 | 2022-12-25 23:05 | 6.9 | 19.2 | 19.3 | 16.5 | 0 | 0
1386 | 2022-12-25 23:06 | 6.7 | 19.2 | 19.2 | 16.4 | 0 | 0
1387 | 2022-12-25 23:07 | 6.9 | 19.2 | 19.1 | 16.4 | 0 | 0
1388 | 2022-12-25 23:08 | 7 | 19.3 | 19 | 16.3 | 0 | 0
1389 | 2022-12-25 23:09 | 6.8 | 19.2 | 18.9 | 16.2 | 0 | 0
1390 | 2022-12-25 23:10 | 6.7 | 19.1 | 18.9 | 16.2 | 0 | 0
1391 | 2022-12-25 23:11 | 6.8 | 19.2 | 18.8 | 16.1 | 0 | 0
1392 | 2022-12-25 23:12 | 6.7 | 19.1 | 18.7 | 16 | 0 | 0
1393 | 2022-12-25 23:13 | 6.9 | 19.1 | 18.7 | 16 | 0 | 0
1394 | 2022-12-25 23:14 | 6.7 | 19.1 | 18.6 | 15.9 | 0 | 0
1395 | 2022-12-25 23:15 | 6.6 | 19.2 | 18.5 | 15.9 | 0 | 0
1396 | 2022-12-25 23:16 | 6.8 | 19.1 | 18.5 | 15.8 | 0 | 0
1397 | 2022-12-25 23:17 | 6.8 | 19.1 | 18.4 | 15.7 | 0 | 0
1398 | 2022-12-25 23:18 | 6.9 | 19.1 | 18.4 | 15.7 | 0 | 0
1399 | 2022-12-25 23:19 | 6.8 | 19.1 | 18.3 | 15.6 | 0 | 0
1400 | 2022-12-25 23:20 | 6.6 | 19.1 | 18.3 | 15.6 | 0 | 0
1401 | 2022-12-25 23:21 | 6.6 | 19.1 | 18.2 | 15.5 | 0 | 0
1402 | 2022-12-25 23:22 | 6.7 | 19.1 | 18.1 | 15.4 | 0 | 0
1403 | 2022-12-25 23:23 | 6.9 | 19.1 | 18.1 | 15.4 | 0 | 0
1404 | 2022-12-25 23:24 | 6.7 | 19.2 | 18 | 15.3 | 0 | 0
1405 | 2022-12-25 23:25 | 6.6 | 19.1 | 17.9 | 15.3 | 0 | 0
1406 | 2022-12-25 23:26 | 6.9 | 19.1 | 17.9 | 15.2 | 0 | 0
1407 | 2022-12-25 23:27 | 6.9 | 19.1 | 17.8 | 15.2 | 0 | 0
1408 | 2022-12-25 23:28 | 6.8 | 19.1 | 17.8 | 15.1 | 0 | 0
1409 | 2022-12-25 23:29 | 6.8 | 19.1 | 17.7 | 15.1 | 0 | 0
1410 | 2022-12-25 23:30 | 6.7 | 19.1 | 17.6 | 15 | 0 | 0
1411 | 2022-12-25 23:31 | 6.7 | 19 | 17.6 | 15 | 0 | 0
1412 | 2022-12-25 23:32 | 6.8 | 19.1 | 17.5 | 14.9 | 0 | 0
1413 | 2022-12-25 23:33 | 6.7 | 19.1 | 17.5 | 14.9 | 0 | 0
1414 | 2022-12-25 23:34 | 6.9 | 19.1 | 17.4 | 14.8 | 0 | 0
1415 | 2022-12-25 23:35 | 7 | 19.2 | 17.4 | 14.7 | 0 | 0
1416 | 2022-12-25 23:36 | 6.9 | 19.1 | 17.3 | 14.7 | 0 | 0
1417 | 2022-12-25 23:37 | 6.7 | 19.1 | 17.3 | 14.6 | 0 | 0
1418 | 2022-12-25 23:38 | 6.8 | 19.1 | 17.2 | 14.6 | 0 | 0
1419 | 2022-12-25 23:39 | 6.8 | 19 | 17.2 | 14.6 | 0 | 0
1420 | 2022-12-25 23:40 | 6.8 | 19.1 | 17.1 | 14.5 | 0 | 0
1421 | 2022-12-25 23:41 | 6.9 | 19.1 | 17.1 | 14.5 | 0 | 0
1422 | 2022-12-25 23:42 | 6.9 | 19.1 | 17 | 14.4 | 0 | 0
1423 | 2022-12-25 23:43 | 6.7 | 19.1 | 17 | 14.4 | 0 | 0
1424 | 2022-12-25 23:44 | 6.8 | 19.1 | 16.9 | 14.3 | 0 | 0
1425 | 2022-12-25 23:45 | 6.6 | 19 | 16.9 | 14.3 | 0 | 0
1426 | 2022-12-25 23:46 | 6.7 | 19 | 16.8 | 14.3 | 0 | 0
1427 | 2022-12-25 23:47 | 6.7 | 19 | 16.8 | 14.2 | 0 | 0
1428 | 2022-12-25 23:48 | 6.6 | 19 | 16.8 | 14.2 | 0 | 0
1429 | 2022-12-25 23:49 | 6.6 | 19 | 16.7 | 14.1 | 0 | 0
1430 | 2022-12-25 23:50 | 6.6 | 19 | 16.7 | 14.1 | 0 | 0
1431 | 2022-12-25 23:51 | 6.7 | 19 | 16.6 | 14 | 0 | 0
1432 | 2022-12-25 23:52 | 6.9 | 19 | 16.6 | 14 | 0 | 0
1433 | 2022-12-25 23:53 | 6.8 | 19 | 16.6 | 14 | 0 | 0
1434 | 2022-12-25 23:54 | 6.8 | 19 | 16.6 | 13.9 | 0 | 0
1435 | 2022-12-25 23:55 | 6.7 | 19 | 16.5 | 13.9 | 0 | 0
1436 | 2022-12-25 23:56 | 6.7 | 19 | 16.5 | 13.8 | 0 | 0
1437 | 2022-12-25 23:57 | 6.7 | 19 | 16.4 | 13.8 | 0 | 0
1438 | 2022-12-25 23:58 | 6.5 | 19 | 16.4 | 13.8 | 0 | 0
1439 | 2022-12-25 23:59 | 6.5 | 19 | 16.4 | 13.7 | 0 | 0

## 26-12-2022_WITH HEAT
| Date&time_x | OUTDOOR_TEMP | INDOOR_TEMP | SH_INLET | SH_RETURN | FLOW_FAN_COILS_INDOOR | PYRANOMETER
0 | 2022-12-26 | 6.7 | 19 | 16.3 | 13.7 | 0 | 0
1 | 2022-12-26 00:01 | 6.6 | 19 | 16.3 | 13.7 | 0 | 0
2 | 2022-12-26 00:02 | 6.5 | 19 | 16.3 | 13.6 | 0 | 0
3 | 2022-12-26 00:03 | 6.5 | 19 | 16.3 | 13.6 | 0 | 0
4 | 2022-12-26 00:04 | 6.5 | 19 | 16.2 | 13.5 | 0 | 0
5 | 2022-12-26 00:05 | 6.6 | 19 | 16.2 | 13.5 | 0 | 0
6 | 2022-12-26 00:06 | 6.5 | 19 | 16.1 | 13.5 | 0 | 0
7 | 2022-12-26 00:07 | 6.7 | 18.9 | 16.1 | 13.4 | 0 | 0
8 | 2022-12-26 00:08 | 6.6 | 18.9 | 16 | 13.4 | 0 | 0
9 | 2022-12-26 00:09 | 6.6 | 18.9 | 16 | 13.4 | 0 | 0
10 | 2022-12-26 00:10 | 6.5 | 18.9 | 16 | 13.3 | 0 | 0
11 | 2022-12-26 00:11 | 6.6 | 18.9 | 16 | 13.3 | 0 | 0
12 | 2022-12-26 00:12 | 6.6 | 19 | 15.9 | 13.3 | 0 | 0
13 | 2022-12-26 00:13 | 6.6 | 18.9 | 15.9 | 13.2 | 0 | 0
14 | 2022-12-26 00:14 | 6.5 | 18.9 | 15.9 | 13.2 | 0 | 0
15 | 2022-12-26 00:15 | 6.6 | 19 | 15.8 | 13.2 | 0 | 0
16 | 2022-12-26 00:16 | 6.5 | 18.9 | 15.8 | 13.1 | 0 | 0
17 | 2022-12-26 00:17 | 6.5 | 18.9 | 15.8 | 13.1 | 0 | 0
18 | 2022-12-26 00:18 | 6.4 | 18.9 | 15.7 | 13.1 | 0 | 0
19 | 2022-12-26 00:19 | 6.5 | 18.9 | 15.7 | 13 | 0 | 0
20 | 2022-12-26 00:20 | 6.5 | 18.9 | 15.7 | 13 | 0 | 0
21 | 2022-12-26 00:21 | 6.4 | 18.9 | 15.6 | 13 | 0 | 0
22 | 2022-12-26 00:22 | 6.6 | 18.9 | 15.6 | 12.9 | 0 | 0
23 | 2022-12-26 00:23 | 6.8 | 18.8 | 15.6 | 12.9 | 0 | 0
24 | 2022-12-26 00:24 | 6.5 | 18.9 | 15.5 | 12.9 | 0 | 0
25 | 2022-12-26 00:25 | 6.6 | 18.9 | 15.5 | 12.8 | 0 | 0
26 | 2022-12-26 00:26 | 6.6 | 18.9 | 15.5 | 12.8 | 0 | 0
27 | 2022-12-26 00:27 | 6.4 | 18.8 | 15.4 | 12.8 | 0 | 0
28 | 2022-12-26 00:28 | 6.7 | 18.9 | 15.4 | 12.7 | 0 | 0
29 | 2022-12-26 00:29 | 6.6 | 18.9 | 15.4 | 12.7 | 0 | 0
30 | 2022-12-26 00:30 | 6.4 | 18.8 | 15.3 | 12.7 | 0 | 0
31 | 2022-12-26 00:31 | 6.7 | 18.8 | 15.3 | 12.7 | 0 | 0
32 | 2022-12-26 00:32 | 6.7 | 18.8 | 15.3 | 12.6 | 0 | 0
33 | 2022-12-26 00:33 | 6.6 | 18.8 | 15.2 | 12.6 | 0 | 0
34 | 2022-12-26 00:34 | 6.4 | 18.8 | 15.2 | 12.6 | 0 | 0
35 | 2022-12-26 00:35 | 6.5 | 18.8 | 15.2 | 12.5 | 0 | 0
36 | 2022-12-26 00:36 | 6.7 | 18.8 | 15.1 | 12.5 | 0 | 0
37 | 2022-12-26 00:37 | 6.5 | 18.8 | 15.1 | 12.5 | 0 | 0
38 | 2022-12-26 00:38 | 6.6 | 18.9 | 15.1 | 12.5 | 0 | 0
39 | 2022-12-26 00:39 | 6.7 | 18.9 | 15.1 | 12.4 | 0 | 0
40 | 2022-12-26 00:40 | 6.5 | 18.8 | 15.1 | 12.4 | 0 | 0
41 | 2022-12-26 00:41 | 6.5 | 18.8 | 15 | 12.4 | 0 | 0
42 | 2022-12-26 00:42 | 6.6 | 18.8 | 15 | 12.4 | 0 | 0
43 | 2022-12-26 00:43 | 6.6 | 18.8 | 15 | 12.3 | 0 | 0
44 | 2022-12-26 00:44 | 6.6 | 18.8 | 15 | 12.3 | 0 | 0
45 | 2022-12-26 00:45 | 6.6 | 18.8 | 15 | 12.3 | 0 | 0
46 | 2022-12-26 00:46 | 6.6 | 18.8 | 14.9 | 12.3 | 0 | 0
47 | 2022-12-26 00:47 | 6.5 | 18.8 | 14.9 | 12.2 | 0 | 0
48 | 2022-12-26 00:48 | 6.6 | 18.8 | 14.9 | 12.2 | 0 | 0
49 | 2022-12-26 00:49 | 6.4 | 18.8 | 14.9 | 12.2 | 0 | 0
50 | 2022-12-26 00:50 | 6.3 | 18.8 | 14.8 | 12.1 | 0 | 0
51 | 2022-12-26 00:51 | 6.3 | 18.7 | 14.8 | 12.1 | 0 | 0
52 | 2022-12-26 00:52 | 6.4 | 18.8 | 14.8 | 12.1 | 0 | 0
53 | 2022-12-26 00:53 | 6.2 | 18.7 | 14.8 | 12.1 | 0 | 0
54 | 2022-12-26 00:54 | 6.2 | 18.8 | 14.8 | 12.1 | 0 | 0
55 | 2022-12-26 00:55 | 6.2 | 18.8 | 14.8 | 12 | 0 | 0
56 | 2022-12-26 00:56 | 6.3 | 18.8 | 14.7 | 12 | 0 | 0
57 | 2022-12-26 00:57 | 6.1 | 18.8 | 14.7 | 12 | 0 | 0
58 | 2022-12-26 00:58 | 6.2 | 18.7 | 14.7 | 11.9 | 0 | 0
59 | 2022-12-26 00:59 | 6.2 | 18.8 | 14.6 | 11.9 | 0 | 0
60 | 2022-12-26 01:00 | 6.2 | 18.7 | 14.6 | 11.9 | 0 | 0
61 | 2022-12-26 01:01 | 6.2 | 18.7 | 14.6 | 11.9 | 0 | 0
62 | 2022-12-26 01:02 | 6.1 | 18.7 | 14.6 | 11.9 | 0 | 0
63 | 2022-12-26 01:03 | 6.1 | 18.7 | 14.6 | 11.8 | 0 | 0
64 | 2022-12-26 01:04 | 6.1 | 18.7 | 14.5 | 11.8 | 0 | 0
65 | 2022-12-26 01:05 | 6 | 18.7 | 14.5 | 11.8 | 0 | 0
66 | 2022-12-26 01:06 | 6 | 18.7 | 14.5 | 11.8 | 0 | 0
67 | 2022-12-26 01:07 | 6.1 | 18.7 | 14.5 | 11.7 | 0 | 0
68 | 2022-12-26 01:08 | 6 | 18.7 | 14.4 | 11.7 | 0 | 0
69 | 2022-12-26 01:09 | 6.1 | 18.7 | 14.4 | 11.7 | 0 | 0
70 | 2022-12-26 01:10 | 5.9 | 18.7 | 14.4 | 11.7 | 0 | 0
71 | 2022-12-26 01:11 | 5.9 | 18.7 | 14.4 | 11.7 | 0.086 | 0
72 | 2022-12-26 01:12 | 5.8 | 18.7 | 14.4 | 12.3 | 0 | 0
73 | 2022-12-26 01:13 | 5.9 | 18.7 | 14.3 | 12.3 | 0 | 0
74 | 2022-12-26 01:14 | 6 | 18.7 | 14.3 | 12.3 | 0.765 | 0
75 | 2022-12-26 01:15 | 6.1 | 18.6 | 40.8 | 16.7 | 0.92 | 0
76 | 2022-12-26 01:16 | 6 | 18.6 | 41.6 | 37.5 | 0.949 | 0
77 | 2022-12-26 01:17 | 6.2 | 18.6 | 40.8 | 38.1 | 0.982 | 0
78 | 2022-12-26 01:18 | 6.1 | 18.7 | 40.4 | 37.9 | 0.981 | 0
79 | 2022-12-26 01:19 | 6 | 18.7 | 40.6 | 37.9 | 0.982 | 0
80 | 2022-12-26 01:20 | 5.9 | 18.7 | 41.5 | 38.3 | 0 | 0
81 | 2022-12-26 01:21 | 6 | 18.8 | 41.2 | 38.3 | 0 | 0
82 | 2022-12-26 01:22 | 6 | 19 | 40.8 | 37.5 | 0 | 0
83 | 2022-12-26 01:23 | 5.8 | 18.9 | 40.4 | 36.6 | 0 | 0
84 | 2022-12-26 01:24 | 5.9 | 18.8 | 40 | 35.8 | 0 | 0
85 | 2022-12-26 01:25 | 6 | 18.9 | 39.6 | 35.1 | 0 | 0
86 | 2022-12-26 01:26 | 6.1 | 18.8 | 39.3 | 34.5 | 0 | 0
87 | 2022-12-26 01:27 | 6.1 | 18.9 | 38.9 | 33.9 | 0 | 0
88 | 2022-12-26 01:28 | 6.1 | 18.8 | 38.6 | 33.3 | 0 | 0
89 | 2022-12-26 01:29 | 6.1 | 18.8 | 38.3 | 32.8 | 0 | 0
90 | 2022-12-26 01:30 | 5.9 | 18.7 | 38 | 32.3 | 0 | 0
91 | 2022-12-26 01:31 | 5.9 | 18.7 | 37.7 | 31.8 | 0 | 0
92 | 2022-12-26 01:32 | 6 | 18.7 | 37.4 | 31.4 | 0 | 0
93 | 2022-12-26 01:33 | 5.9 | 18.7 | 37.2 | 30.9 | 0 | 0
94 | 2022-12-26 01:34 | 6 | 18.7 | 36.9 | 30.5 | 0 | 0
95 | 2022-12-26 01:35 | 5.9 | 18.7 | 36.6 | 30.1 | 0 | 0
96 | 2022-12-26 01:36 | 5.9 | 18.8 | 36.4 | 29.8 | 0 | 0
97 | 2022-12-26 01:37 | 6.1 | 18.7 | 36.1 | 29.4 | 0 | 0
98 | 2022-12-26 01:38 | 6.1 | 18.7 | 35.9 | 29.1 | 0 | 0
99 | 2022-12-26 01:39 | 5.9 | 18.6 | 35.6 | 28.7 | 0 | 0
100 | 2022-12-26 01:40 | 6 | 18.7 | 35.4 | 28.4 | 0 | 0
101 | 2022-12-26 01:41 | 5.9 | 18.7 | 35.2 | 28.1 | 0 | 0
102 | 2022-12-26 01:42 | 5.9 | 18.7 | 34.9 | 27.8 | 0 | 0
103 | 2022-12-26 01:43 | 5.9 | 18.6 | 34.7 | 27.5 | 0 | 0
104 | 2022-12-26 01:44 | 6 | 18.6 | 34.5 | 27.3 | 0 | 0
105 | 2022-12-26 01:45 | 5.9 | 18.6 | 34.3 | 27 | 0 | 0
106 | 2022-12-26 01:46 | 5.9 | 18.6 | 34 | 26.7 | 0 | 0
107 | 2022-12-26 01:47 | 6.1 | 18.6 | 33.8 | 26.5 | 0 | 0
108 | 2022-12-26 01:48 | 6.1 | 18.6 | 33.6 | 26.2 | 0 | 0
109 | 2022-12-26 01:49 | 6.1 | 18.6 | 33.4 | 26 | 0 | 0
110 | 2022-12-26 01:50 | 6 | 18.6 | 33.2 | 25.7 | 0 | 0
111 | 2022-12-26 01:51 | 6.1 | 18.6 | 32.9 | 25.5 | 0 | 0
112 | 2022-12-26 01:52 | 6.1 | 18.6 | 32.7 | 25.3 | 0 | 0
113 | 2022-12-26 01:53 | 6 | 18.6 | 32.5 | 25 | 0 | 0
114 | 2022-12-26 01:54 | 6.3 | 18.6 | 32.3 | 24.8 | 0 | 0
115 | 2022-12-26 01:55 | 6.2 | 18.6 | 32.1 | 24.6 | 0 | 0
116 | 2022-12-26 01:56 | 6.1 | 18.6 | 31.9 | 24.4 | 0 | 0
117 | 2022-12-26 01:57 | 6.1 | 18.6 | 31.7 | 24.2 | 0 | 0
118 | 2022-12-26 01:58 | 6.2 | 18.7 | 31.5 | 24 | 0 | 0
119 | 2022-12-26 01:59 | 6.3 | 18.6 | 31.3 | 23.8 | 0 | 0
120 | 2022-12-26 02:00 | 6.2 | 18.5 | 31.1 | 23.6 | 0 | 0
121 | 2022-12-26 02:01 | 6.3 | 18.6 | 30.9 | 23.4 | 0 | 0
122 | 2022-12-26 02:02 | 6.2 | 18.6 | 30.7 | 23.2 | 0 | 0
123 | 2022-12-26 02:03 | 6.3 | 18.5 | 30.5 | 23 | 0.017 | 0
124 | 2022-12-26 02:04 | 6.2 | 18.5 | 30.3 | 27.4 | 0 | 0
125 | 2022-12-26 02:05 | 6.1 | 18.5 | 30.1 | 27.1 | 0 | 0
126 | 2022-12-26 02:06 | 6.2 | 18.5 | 32.6 | 28.9 | 0.416 | 0
127 | 2022-12-26 02:07 | 6.3 | 18.5 | 40.9 | 28.7 | 0.927 | 0
128 | 2022-12-26 02:08 | 6.5 | 18.5 | 41.4 | 37.6 | 0.945 | 0
129 | 2022-12-26 02:09 | 6.6 | 18.5 | 41.2 | 38.5 | 0.977 | 0
130 | 2022-12-26 02:10 | 6.5 | 18.5 | 41.6 | 38.8 | 0.977 | 0
131 | 2022-12-26 02:11 | 6.5 | 18.7 | 42.3 | 39.3 | 0 | 0
132 | 2022-12-26 02:12 | 6.7 | 18.7 | 42.4 | 39.4 | 0 | 0
133 | 2022-12-26 02:13 | 6.8 | 18.8 | 42 | 38.8 | 0 | 0
134 | 2022-12-26 02:14 | 6.6 | 18.8 | 41.7 | 38 | 0 | 0
135 | 2022-12-26 02:15 | 6.6 | 18.7 | 41.3 | 37.3 | 0 | 0
136 | 2022-12-26 02:16 | 6.8 | 18.7 | 41 | 36.6 | 0 | 0
137 | 2022-12-26 02:17 | 6.6 | 18.7 | 40.6 | 36 | 0 | 0
138 | 2022-12-26 02:18 | 6.5 | 18.7 | 40.3 | 35.4 | 0 | 0
139 | 2022-12-26 02:19 | 6.6 | 18.6 | 40 | 34.9 | 0 | 0
140 | 2022-12-26 02:20 | 6.6 | 18.6 | 39.7 | 34.3 | 0 | 0
141 | 2022-12-26 02:21 | 6.6 | 18.5 | 39.4 | 33.9 | 0 | 0
142 | 2022-12-26 02:22 | 6.6 | 18.6 | 39.1 | 33.4 | 0 | 0
143 | 2022-12-26 02:23 | 6.5 | 18.5 | 38.8 | 32.9 | 0 | 0
144 | 2022-12-26 02:24 | 6.7 | 18.5 | 38.5 | 32.5 | 0 | 0
145 | 2022-12-26 02:25 | 6.5 | 18.5 | 38.3 | 32.1 | 0 | 0
146 | 2022-12-26 02:26 | 6.7 | 18.5 | 38 | 31.7 | 0 | 0
147 | 2022-12-26 02:27 | 6.7 | 18.5 | 37.7 | 31.3 | 0 | 0
148 | 2022-12-26 02:28 | 6.6 | 18.5 | 37.5 | 31 | 0 | 0
149 | 2022-12-26 02:29 | 6.8 | 18.5 | 37.2 | 30.6 | 0 | 0
150 | 2022-12-26 02:30 | 6.6 | 18.5 | 37 | 30.3 | 0 | 0
151 | 2022-12-26 02:31 | 6.8 | 18.5 | 36.7 | 29.9 | 0 | 0
152 | 2022-12-26 02:32 | 6.6 | 18.6 | 36.5 | 29.6 | 0 | 0
153 | 2022-12-26 02:33 | 6.7 | 18.5 | 36.2 | 29.3 | 0 | 0
154 | 2022-12-26 02:34 | 6.8 | 18.6 | 36 | 29 | 0 | 0
155 | 2022-12-26 02:35 | 6.8 | 18.5 | 35.8 | 28.7 | 0 | 0
156 | 2022-12-26 02:36 | 6.9 | 18.5 | 35.5 | 28.5 | 0 | 0
157 | 2022-12-26 02:37 | 6.8 | 18.5 | 35.3 | 28.2 | 0 | 0
158 | 2022-12-26 02:38 | 6.9 | 18.5 | 35.1 | 27.9 | 0 | 0
159 | 2022-12-26 02:39 | 7 | 18.5 | 34.9 | 27.7 | 0 | 0
160 | 2022-12-26 02:40 | 7.1 | 18.5 | 34.6 | 27.4 | 0 | 0
161 | 2022-12-26 02:41 | 6.9 | 18.5 | 34.4 | 27.1 | 0 | 0
162 | 2022-12-26 02:42 | 6.8 | 18.5 | 34.2 | 26.9 | 0 | 0
163 | 2022-12-26 02:43 | 7 | 18.5 | 34 | 26.7 | 0 | 0
164 | 2022-12-26 02:44 | 6.8 | 18.5 | 33.8 | 26.4 | 0 | 0
165 | 2022-12-26 02:45 | 7 | 18.4 | 33.5 | 26.2 | 0 | 0
166 | 2022-12-26 02:46 | 6.9 | 18.4 | 33.3 | 26 | 0 | 0
167 | 2022-12-26 02:47 | 7 | 18.4 | 33.1 | 25.8 | 0 | 0
168 | 2022-12-26 02:48 | 7.1 | 18.4 | 32.9 | 25.6 | 0 | 0
169 | 2022-12-26 02:49 | 7 | 18.4 | 32.7 | 29.2 | 0 | 0
170 | 2022-12-26 02:50 | 7 | 18.4 | 32.5 | 28.8 | 0.522 | 0
171 | 2022-12-26 02:51 | 6.9 | 18.4 | 41 | 30.1 | 0.978 | 0
172 | 2022-12-26 02:52 | 7.2 | 18.4 | 41.7 | 38.1 | 0.983 | 0
173 | 2022-12-26 02:53 | 7 | 18.4 | 41.1 | 38.7 | 0.98 | 0
174 | 2022-12-26 02:54 | 7 | 18.4 | 41.5 | 38.7 | 0.984 | 0
175 | 2022-12-26 02:55 | 7 | 18.5 | 41.6 | 39 | 0.983 | 0
176 | 2022-12-26 02:56 | 6.9 | 18.6 | 41.7 | 39.1 | 0 | 0
177 | 2022-12-26 02:57 | 7.1 | 18.7 | 41.5 | 38.9 | 0 | 0
178 | 2022-12-26 02:58 | 7.1 | 18.8 | 41.2 | 38.2 | 0 | 0
179 | 2022-12-26 02:59 | 7.2 | 18.7 | 40.8 | 37.5 | 0 | 0
180 | 2022-12-26 03:00 | 7.2 | 18.6 | 40.5 | 36.8 | 0 | 0
181 | 2022-12-26 03:01 | 7.1 | 18.5 | 40.2 | 36.2 | 0 | 0
182 | 2022-12-26 03:02 | 6.9 | 18.5 | 39.9 | 35.6 | 0 | 0
183 | 2022-12-26 03:03 | 7 | 18.5 | 39.6 | 35.1 | 0 | 0
184 | 2022-12-26 03:04 | 7 | 18.5 | 39.3 | 34.6 | 0 | 0
185 | 2022-12-26 03:05 | 7.1 | 18.4 | 39 | 34.1 | 0 | 0
186 | 2022-12-26 03:06 | 7.1 | 18.4 | 38.7 | 33.6 | 0 | 0
187 | 2022-12-26 03:07 | 7.2 | 18.4 | 38.5 | 33.2 | 0 | 0
188 | 2022-12-26 03:08 | 7.1 | 18.5 | 38.2 | 32.7 | 0 | 0
189 | 2022-12-26 03:09 | 7.2 | 18.4 | 37.9 | 32.3 | 0 | 0
190 | 2022-12-26 03:10 | 7.2 | 18.5 | 37.7 | 32 | 0 | 0
191 | 2022-12-26 03:11 | 7.2 | 18.5 | 37.4 | 31.6 | 0 | 0
192 | 2022-12-26 03:12 | 7.1 | 18.5 | 37.2 | 31.2 | 0 | 0
193 | 2022-12-26 03:13 | 7 | 18.4 | 36.9 | 30.9 | 0 | 0
194 | 2022-12-26 03:14 | 7 | 18.4 | 36.7 | 30.6 | 0 | 0
195 | 2022-12-26 03:15 | 7.2 | 18.4 | 36.5 | 30.2 | 0 | 0
196 | 2022-12-26 03:16 | 7.1 | 18.4 | 36.3 | 29.9 | 0 | 0
197 | 2022-12-26 03:17 | 7 | 18.4 | 36 | 29.6 | 0 | 0
198 | 2022-12-26 03:18 | 7 | 18.3 | 35.8 | 29.3 | 0 | 0
199 | 2022-12-26 03:19 | 7 | 18.3 | 35.6 | 29 | 0 | 0
200 | 2022-12-26 03:20 | 7 | 18.4 | 35.3 | 28.7 | 0 | 0
201 | 2022-12-26 03:21 | 6.9 | 18.4 | 35.1 | 28.5 | 0 | 0
202 | 2022-12-26 03:22 | 7.1 | 18.4 | 34.9 | 28.2 | 0 | 0
203 | 2022-12-26 03:23 | 7.1 | 18.4 | 34.6 | 27.9 | 0 | 0
204 | 2022-12-26 03:24 | 6.9 | 18.4 | 34.4 | 27.7 | 0 | 0
205 | 2022-12-26 03:25 | 6.9 | 18.4 | 34.2 | 30.1 | 0.009 | 0
206 | 2022-12-26 03:26 | 7.3 | 18.4 | 34 | 31.3 | 0 | 0
207 | 2022-12-26 03:27 | 7.1 | 18.3 | 34 | 31.7 | 0.931 | 0
208 | 2022-12-26 03:28 | 7.2 | 18.3 | 40.4 | 33 | 0.977 | 0
209 | 2022-12-26 03:29 | 7.4 | 18.3 | 39.9 | 37.7 | 0.98 | 0
210 | 2022-12-26 03:30 | 7.3 | 18.4 | 39.5 | 37.1 | 0.98 | 0
211 | 2022-12-26 03:31 | 7.3 | 18.4 | 39.8 | 37.3 | 0.982 | 0
212 | 2022-12-26 03:32 | 7 | 18.4 | 38.7 | 37.3 | 0 | 0
213 | 2022-12-26 03:33 | 7 | 18.5 | 39.8 | 36.4 | 0 | 0
214 | 2022-12-26 03:34 | 6.9 | 18.5 | 39.6 | 36.2 | 0 | 0
215 | 2022-12-26 03:35 | 7.1 | 18.6 | 39.3 | 35.6 | 0 | 0
216 | 2022-12-26 03:36 | 7.1 | 18.6 | 39 | 35 | 0 | 0
217 | 2022-12-26 03:37 | 7.2 | 18.5 | 38.7 | 34.5 | 0 | 0
218 | 2022-12-26 03:38 | 7.1 | 18.5 | 38.4 | 33.9 | 0 | 0
219 | 2022-12-26 03:39 | 7.4 | 18.4 | 38.1 | 33.5 | 0 | 0
220 | 2022-12-26 03:40 | 7.1 | 18.5 | 37.9 | 33 | 0 | 0
221 | 2022-12-26 03:41 | 7.2 | 18.4 | 37.6 | 32.6 | 0 | 0
222 | 2022-12-26 03:42 | 7.1 | 18.4 | 37.3 | 32.2 | 0 | 0
223 | 2022-12-26 03:43 | 7 | 18.4 | 37.1 | 31.8 | 0 | 0
224 | 2022-12-26 03:44 | 6.8 | 18.4 | 36.8 | 31.4 | 0 | 0
225 | 2022-12-26 03:45 | 6.9 | 18.3 | 36.6 | 31 | 0 | 0
226 | 2022-12-26 03:46 | 6.8 | 18.3 | 36.3 | 30.7 | 0 | 0
227 | 2022-12-26 03:47 | 6.8 | 18.3 | 36.1 | 30.3 | 0 | 0
228 | 2022-12-26 03:48 | 6.8 | 18.4 | 35.8 | 30 | 0 | 0
229 | 2022-12-26 03:49 | 6.6 | 18.3 | 35.6 | 29.7 | 0 | 0
230 | 2022-12-26 03:50 | 6.6 | 18.3 | 35.4 | 29.4 | 0 | 0
231 | 2022-12-26 03:51 | 6.5 | 18.3 | 35.1 | 29.1 | 0 | 0
232 | 2022-12-26 03:52 | 6.6 | 18.4 | 34.9 | 28.8 | 0 | 0
233 | 2022-12-26 03:53 | 6.6 | 18.4 | 34.7 | 28.5 | 0 | 0
234 | 2022-12-26 03:54 | 6.4 | 18.4 | 34.5 | 28.2 | 0 | 0
235 | 2022-12-26 03:55 | 6.4 | 18.3 | 34.2 | 28 | 0 | 0
236 | 2022-12-26 03:56 | 6.6 | 18.3 | 34 | 27.7 | 0 | 0
237 | 2022-12-26 03:57 | 6.5 | 18.2 | 33.8 | 27.4 | 0 | 0
238 | 2022-12-26 03:58 | 6.4 | 18.2 | 33.6 | 30.4 | 0 | 0
239 | 2022-12-26 03:59 | 6.5 | 18.3 | 33.4 | 30.1 | 0.85 | 0
240 | 2022-12-26 04:00 | 6.3 | 18.2 | 41.9 | 27.7 | 0.981 | 0
241 | 2022-12-26 04:01 | 6.3 | 18.3 | 41.9 | 38.9 | 0.98 | 0
242 | 2022-12-26 04:02 | 6.1 | 18.3 | 41.5 | 38.9 | 0.981 | 0
243 | 2022-12-26 04:03 | 6 | 18.3 | 41.9 | 39.1 | 0.983 | 0
244 | 2022-12-26 04:04 | 6.1 | 18.4 | 42 | 39.3 | 0 | 0
245 | 2022-12-26 04:05 | 6.3 | 18.4 | 42.1 | 39.3 | 0 | 0
246 | 2022-12-26 04:06 | 6 | 18.6 | 41.8 | 39 | 0 | 0
247 | 2022-12-26 04:07 | 6 | 18.6 | 41.5 | 38.3 | 0 | 0
248 | 2022-12-26 04:08 | 6.2 | 18.6 | 41.2 | 37.6 | 0 | 0
249 | 2022-12-26 04:09 | 6 | 18.5 | 40.8 | 36.9 | 0 | 0
250 | 2022-12-26 04:10 | 6.2 | 18.5 | 40.5 | 36.3 | 0 | 0
251 | 2022-12-26 04:11 | 6.2 | 18.3 | 40.2 | 35.8 | 0 | 0
252 | 2022-12-26 04:12 | 5.9 | 18.4 | 39.9 | 35.2 | 0 | 0
253 | 2022-12-26 04:13 | 6.1 | 18.4 | 39.6 | 34.7 | 0 | 0
254 | 2022-12-26 04:14 | 6 | 18.3 | 39.3 | 34.2 | 0 | 0
255 | 2022-12-26 04:15 | 6.2 | 18.3 | 39 | 33.8 | 0 | 0
256 | 2022-12-26 04:16 | 6.1 | 18.2 | 38.7 | 33.3 | 0 | 0
257 | 2022-12-26 04:17 | 6.1 | 18.3 | 38.5 | 32.9 | 0.01 | 0
258 | 2022-12-26 04:18 | 5.9 | 18.2 | 38.2 | 35.3 | 0.013 | 0
259 | 2022-12-26 04:19 | 5.8 | 18.2 | 37.9 | 35.7 | 0 | 0
260 | 2022-12-26 04:20 | 5.9 | 18.2 | 37.7 | 35.4 | 0.907 | 0
261 | 2022-12-26 04:21 | 5.9 | 18.3 | 41.4 | 21.1 | 1.083 | 0
262 | 2022-12-26 04:22 | 5.8 | 18.3 | 41.1 | 38.2 | 1.096 | 0
263 | 2022-12-26 04:23 | 5.9 | 18.3 | 40.8 | 38.8 | 1.1 | 0
264 | 2022-12-26 04:24 | 6 | 18.3 | 40.5 | 38.8 | 1.092 | 0
265 | 2022-12-26 04:25 | 5.8 | 18.2 | 39.8 | 38.5 | 1.095 | 0
266 | 2022-12-26 04:26 | 5.8 | 18.3 | 39.7 | 38 | 1.091 | 0
267 | 2022-12-26 04:27 | 5.9 | 18.3 | 39.7 | 38 | 1.091 | 0
268 | 2022-12-26 04:28 | 5.8 | 18.3 | 39.6 | 38 | 1.091 | 0
269 | 2022-12-26 04:29 | 5.8 | 18.3 | 39.5 | 37.9 | 1.095 | 0
270 | 2022-12-26 04:30 | 5.8 | 18.3 | 39.4 | 37.8 | 1.088 | 0
271 | 2022-12-26 04:31 | 5.7 | 18.3 | 39.3 | 37.7 | 1.093 | 0
272 | 2022-12-26 04:32 | 5.8 | 18.3 | 39.3 | 37.6 | 1.623 | 0
273 | 2022-12-26 04:33 | 5.7 | 18.3 | 39.2 | 36 | 1.633 | 0
274 | 2022-12-26 04:34 | 5.8 | 18.3 | 39.3 | 36.8 | 1.632 | 0
275 | 2022-12-26 04:35 | 5.9 | 18.4 | 39.1 | 36.9 | 1.634 | 0
276 | 2022-12-26 04:36 | 5.8 | 18.4 | 39.2 | 36.8 | 1.632 | 0
277 | 2022-12-26 04:37 | 5.7 | 18.5 | 39.3 | 36.9 | 1.632 | 0
278 | 2022-12-26 04:38 | 5.7 | 18.6 | 39.2 | 36.9 | 1.631 | 0
279 | 2022-12-26 04:39 | 5.8 | 18.6 | 39.2 | 37.7 | 1.638 | 0
280 | 2022-12-26 04:40 | 5.9 | 18.7 | 39.2 | 37.9 | 1.632 | 0
281 | 2022-12-26 04:41 | 5.9 | 18.7 | 39.2 | 37.9 | 1.607 | 0
282 | 2022-12-26 04:42 | 5.9 | 18.7 | 39.2 | 37.9 | 1.115 | 0
283 | 2022-12-26 04:43 | 5.7 | 18.6 | 39.1 | 37.6 | 1.088 | 0
284 | 2022-12-26 04:44 | 5.7 | 18.6 | 39.1 | 37.5 | 1.092 | 0
285 | 2022-12-26 04:45 | 5.6 | 18.6 | 39 | 37.4 | 1.091 | 0
286 | 2022-12-26 04:46 | 5.6 | 18.5 | 38.9 | 37.4 | 1.086 | 0
287 | 2022-12-26 04:47 | 5.8 | 18.5 | 38.8 | 37.3 | 1.084 | 0
288 | 2022-12-26 04:48 | 6 | 18.6 | 38.7 | 37.2 | 0 | 0
289 | 2022-12-26 04:49 | 5.8 | 18.5 | 38.6 | 37.1 | 0 | 0
290 | 2022-12-26 04:50 | 5.8 | 18.5 | 38.4 | 36.7 | 0 | 0
291 | 2022-12-26 04:51 | 5.9 | 18.5 | 38.1 | 36.1 | 0 | 0
292 | 2022-12-26 04:52 | 5.6 | 18.5 | 37.9 | 35.5 | 0 | 0
293 | 2022-12-26 04:53 | 5.7 | 18.4 | 37.6 | 35 | 0 | 0
294 | 2022-12-26 04:54 | 5.5 | 18.4 | 37.4 | 34.5 | 0 | 0
295 | 2022-12-26 04:55 | 5.5 | 18.4 | 37.1 | 34 | 0 | 0
296 | 2022-12-26 04:56 | 5.6 | 18.4 | 36.9 | 33.6 | 0 | 0
297 | 2022-12-26 04:57 | 5.9 | 18.3 | 36.6 | 33.1 | 0 | 0
298 | 2022-12-26 04:58 | 5.7 | 18.4 | 36.4 | 32.7 | 0 | 0
299 | 2022-12-26 04:59 | 5.7 | 18.4 | 36.1 | 32.3 | 0 | 0
300 | 2022-12-26 05:00 | 5.6 | 18.3 | 35.9 | 31.9 | 0 | 0
301 | 2022-12-26 05:01 | 5.7 | 18.3 | 35.7 | 31.5 | 0 | 0
302 | 2022-12-26 05:02 | 5.6 | 18.3 | 35.4 | 31.2 | 0 | 0
303 | 2022-12-26 05:03 | 5.5 | 18.3 | 35.2 | 30.8 | 0 | 0
304 | 2022-12-26 05:04 | 5.6 | 18.3 | 34.9 | 32.8 | 0.009 | 0
305 | 2022-12-26 05:05 | 5.8 | 18.3 | 34.7 | 33.6 | 0.017 | 0
306 | 2022-12-26 05:06 | 5.8 | 18.4 | 34.7 | 34.4 | 0.526 | 0
307 | 2022-12-26 05:07 | 5.7 | 18.2 | 39.2 | 31.3 | 0.934 | 0
308 | 2022-12-26 05:08 | 5.7 | 18.3 | 39.3 | 36.5 | 0.953 | 0
309 | 2022-12-26 05:09 | 5.8 | 18.3 | 39.2 | 36.7 | 0.975 | 0
310 | 2022-12-26 05:10 | 5.6 | 18.3 | 39.7 | 36.9 | 0.977 | 0
311 | 2022-12-26 05:11 | 5.8 | 18.3 | 40.1 | 37.6 | 0.978 | 0
312 | 2022-12-26 05:12 | 5.6 | 18.4 | 40.6 | 37.8 | 0 | 0
313 | 2022-12-26 05:13 | 5.8 | 18.5 | 40.5 | 37.7 | 0 | 0
314 | 2022-12-26 05:14 | 5.9 | 18.5 | 40.1 | 37.1 | 0 | 0
315 | 2022-12-26 05:15 | 5.8 | 18.6 | 39.8 | 36.5 | 0 | 0
316 | 2022-12-26 05:16 | 5.6 | 18.5 | 39.5 | 35.9 | 0 | 0
317 | 2022-12-26 05:17 | 5.7 | 18.4 | 39.2 | 35.4 | 0 | 0
318 | 2022-12-26 05:18 | 5.6 | 18.4 | 38.9 | 34.8 | 0 | 0
319 | 2022-12-26 05:19 | 5.8 | 18.4 | 38.6 | 34.3 | 0 | 0
320 | 2022-12-26 05:20 | 6 | 18.3 | 38.3 | 33.9 | 0 | 0
321 | 2022-12-26 05:21 | 5.7 | 18.3 | 38 | 33.4 | 0 | 0
322 | 2022-12-26 05:22 | 5.8 | 18.3 | 37.7 | 33 | 0 | 0
323 | 2022-12-26 05:23 | 5.8 | 18.2 | 37.5 | 32.6 | 0 | 0
324 | 2022-12-26 05:24 | 5.6 | 18.2 | 37.2 | 32.2 | 0 | 0
325 | 2022-12-26 05:25 | 5.7 | 18.2 | 36.9 | 31.8 | 0 | 0
326 | 2022-12-26 05:26 | 5.5 | 18.2 | 36.7 | 31.5 | 0 | 0
327 | 2022-12-26 05:27 | 5.6 | 18.2 | 36.4 | 31.1 | 0 | 0
328 | 2022-12-26 05:28 | 5.6 | 18.2 | 36.2 | 33.5 | 0 | 0
329 | 2022-12-26 05:29 | 5.4 | 18.2 | 35.9 | 33.1 | 0 | 0
330 | 2022-12-26 05:30 | 5.4 | 18.2 | 35.7 | 33.3 | 0.196 | 0
331 | 2022-12-26 05:31 | 5.4 | 18.2 | 39.8 | 34 | 0.957 | 0
332 | 2022-12-26 05:32 | 5.6 | 18.3 | 41.9 | 34.6 | 0.982 | 0
333 | 2022-12-26 05:33 | 5.6 | 18.2 | 41.2 | 39.6 | 0.984 | 0
334 | 2022-12-26 05:34 | 5.4 | 18.2 | 41.6 | 39.3 | 0.98 | 0
335 | 2022-12-26 05:35 | 5.7 | 18.2 | 41.7 | 39.8 | 1.128 | 0
336 | 2022-12-26 05:36 | 5.5 | 18.1 | 41.7 | 39.3 | 1.576 | 0
337 | 2022-12-26 05:37 | 5.7 | 18.2 | 41.3 | 38.8 | 1.58 | 0
338 | 2022-12-26 05:38 | 5.4 | 18.1 | 41.2 | 38.7 | 1.578 | 0
339 | 2022-12-26 05:39 | 5.5 | 18.2 | 41 | 38.6 | 1.578 | 0
340 | 2022-12-26 05:40 | 5.5 | 18.2 | 41 | 38.5 | 1.578 | 0
341 | 2022-12-26 05:41 | 5.6 | 18.3 | 41 | 38.5 | 1.579 | 0
342 | 2022-12-26 05:42 | 5.6 | 18.4 | 40.9 | 39.2 | 1.58 | 0
343 | 2022-12-26 05:43 | 5.6 | 18.6 | 40.8 | 39.7 | 1.581 | 0
344 | 2022-12-26 05:44 | 5.5 | 18.5 | 40.8 | 39.6 | 1.571 | 0
345 | 2022-12-26 05:45 | 5.5 | 18.5 | 40.9 | 39.6 | 1.03 | 0
346 | 2022-12-26 05:46 | 5.6 | 18.4 | 40.8 | 39.3 | 0.976 | 0
347 | 2022-12-26 05:47 | 5.6 | 18.3 | 40.8 | 39.2 | 0.98 | 0
348 | 2022-12-26 05:48 | 5.6 | 18.3 | 40.7 | 39.1 | 0.973 | 0
349 | 2022-12-26 05:49 | 5.6 | 18.3 | 40.6 | 39 | 0 | 0
350 | 2022-12-26 05:50 | 5.6 | 18.2 | 40.5 | 38.8 | 0 | 0
351 | 2022-12-26 05:51 | 5.4 | 18.2 | 40.2 | 38.2 | 0 | 0
352 | 2022-12-26 05:52 | 5.5 | 18.2 | 39.9 | 37.6 | 0 | 0
353 | 2022-12-26 05:53 | 5.5 | 18.2 | 39.7 | 37 | 0 | 0
354 | 2022-12-26 05:54 | 5.5 | 18.2 | 39.4 | 36.4 | 0 | 0
355 | 2022-12-26 05:55 | 5.6 | 18.1 | 39.1 | 35.9 | 0 | 0
356 | 2022-12-26 05:56 | 5.6 | 18.1 | 38.8 | 35.4 | 0 | 0
357 | 2022-12-26 05:57 | 5.5 | 18.1 | 38.5 | 34.9 | 0 | 0
358 | 2022-12-26 05:58 | 5.4 | 18.1 | 38.3 | 34.4 | 0 | 0
359 | 2022-12-26 05:59 | 5.4 | 18.1 | 38 | 33.9 | 0 | 0
360 | 2022-12-26 06:00 | 5.4 | 18.1 | 37.7 | 33.5 | 0 | 0
361 | 2022-12-26 06:01 | 5.6 | 18.1 | 37.5 | 33.1 | 0 | 0
362 | 2022-12-26 06:02 | 5.5 | 18.2 | 37.2 | 32.7 | 0 | 0
363 | 2022-12-26 06:03 | 5.5 | 18.1 | 36.9 | 34.7 | 0.012 | 0
364 | 2022-12-26 06:04 | 5.4 | 18.1 | 36.7 | 35.7 | 0.079 | 0
365 | 2022-12-26 06:05 | 5.5 | 18.1 | 38 | 35.7 | 0.963 | 0
366 | 2022-12-26 06:06 | 5.8 | 18.1 | 39.8 | 36.4 | 0.976 | 0
367 | 2022-12-26 06:07 | 5.7 | 18.1 | 39.2 | 37.2 | 0.98 | 0
368 | 2022-12-26 06:08 | 5.5 | 18.1 | 39.3 | 36.9 | 0.981 | 0
369 | 2022-12-26 06:09 | 5.4 | 18.1 | 39.4 | 37.1 | 0.98 | 0
370 | 2022-12-26 06:10 | 5.3 | 18.2 | 39.3 | 37 | 0 | 0
371 | 2022-12-26 06:11 | 5.5 | 18.3 | 39.3 | 37 | 0 | 0
372 | 2022-12-26 06:12 | 5.5 | 18.5 | 39.1 | 36.7 | 0.983 | 0
373 | 2022-12-26 06:13 | 5.5 | 18.5 | 39 | 38.5 | 0.966 | 0
374 | 2022-12-26 06:14 | 5.4 | 18.4 | 38.8 | 38.6 | 0.987 | 0
375 | 2022-12-26 06:15 | 5.4 | 18.3 | 38.7 | 37.1 | 1.068 | 0
376 | 2022-12-26 06:16 | 5.3 | 18.3 | 38.7 | 35.9 | 1.085 | 0
377 | 2022-12-26 06:17 | 5.4 | 18.2 | 38.7 | 36.9 | 1.091 | 0
378 | 2022-12-26 06:18 | 5.3 | 18.3 | 38.7 | 37 | 1.093 | 0
379 | 2022-12-26 06:19 | 5.3 | 18.3 | 38.2 | 37 | 1.092 | 0
380 | 2022-12-26 06:20 | 5.2 | 18.2 | 38.1 | 36.5 | 1.089 | 0
381 | 2022-12-26 06:21 | 5.3 | 18.2 | 38.1 | 36.5 | 1.085 | 0
382 | 2022-12-26 06:22 | 5.5 | 18.1 | 38 | 36.5 | 1.091 | 0
383 | 2022-12-26 06:23 | 5.4 | 18.2 | 38 | 36.4 | 1.091 | 0
384 | 2022-12-26 06:24 | 5.3 | 18.2 | 37.9 | 36.4 | 1.083 | 0
385 | 2022-12-26 06:25 | 5.3 | 18.2 | 37.8 | 36.3 | 1.086 | 0
386 | 2022-12-26 06:26 | 5.3 | 18.2 | 37.7 | 36.2 | 1.085 | 0
387 | 2022-12-26 06:27 | 5.6 | 18.2 | 37.6 | 36.2 | 1.089 | 0
388 | 2022-12-26 06:28 | 5.6 | 18.3 | 37.6 | 36.1 | 1.089 | 0
389 | 2022-12-26 06:29 | 5.6 | 18.2 | 37.5 | 36 | 1.089 | 0
390 | 2022-12-26 06:30 | 5.5 | 18.2 | 37.4 | 36 | 1.084 | 0
391 | 2022-12-26 06:31 | 5.4 | 18.1 | 37.3 | 35.9 | 1.09 | 0
392 | 2022-12-26 06:32 | 5.4 | 18.2 | 37.2 | 35.8 | 1.088 | 0
393 | 2022-12-26 06:33 | 5.6 | 18.3 | 37.2 | 35.7 | 1.605 | 0
394 | 2022-12-26 06:34 | 5.6 | 18.3 | 37.5 | 33.7 | 1.632 | 0
395 | 2022-12-26 06:35 | 5.4 | 18.3 | 37.9 | 35.4 | 1.632 | 0
396 | 2022-12-26 06:36 | 5.4 | 18.3 | 38 | 35.7 | 1.633 | 0
397 | 2022-12-26 06:37 | 5.4 | 18.3 | 38.4 | 35.9 | 1.632 | 0
398 | 2022-12-26 06:38 | 5.4 | 18.3 | 38.7 | 36.1 | 1.632 | 0
399 | 2022-12-26 06:39 | 5.6 | 18.3 | 39.1 | 36.5 | 1.633 | 0
400 | 2022-12-26 06:40 | 5.5 | 18.5 | 39.3 | 36.8 | 1.641 | 0
401 | 2022-12-26 06:41 | 5.7 | 18.6 | 39.7 | 38.1 | 1.633 | 0
402 | 2022-12-26 06:42 | 5.7 | 18.7 | 40 | 38.5 | 1.628 | 0
403 | 2022-12-26 06:43 | 5.5 | 18.7 | 40.2 | 38.8 | 1.382 | 0
404 | 2022-12-26 06:44 | 5.5 | 18.6 | 40.1 | 38.8 | 1.089 | 0
405 | 2022-12-26 06:45 | 5.6 | 18.6 | 40.1 | 38.4 | 1.09 | 0
406 | 2022-12-26 06:46 | 5.4 | 18.5 | 40.1 | 38.4 | 0 | 0
407 | 2022-12-26 06:47 | 5.5 | 18.4 | 40 | 38.3 | 0 | 0
408 | 2022-12-26 06:48 | 5.7 | 18.5 | 39.8 | 37.8 | 0 | 0
409 | 2022-12-26 06:49 | 5.6 | 18.4 | 39.5 | 37.3 | 0 | 0
410 | 2022-12-26 06:50 | 5.6 | 18.4 | 39.2 | 36.7 | 0 | 0
411 | 2022-12-26 06:51 | 5.6 | 18.3 | 38.9 | 36.1 | 0 | 0
412 | 2022-12-26 06:52 | 5.5 | 18.3 | 38.6 | 35.6 | 0 | 0
413 | 2022-12-26 06:53 | 5.6 | 18.2 | 38.3 | 35.1 | 0 | 0
414 | 2022-12-26 06:54 | 5.6 | 18.3 | 38 | 34.6 | 0 | 0
415 | 2022-12-26 06:55 | 5.5 | 18.2 | 37.8 | 34.2 | 0 | 0
416 | 2022-12-26 06:56 | 5.4 | 18.2 | 37.5 | 33.7 | 0 | 0
417 | 2022-12-26 06:57 | 5.4 | 18.1 | 37.2 | 33.3 | 0 | 0
418 | 2022-12-26 06:58 | 5.5 | 18.1 | 37 | 32.9 | 0 | 0
419 | 2022-12-26 06:59 | 5.4 | 18.1 | 36.7 | 32.4 | 0 | 0
420 | 2022-12-26 07:00 | 5.4 | 18.1 | 36.4 | 32 | 0 | 0
421 | 2022-12-26 07:01 | 5.4 | 18.1 | 36.2 | 31.7 | 0.011 | 0
422 | 2022-12-26 07:02 | 5.5 | 18.1 | 35.9 | 34.7 | 0 | 0
423 | 2022-12-26 07:03 | 5.7 | 18.2 | 35.8 | 34.6 | 0.454 | 0
424 | 2022-12-26 07:04 | 5.4 | 18.1 | 39.2 | 30.6 | 0.478 | 0
425 | 2022-12-26 07:05 | 5.7 | 18 | 39.7 | 34.7 | 0.932 | 0
426 | 2022-12-26 07:06 | 5.7 | 18.1 | 39.5 | 36.9 | 0.948 | 0
427 | 2022-12-26 07:07 | 5.6 | 18.1 | 40 | 37.1 | 0.942 | 0
428 | 2022-12-26 07:08 | 5.7 | 18.2 | 40.6 | 37.8 | 0.983 | 0
429 | 2022-12-26 07:09 | 5.7 | 18.3 | 40.1 | 38 | 0 | 0
430 | 2022-12-26 07:10 | 5.8 | 18.5 | 40.2 | 37.7 | 0 | 0
431 | 2022-12-26 07:11 | 5.8 | 18.5 | 39.8 | 37.2 | 0 | 0
432 | 2022-12-26 07:12 | 5.7 | 18.4 | 39.6 | 36.8 | 0.887 | 0
433 | 2022-12-26 07:13 | 5.9 | 18.3 | 40 | 39.4 | 0.017 | 0
434 | 2022-12-26 07:14 | 5.8 | 18.3 | 40.1 | 39.8 | 0.021 | 0
435 | 2022-12-26 07:15 | 5.9 | 18.3 | 40.1 | 40.4 | 0.886 | 0
436 | 2022-12-26 07:16 | 5.8 | 18.2 | 39.9 | 30.2 | 0.976 | 0
437 | 2022-12-26 07:17 | 5.6 | 18.1 | 39.6 | 37.7 | 0.979 | 0
438 | 2022-12-26 07:18 | 5.4 | 18.1 | 39.6 | 37.9 | 0.982 | 0
439 | 2022-12-26 07:19 | 5.6 | 18.2 | 39.7 | 38 | 0.98 | 0
440 | 2022-12-26 07:20 | 5.5 | 18.1 | 39.2 | 38 | 0.975 | 0
441 | 2022-12-26 07:21 | 5.5 | 18.1 | 39.2 | 37.6 | 0.976 | 0
442 | 2022-12-26 07:22 | 5.3 | 18 | 39.4 | 37.6 | 0.976 | 0
443 | 2022-12-26 07:23 | 5.3 | 18.1 | 39.3 | 37.8 | 0.979 | 0
444 | 2022-12-26 07:24 | 5.4 | 18 | 39.1 | 37.8 | 0.977 | 0
445 | 2022-12-26 07:25 | 5.6 | 18.1 | 39 | 37.5 | 0.977 | 0
446 | 2022-12-26 07:26 | 5.5 | 18 | 38.8 | 37.4 | 0.977 | 0
447 | 2022-12-26 07:27 | 5.7 | 18.1 | 38.8 | 37.3 | 0.977 | 0
448 | 2022-12-26 07:28 | 5.5 | 18.1 | 38.7 | 37.2 | 0.977 | 0
449 | 2022-12-26 07:29 | 5.6 | 18 | 38.6 | 37.2 | 1.345 | 0
450 | 2022-12-26 07:30 | 5.6 | 18 | 38.5 | 36 | 1.569 | 0
451 | 2022-12-26 07:31 | 5.5 | 18 | 38.4 | 36.1 | 1.567 | 1
452 | 2022-12-26 07:32 | 5.4 | 18 | 38.4 | 36.2 | 1.572 | 1
453 | 2022-12-26 07:33 | 5.4 | 18 | 38.6 | 36.2 | 1.577 | 1
454 | 2022-12-26 07:34 | 5.5 | 18 | 38.9 | 36.4 | 1.576 | 2
455 | 2022-12-26 07:35 | 5.3 | 18.1 | 39.2 | 36.7 | 1.578 | 2
456 | 2022-12-26 07:36 | 5.5 | 18.2 | 39.6 | 37 | 1.578 | 2
457 | 2022-12-26 07:37 | 5.2 | 18.4 | 39.9 | 38.4 | 0.103 | 3
458 | 2022-12-26 07:38 | 5.5 | 18.5 | 40.3 | 38.7 | 0 | 3
459 | 2022-12-26 07:39 | 5.2 | 18.4 | 40.2 | 38.5 | 0 | 3
460 | 2022-12-26 07:40 | 5.5 | 18.3 | 39.9 | 37.9 | 0 | 4
461 | 2022-12-26 07:41 | 5.2 | 18.1 | 39.6 | 37.3 | 0 | 4
462 | 2022-12-26 07:42 | 5.5 | 18.1 | 39.3 | 36.7 | 0 | 4
463 | 2022-12-26 07:43 | 5.3 | 18.1 | 39 | 36.1 | 0 | 5
464 | 2022-12-26 07:44 | 5.4 | 18.1 | 38.7 | 35.6 | 0 | 5
465 | 2022-12-26 07:45 | 5.3 | 18 | 38.4 | 35.1 | 0 | 5
466 | 2022-12-26 07:46 | 5.2 | 18.1 | 38.1 | 34.7 | 0 | 6
467 | 2022-12-26 07:47 | 5.2 | 18.1 | 37.8 | 34.2 | 0.083 | 6
468 | 2022-12-26 07:48 | 5.2 | 18.1 | 37.6 | 36 | 0 | 6
469 | 2022-12-26 07:49 | 5.4 | 18 | 37.3 | 35.7 | 0 | 7
470 | 2022-12-26 07:50 | 5.4 | 17.9 | 37.1 | 35.1 | 0.993 | 7
471 | 2022-12-26 07:51 | 5.4 | 17.9 | 44.8 | 29.5 | 1.094 | 8
472 | 2022-12-26 07:52 | 5.2 | 17.9 | 44.9 | 42.1 | 1.094 | 8
473 | 2022-12-26 07:53 | 5.2 | 18 | 45 | 42.5 | 1.102 | 8
474 | 2022-12-26 07:54 | 5.3 | 18 | 45.5 | 42.9 | 1.095 | 9
475 | 2022-12-26 07:55 | 5.2 | 18 | 46.1 | 43.3 | 1.101 | 9
476 | 2022-12-26 07:56 | 5.2 | 18.1 | 46.6 | 44 | 1.098 | 10
477 | 2022-12-26 07:57 | 5.2 | 18.1 | 47 | 44.4 | 1.633 | 10
478 | 2022-12-26 07:58 | 5.3 | 18 | 47.5 | 42.8 | 1.647 | 11
479 | 2022-12-26 07:59 | 5.5 | 18.1 | 48.1 | 44.3 | 1.649 | 11
480 | 2022-12-26 08:00 | 5.3 | 18.1 | 47.2 | 44.7 | 1.648 | 12
481 | 2022-12-26 08:01 | 5.4 | 18.3 | 47.2 | 43.9 | 1.801 | 12
482 | 2022-12-26 08:02 | 5.4 | 18.4 | 47.3 | 44 | 1.947 | 13
483 | 2022-12-26 08:03 | 5.5 | 18.5 | 47.4 | 39.8 | 2.014 | 13
484 | 2022-12-26 08:04 | 5.5 | 18.6 | 47.4 | 42.1 | 2.02 | 14
485 | 2022-12-26 08:05 | 5.4 | 19 | 46.7 | 42.6 | 2.011 | 14
486 | 2022-12-26 08:06 | 5.4 | 19.9 | 47.3 | 42.2 | 2.02 | 14
487 | 2022-12-26 08:07 | 5.3 | 20.4 | 46.7 | 42.6 | 2.012 | 15
488 | 2022-12-26 08:08 | 5.3 | 20.7 | 46.4 | 42.2 | 2.019 | 15
489 | 2022-12-26 08:09 | 5.3 | 20.9 | 46.4 | 41.9 | 2.019 | 15
490 | 2022-12-26 08:10 | 5.6 | 21 | 46.4 | 41.9 | 2.007 | 16
491 | 2022-12-26 08:11 | 5.7 | 21.2 | 46.5 | 41.9 | 2.018 | 16
492 | 2022-12-26 08:12 | 5.3 | 21.4 | 46.6 | 42 | 2.017 | 16
493 | 2022-12-26 08:13 | 5.6 | 21.3 | 46.6 | 42.9 | 2.015 | 17
494 | 2022-12-26 08:14 | 5.3 | 21.4 | 46.3 | 43.2 | 2.023 | 17
495 | 2022-12-26 08:15 | 5.4 | 21.3 | 46.1 | 43 | 2.013 | 18
496 | 2022-12-26 08:16 | 5.5 | 21.2 | 46 | 42.8 | 2.003 | 18
497 | 2022-12-26 08:17 | 5.4 | 21.1 | 45.7 | 42.6 | 1.846 | 18
498 | 2022-12-26 08:18 | 5.4 | 21.1 | 45.4 | 42 | 1.841 | 19
499 | 2022-12-26 08:19 | 5.4 | 21 | 45.2 | 41.9 | 1.843 | 19
500 | 2022-12-26 08:20 | 5.4 | 21 | 44.9 | 41.7 | 1.84 | 19
501 | 2022-12-26 08:21 | 5.5 | 21 | 44.5 | 41.4 | 1.834 | 20
502 | 2022-12-26 08:22 | 5.6 | 21 | 44.3 | 41.2 | 1.841 | 20
503 | 2022-12-26 08:23 | 5.6 | 21.1 | 44.1 | 41 | 2.006 | 21
504 | 2022-12-26 08:24 | 5.7 | 21 | 43.8 | 39.7 | 2.003 | 21
505 | 2022-12-26 08:25 | 5.6 | 21 | 43.4 | 39.7 | 2.011 | 21
506 | 2022-12-26 08:26 | 5.7 | 21 | 43.1 | 39.4 | 2.005 | 22
507 | 2022-12-26 08:27 | 5.6 | 21.1 | 42.7 | 39.1 | 2.01 | 22
508 | 2022-12-26 08:28 | 5.6 | 21.1 | 42.4 | 38.9 | 2.01 | 23
509 | 2022-12-26 08:29 | 5.6 | 21.2 | 42.1 | 38.6 | 2.006 | 23
510 | 2022-12-26 08:30 | 5.6 | 21.2 | 41.8 | 38.4 | 2.005 | 23
511 | 2022-12-26 08:31 | 5.6 | 21.3 | 41.5 | 38.1 | 2 | 24
512 | 2022-12-26 08:32 | 5.6 | 21.4 | 41.2 | 37.8 | 2.006 | 24
513 | 2022-12-26 08:33 | 5.9 | 21.4 | 41 | 37.6 | 2.001 | 24
514 | 2022-12-26 08:34 | 5.7 | 21.5 | 41.1 | 37.5 | 2.007 | 24
515 | 2022-12-26 08:35 | 5.8 | 21.4 | 41.3 | 38.5 | 2.005 | 25
516 | 2022-12-26 08:36 | 5.8 | 21.4 | 41.6 | 38.6 | 2.01 | 25
517 | 2022-12-26 08:37 | 5.7 | 21.4 | 41.9 | 38.9 | 1.996 | 25
518 | 2022-12-26 08:38 | 5.8 | 21.2 | 42.2 | 39.1 | 1.845 | 26
519 | 2022-12-26 08:39 | 5.7 | 21.2 | 42.4 | 39 | 1.836 | 26
520 | 2022-12-26 08:40 | 5.9 | 21.2 | 42.7 | 39.4 | 1.84 | 26
521 | 2022-12-26 08:41 | 5.9 | 21.1 | 42.8 | 39.6 | 1.829 | 27
522 | 2022-12-26 08:42 | 6 | 21.2 | 43.1 | 39.8 | 1.84 | 27
523 | 2022-12-26 08:43 | 5.9 | 21.2 | 43.3 | 40 | 1.835 | 27
524 | 2022-12-26 08:44 | 6.1 | 21.3 | 43.3 | 40.1 | 1.841 | 28
525 | 2022-12-26 08:45 | 6.1 | 21.4 | 43.1 | 40 | 1.831 | 28
526 | 2022-12-26 08:46 | 6.1 | 21.3 | 42.8 | 39.9 | 1.83 | 28
527 | 2022-12-26 08:47 | 6.1 | 21.3 | 42.6 | 39.7 | 1.996 | 28
528 | 2022-12-26 08:48 | 5.9 | 21.3 | 42.4 | 37.3 | 2.007 | 29
529 | 2022-12-26 08:49 | 5.9 | 21.4 | 42.1 | 38.5 | 2.004 | 29
530 | 2022-12-26 08:50 | 6.1 | 21.5 | 41.7 | 38.3 | 2.012 | 29
531 | 2022-12-26 08:51 | 6.1 | 21.5 | 41.4 | 38 | 2.002 | 29
532 | 2022-12-26 08:52 | 6 | 21.5 | 41.1 | 37.7 | 2.003 | 30
533 | 2022-12-26 08:53 | 5.8 | 21.5 | 40.8 | 37.5 | 2.01 | 30
534 | 2022-12-26 08:54 | 5.9 | 21.6 | 40.6 | 37.3 | 1.998 | 30
535 | 2022-12-26 08:55 | 5.9 | 21.5 | 40.3 | 37.1 | 2.005 | 31
536 | 2022-12-26 08:56 | 5.9 | 21.5 | 40 | 36.8 | 2.005 | 31
537 | 2022-12-26 08:57 | 6 | 21.7 | 39.8 | 36.6 | 2.001 | 31
538 | 2022-12-26 08:58 | 5.9 | 21.6 | 39.5 | 36.6 | 2.003 | 31
539 | 2022-12-26 08:59 | 5.9 | 21.6 | 39.2 | 37 | 2 | 31
540 | 2022-12-26 09:00 | 6.1 | 21.6 | 39.1 | 36.8 | 1.999 | 32
541 | 2022-12-26 09:01 | 6.2 | 21.5 | 39 | 36.7 | 1.985 | 32
542 | 2022-12-26 09:02 | 6 | 21.4 | 38.8 | 36.5 | 1.831 | 32
543 | 2022-12-26 09:03 | 6 | 21.3 | 38.7 | 36.1 | 1.826 | 33
544 | 2022-12-26 09:04 | 6.2 | 21.4 | 38.8 | 36.1 | 1.828 | 33
545 | 2022-12-26 09:05 | 6.2 | 21.3 | 39.2 | 36.3 | 1.824 | 33
546 | 2022-12-26 09:06 | 6 | 21.3 | 39.4 | 36.6 | 1.826 | 33
547 | 2022-12-26 09:07 | 6.2 | 21.3 | 39.7 | 36.8 | 1.833 | 34
548 | 2022-12-26 09:08 | 5.9 | 21.3 | 40 | 37 | 1.83 | 34
549 | 2022-12-26 09:09 | 6 | 21.4 | 40.2 | 37.3 | 1.832 | 35
550 | 2022-12-26 09:10 | 6.2 | 21.3 | 40.6 | 37.5 | 1.834 | 35
551 | 2022-12-26 09:11 | 6.1 | 21.3 | 40.8 | 37.8 | 1.831 | 35
552 | 2022-12-26 09:12 | 6 | 21.3 | 41 | 38 | 1.984 | 36
553 | 2022-12-26 09:13 | 6.1 | 21.4 | 41.3 | 35.9 | 2.002 | 36
554 | 2022-12-26 09:14 | 5.9 | 21.3 | 41.6 | 37.7 | 2 | 36
555 | 2022-12-26 09:15 | 6 | 21.5 | 41.5 | 38 | 2.008 | 36
556 | 2022-12-26 09:16 | 6.2 | 21.5 | 41.8 | 37.9 | 2.001 | 36
557 | 2022-12-26 09:17 | 5.9 | 21.5 | 42 | 38.2 | 2.006 | 37
558 | 2022-12-26 09:18 | 5.9 | 21.6 | 42.2 | 38.4 | 2.002 | 37
559 | 2022-12-26 09:19 | 6 | 21.7 | 42.4 | 38.5 | 2 | 37
560 | 2022-12-26 09:20 | 6.1 | 21.8 | 42.6 | 38.7 | 2.007 | 37
561 | 2022-12-26 09:21 | 6 | 21.7 | 42.7 | 39.6 | 2.008 | 37
562 | 2022-12-26 09:22 | 6.1 | 21.9 | 42.9 | 39.9 | 2.008 | 38
563 | 2022-12-26 09:23 | 6.3 | 21.9 | 43.2 | 40.1 | 2.005 | 38
564 | 2022-12-26 09:24 | 6.4 | 21.7 | 43.5 | 40.3 | 1.896 | 38
565 | 2022-12-26 09:25 | 6.3 | 21.8 | 43.8 | 40.3 | 1.841 | 39
566 | 2022-12-26 09:26 | 6.2 | 21.7 | 43.9 | 40.6 | 1.838 | 39
567 | 2022-12-26 09:27 | 6.4 | 21.8 | 44.1 | 40.7 | 1.843 | 40
568 | 2022-12-26 09:28 | 6.3 | 21.7 | 44.3 | 40.9 | 1.838 | 40
569 | 2022-12-26 09:29 | 6.2 | 21.7 | 44.6 | 41.1 | 1.834 | 78
570 | 2022-12-26 09:30 | 6.4 | 21.8 | 44.5 | 41.3 | 1.84 | 225
571 | 2022-12-26 09:31 | 6.3 | 21.8 | 44.2 | 41.1 | 1.835 | 381
572 | 2022-12-26 09:32 | 6.6 | 21.6 | 44 | 41 | 1.841 | 509
573 | 2022-12-26 09:33 | 6.6 | 21.8 | 43.8 | 40.7 | 1.835 | 514
574 | 2022-12-26 09:34 | 7.1 | 21.8 | 43.9 | 40.7 | 1.835 | 516
575 | 2022-12-26 09:35 | 7.4 | 21.9 | 44.2 | 40.8 | 1.833 | 523
576 | 2022-12-26 09:36 | 7.3 | 21.9 | 44.4 | 41 | 1.835 | 531
577 | 2022-12-26 09:37 | 7.5 | 22 | 44.7 | 41.2 | 1.84 | 555
578 | 2022-12-26 09:38 | 7.9 | 21.9 | 44.9 | 41.4 | 1.837 | 562
579 | 2022-12-26 09:39 | 7.8 | 22 | 45.1 | 41.6 | 1.835 | 568
580 | 2022-12-26 09:40 | 8.1 | 21.8 | 45.4 | 41.8 | 1.84 | 572
581 | 2022-12-26 09:41 | 8.2 | 21.9 | 45.6 | 42.1 | 1.844 | 572
582 | 2022-12-26 09:42 | 8.3 | 21.9 | 45.7 | 42.2 | 2.004 | 572
583 | 2022-12-26 09:43 | 8.6 | 21.9 | 46 | 39.3 | 2.01 | 569
584 | 2022-12-26 09:44 | 8.7 | 21.9 | 46.2 | 42.3 | 2.009 | 567
585 | 2022-12-26 09:45 | 8.8 | 21.9 | 46 | 43 | 2.014 | 568
586 | 2022-12-26 09:46 | 9 | 21.7 | 46.5 | 42.8 | 2.015 | 570
587 | 2022-12-26 09:47 | 8.8 | 21.5 | 46.8 | 43.3 | 1.995 | 572
588 | 2022-12-26 09:48 | 9.3 | 21.5 | 47 | 43.4 | 1.851 | 575
589 | 2022-12-26 09:49 | 9.7 | 21.4 | 47 | 44.4 | 1.85 | 578
590 | 2022-12-26 09:50 | 9.7 | 21.1 | 46.8 | 44.7 | 1.847 | 581
591 | 2022-12-26 09:51 | 9.5 | 21 | 46.8 | 44.6 | 1.837 | 586
592 | 2022-12-26 09:52 | 9.8 | 20.9 | 46.9 | 44.6 | 1.549 | 588
593 | 2022-12-26 09:53 | 9.5 | 20.7 | 47.2 | 44.2 | 1.516 | 590
594 | 2022-12-26 09:54 | 9.6 | 20.5 | 47.4 | 44.6 | 1.517 | 593
595 | 2022-12-26 09:55 | 9.5 | 20.4 | 47.6 | 44.9 | 1.515 | 598
596 | 2022-12-26 09:56 | 9.7 | 20.4 | 48 | 45.1 | 1.511 | 601
597 | 2022-12-26 09:57 | 10.5 | 20.3 | 48.4 | 45.5 | 1.812 | 603
598 | 2022-12-26 09:58 | 10.3 | 20.5 | 47.8 | 42.1 | 1.845 | 606
599 | 2022-12-26 09:59 | 10.1 | 20.6 | 47.7 | 44.8 | 1.848 | 609
600 | 2022-12-26 10:00 | 10 | 20.8 | 47.5 | 44.9 | 1.836 | 611
601 | 2022-12-26 10:01 | 10.2 | 21.2 | 47.6 | 44.6 | 1.838 | 613
602 | 2022-12-26 10:02 | 10.4 | 21.5 | 47.6 | 44.8 | 1.745 | 617
603 | 2022-12-26 10:03 | 10.4 | 21.7 | 47.5 | 44.7 | 1.625 | 620
604 | 2022-12-26 10:04 | 10.5 | 21.9 | 47.4 | 44.3 | 1.632 | 623
605 | 2022-12-26 10:05 | 10.9 | 22 | 47.3 | 44.3 | 1.629 | 625
606 | 2022-12-26 10:06 | 10.9 | 22.1 | 47.1 | 44.2 | 1.619 | 628
607 | 2022-12-26 10:07 | 10.9 | 22.2 | 46.9 | 44 | 1.717 | 630
608 | 2022-12-26 10:08 | 11.3 | 22.3 | 46.6 | 43.8 | 1.837 | 634
609 | 2022-12-26 10:09 | 12.1 | 22.3 | 46.4 | 43 | 1.842 | 637
610 | 2022-12-26 10:10 | 12.5 | 22 | 46.2 | 44.1 | 1.84 | 640
611 | 2022-12-26 10:11 | 12.8 | 21.6 | 45.9 | 43.9 | 1.839 | 642
612 | 2022-12-26 10:12 | 13 | 21.3 | 45.8 | 43.8 | 1.821 | 645
613 | 2022-12-26 10:13 | 13 | 21.1 | 45.7 | 43.6 | 1.843 | 647
614 | 2022-12-26 10:14 | 13.2 | 20.9 | 45.6 | 40.9 | 1.845 | 650
615 | 2022-12-26 10:15 | 12.6 | 20.8 | 45.5 | 42.1 | 1.845 | 654
616 | 2022-12-26 10:16 | 12.5 | 20.6 | 45 | 42.1 | 1.841 | 657
617 | 2022-12-26 10:17 | 12.7 | 20.6 | 44.6 | 41.6 | 1.838 | 660
618 | 2022-12-26 10:18 | 12.9 | 20.8 | 44.5 | 41.4 | 1.841 | 662
619 | 2022-12-26 10:19 | 12.8 | 21 | 44.2 | 41.3 | 1.839 | 666
620 | 2022-12-26 10:20 | 12.8 | 21.1 | 43.9 | 41.7 | 1.842 | 669
621 | 2022-12-26 10:21 | 12.6 | 21.1 | 43.7 | 41.9 | 1.84 | 672
622 | 2022-12-26 10:22 | 12.8 | 21 | 43.5 | 41.7 | 1.834 | 673
623 | 2022-12-26 10:23 | 13.3 | 20.9 | 43.5 | 41.6 | 1.617 | 676
624 | 2022-12-26 10:24 | 13.9 | 20.7 | 43.4 | 41.2 | 1.502 | 679
625 | 2022-12-26 10:25 | 13.7 | 20.6 | 43.3 | 41.1 | 1.507 | 681
626 | 2022-12-26 10:26 | 13.9 | 20.7 | 43.1 | 41 | 1.834 | 683
627 | 2022-12-26 10:27 | 14.3 | 20.8 | 43 | 40.3 | 1.832 | 686
628 | 2022-12-26 10:28 | 14.7 | 20.8 | 42.7 | 40.5 | 1.835 | 688
629 | 2022-12-26 10:29 | 15 | 21 | 42.5 | 40.3 | 1.829 | 691
630 | 2022-12-26 10:30 | 15 | 21.4 | 42.4 | 40.1 | 1.643 | 693
631 | 2022-12-26 10:31 | 15.1 | 21.6 | 42.2 | 39.9 | 1.615 | 694
632 | 2022-12-26 10:32 | 14.3 | 21.8 | 42.1 | 39.6 | 1.624 | 697
633 | 2022-12-26 10:33 | 14.2 | 21.8 | 42 | 39.5 | 1.622 | 700
634 | 2022-12-26 10:34 | 14.4 | 22 | 42 | 39.5 | 1.614 | 702
635 | 2022-12-26 10:35 | 14.9 | 22.1 | 42.2 | 39.5 | 1.627 | 705
636 | 2022-12-26 10:36 | 14.7 | 22.1 | 42.4 | 39.7 | 1.824 | 707
637 | 2022-12-26 10:37 | 15.1 | 22.1 | 42.9 | 38.8 | 1.837 | 710
638 | 2022-12-26 10:38 | 15.7 | 21.9 | 43.1 | 41 | 1.829 | 712
639 | 2022-12-26 10:39 | 15.8 | 21.5 | 43.5 | 41.3 | 1.834 | 714
640 | 2022-12-26 10:40 | 16 | 21.2 | 43.9 | 41.6 | 1.784 | 716
641 | 2022-12-26 10:41 | 15.2 | 21 | 44.4 | 41.9 | 1.512 | 718
642 | 2022-12-26 10:42 | 15.3 | 20.8 | 44.5 | 42 | 1.51 | 721
643 | 2022-12-26 10:43 | 15.2 | 20.7 | 44.7 | 42.2 | 1.507 | 723
644 | 2022-12-26 10:44 | 15.6 | 20.6 | 45 | 42.4 | 1.505 | 725
645 | 2022-12-26 10:45 | 15.9 | 20.5 | 45.4 | 42.7 | 1.517 | 726
646 | 2022-12-26 10:46 | 16.2 | 20.5 | 45.8 | 43.1 | 1.51 | 730
647 | 2022-12-26 10:47 | 16.4 | 20.4 | 46.1 | 43.4 | 1.513 | 731
648 | 2022-12-26 10:48 | 17 | 20.4 | 46.3 | 43.6 | 1.82 | 732
649 | 2022-12-26 10:49 | 16.9 | 20.4 | 47.1 | 40.8 | 1.844 | 735
650 | 2022-12-26 10:50 | 16.6 | 20.5 | 46.7 | 43.6 | 2.002 | 737
651 | 2022-12-26 10:51 | 16.4 | 20.7 | 46.2 | 40.9 | 2.007 | 738
652 | 2022-12-26 10:52 | 16.5 | 20.9 | 46.2 | 42 | 2 | 739
653 | 2022-12-26 10:53 | 17.2 | 21.3 | 46.1 | 42.6 | 2.006 | 741
654 | 2022-12-26 10:54 | 17.6 | 21.7 | 46.1 | 42.6 | 2.013 | 742
655 | 2022-12-26 10:55 | 17.9 | 22 | 45.8 | 43.6 | 1.988 | 743
656 | 2022-12-26 10:56 | 17.1 | 22.3 | 45.7 | 43.7 | 0 | 746
657 | 2022-12-26 10:57 | 17 | 22.4 | 45.7 | 43.9 | 0 | 748
658 | 2022-12-26 10:58 | 16.9 | 22.2 | 45.6 | 43.6 | 0 | 749
659 | 2022-12-26 10:59 | 17.4 | 21.6 | 45.4 | 43.2 | 0 | 751
660 | 2022-12-26 11:00 | 17 | 21.4 | 45.2 | 42.7 | 1.465 | 754
661 | 2022-12-26 11:01 | 17.1 | 21.1 | 45.6 | 41.8 | 0.901 | 757
662 | 2022-12-26 11:02 | 17.2 | 20.9 | 45.2 | 44.8 | 1.168 | 759
663 | 2022-12-26 11:03 | 17.6 | 20.7 | 45.2 | 43.3 | 0.984 | 760
664 | 2022-12-26 11:04 | 17.4 | 20.5 | 45.3 | 43.4 | 1.209 | 761
665 | 2022-12-26 11:05 | 17.6 | 20.5 | 45.2 | 43.5 | 1.511 | 762
666 | 2022-12-26 11:06 | 17.7 | 20.4 | 45 | 42.7 | 1.514 | 763
667 | 2022-12-26 11:07 | 18 | 20.3 | 45 | 42.7 | 1.511 | 763
668 | 2022-12-26 11:08 | 17.7 | 20.3 | 44.8 | 42.6 | 1.796 | 761
669 | 2022-12-26 11:09 | 17.8 | 20.4 | 44.7 | 40.4 | 1.838 | 762
670 | 2022-12-26 11:10 | 17.1 | 20.7 | 44.6 | 41.4 | 1.834 | 763
671 | 2022-12-26 11:11 | 17.2 | 20.9 | 44.3 | 41.3 | 1.836 | 764
672 | 2022-12-26 11:12 | 17.2 | 21.3 | 44 | 41 | 1.832 | 766
673 | 2022-12-26 11:13 | 17.4 | 21.6 | 43.8 | 40.8 | 1.832 | 767
674 | 2022-12-26 11:14 | 17.5 | 21.9 | 43.5 | 40.7 | 1.839 | 765
675 | 2022-12-26 11:15 | 17.2 | 22 | 43.3 | 40.4 | 1.831 | 768
676 | 2022-12-26 11:16 | 16.9 | 22.1 | 43 | 40.7 | 1.829 | 771
677 | 2022-12-26 11:17 | 16.9 | 22.2 | 42.8 | 40.7 | 1.83 | 775
678 | 2022-12-26 11:18 | 16.9 | 22.2 | 42.7 | 41.5 | 1.836 | 778
679 | 2022-12-26 11:19 | 16.9 | 21.8 | 42.6 | 41.5 | 1.775 | 779
680 | 2022-12-26 11:20 | 17.1 | 21.5 | 42.6 | 41.4 | 1.612 | 781
681 | 2022-12-26 11:21 | 17.4 | 21.1 | 42.6 | 41.3 | 1.392 | 783
682 | 2022-12-26 11:22 | 17.7 | 21 | 42.5 | 41.1 | 1.092 | 785
683 | 2022-12-26 11:23 | 17.5 | 20.8 | 42.4 | 40.8 | 1.094 | 787
684 | 2022-12-26 11:24 | 17 | 20.7 | 42.4 | 40.7 | 1.094 | 787
685 | 2022-12-26 11:25 | 17.3 | 20.6 | 42.3 | 40.7 | 1.092 | 784
686 | 2022-12-26 11:26 | 17.5 | 20.6 | 42.2 | 40.6 | 1.507 | 782
687 | 2022-12-26 11:27 | 17.7 | 20.5 | 42.1 | 39.8 | 1.503 | 784
688 | 2022-12-26 11:28 | 17.3 | 20.5 | 42 | 40 | 1.508 | 787
689 | 2022-12-26 11:29 | 17.7 | 20.5 | 41.7 | 39.8 | 1.505 | 783
690 | 2022-12-26 11:30 | 17.7 | 20.4 | 41.6 | 39.6 | 1.505 | 788
691 | 2022-12-26 11:31 | 18.3 | 20.5 | 41.5 | 39.6 | 1.508 | 788
692 | 2022-12-26 11:32 | 18.2 | 20.4 | 41.3 | 39.4 | 1.508 | 790
693 | 2022-12-26 11:33 | 17.5 | 20.4 | 41.2 | 39.3 | 1.663 | 793
694 | 2022-12-26 11:34 | 17.7 | 20.6 | 41.5 | 39.2 | 1.826 | 795
695 | 2022-12-26 11:35 | 18.1 | 20.6 | 41.7 | 38.6 | 1.834 | 800
696 | 2022-12-26 11:36 | 18 | 20.8 | 42 | 39 | 1.828 | 800
697 | 2022-12-26 11:37 | 18 | 21.1 | 42.1 | 39.1 | 1.947 | 799
698 | 2022-12-26 11:38 | 17.3 | 21.4 | 42.4 | 38.5 | 1.997 | 799
699 | 2022-12-26 11:39 | 17.1 | 21.8 | 42.2 | 38.6 | 1.997 | 800
700 | 2022-12-26 11:40 | 17.1 | 22 | 41.8 | 38.6 | 1.998 | 800
701 | 2022-12-26 11:41 | 16.9 | 22.1 | 41.5 | 38.2 | 1.994 | 798
702 | 2022-12-26 11:42 | 17.2 | 22.1 | 41.3 | 38 | 2 | 802
703 | 2022-12-26 11:43 | 17 | 22.2 | 41 | 38.2 | 1.995 | 806
704 | 2022-12-26 11:44 | 17.3 | 22.1 | 40.8 | 38.5 | 1.999 | 809
705 | 2022-12-26 11:45 | 17.4 | 22 | 40.7 | 39.6 | 1.992 | 809
706 | 2022-12-26 11:46 | 17.7 | 21.7 | 40.7 | 39.6 | 1.925 | 808
707 | 2022-12-26 11:47 | 18.1 | 21.5 | 40.7 | 39.5 | 1.548 | 807
708 | 2022-12-26 11:48 | 17.9 | 21.3 | 40.6 | 39.4 | 1.091 | 807
709 | 2022-12-26 11:49 | 18 | 21.1 | 40.6 | 39.2 | 1.088 | 810
710 | 2022-12-26 11:50 | 18.1 | 20.9 | 40.5 | 39 | 1.087 | 812
711 | 2022-12-26 11:51 | 18 | 20.8 | 40.4 | 38.9 | 1.089 | 812
712 | 2022-12-26 11:52 | 18.1 | 20.7 | 40.4 | 38.8 | 1.091 | 815
713 | 2022-12-26 11:53 | 18.2 | 20.6 | 40.3 | 38.8 | 1.091 | 814
714 | 2022-12-26 11:54 | 17.8 | 20.6 | 40.1 | 38.7 | 1.093 | 813
715 | 2022-12-26 11:55 | 18.2 | 20.5 | 40.1 | 38.6 | 1.5 | 815
716 | 2022-12-26 11:56 | 18.1 | 20.5 | 40 | 37.9 | 1.502 | 815
717 | 2022-12-26 11:57 | 18.1 | 20.5 | 39.9 | 38.1 | 1.501 | 814
718 | 2022-12-26 11:58 | 17.9 | 20.5 | 39.7 | 37.9 | 1.508 | 816
719 | 2022-12-26 11:59 | 17.7 | 20.4 | 39.6 | 37.8 | 1.509 | 817
720 | 2022-12-26 12:00 | 17.7 | 20.4 | 39.4 | 37.7 | 1.499 | 819
721 | 2022-12-26 12:01 | 17.6 | 20.4 | 39.3 | 37.5 | 1.503 | 820
722 | 2022-12-26 12:02 | 17.9 | 20.5 | 39.2 | 37.5 | 1.78 | 821
723 | 2022-12-26 12:03 | 17 | 20.6 | 39.2 | 35 | 1.822 | 822
724 | 2022-12-26 12:04 | 16.7 | 20.6 | 39.2 | 36.6 | 1.823 | 824
725 | 2022-12-26 12:05 | 16.8 | 20.9 | 39.4 | 36.8 | 1.821 | 825
726 | 2022-12-26 12:06 | 17.1 | 21.1 | 39.9 | 36.9 | 1.828 | 825
727 | 2022-12-26 12:07 | 17.1 | 21.5 | 40.1 | 37.3 | 1.826 | 825
728 | 2022-12-26 12:08 | 17.5 | 21.8 | 40.4 | 37.6 | 1.825 | 825
729 | 2022-12-26 12:09 | 17.6 | 21.8 | 40.7 | 37.8 | 1.826 | 824
730 | 2022-12-26 12:10 | 17.4 | 21.9 | 41 | 38.1 | 1.823 | 826
731 | 2022-12-26 12:11 | 17.8 | 22 | 41.3 | 38.3 | 1.826 | 827
732 | 2022-12-26 12:12 | 18.2 | 22 | 41.6 | 39 | 1.829 | 831
733 | 2022-12-26 12:13 | 18.3 | 21.9 | 41.9 | 39.9 | 1.827 | 831
734 | 2022-12-26 12:14 | 18 | 21.5 | 42 | 40.1 | 1.826 | 832
735 | 2022-12-26 12:15 | 18.1 | 21.3 | 41.9 | 40.2 | 1.718 | 830
736 | 2022-12-26 12:16 | 17.7 | 21.1 | 41.8 | 39.9 | 1.501 | 828
737 | 2022-12-26 12:17 | 18.3 | 20.9 | 41.7 | 39.7 | 1.51 | 827
738 | 2022-12-26 12:18 | 18.3 | 20.8 | 41.7 | 40.4 | 1.507 | 829
739 | 2022-12-26 12:19 | 18 | 20.8 | 41.5 | 40.4 | 1.506 | 827
740 | 2022-12-26 12:20 | 18.2 | 20.7 | 41.5 | 40.2 | 1.494 | 826
741 | 2022-12-26 12:21 | 18.5 | 20.6 | 41.5 | 40.2 | 1.096 | 825
742 | 2022-12-26 12:22 | 18.3 | 20.5 | 41.4 | 40 | 1.092 | 829
743 | 2022-12-26 12:23 | 17.8 | 20.5 | 41.4 | 39.8 | 1.09 | 830
744 | 2022-12-26 12:24 | 17.5 | 20.5 | 41.3 | 39.7 | 1.086 | 829
745 | 2022-12-26 12:25 | 17.9 | 20.5 | 41.3 | 39.7 | 1.088 | 831
746 | 2022-12-26 12:26 | 17.1 | 20.4 | 41.1 | 39.6 | 1.089 | 829
747 | 2022-12-26 12:27 | 17.1 | 20.4 | 41 | 39.5 | 1.089 | 830
748 | 2022-12-26 12:28 | 17.4 | 20.5 | 40.9 | 39.4 | 1.673 | 830
749 | 2022-12-26 12:29 | 17.3 | 20.7 | 40.9 | 38.6 | 1.825 | 830
750 | 2022-12-26 12:30 | 17.4 | 20.7 | 40.7 | 38 | 1.822 | 829
751 | 2022-12-26 12:31 | 17.9 | 20.9 | 40.4 | 37.9 | 1.826 | 828
752 | 2022-12-26 12:32 | 17.6 | 21.3 | 40.1 | 37.6 | 1.825 | 829
753 | 2022-12-26 12:33 | 17.6 | 21.5 | 40 | 37.5 | 1.82 | 829
754 | 2022-12-26 12:34 | 17.7 | 21.7 | 40.2 | 37.4 | 1.828 | 828
755 | 2022-12-26 12:35 | 17.9 | 21.9 | 40.5 | 37.7 | 1.828 | 826
756 | 2022-12-26 12:36 | 18 | 21.9 | 40.8 | 37.9 | 1.83 | 826
757 | 2022-12-26 12:37 | 17.5 | 22.1 | 41 | 38.1 | 1.83 | 825
758 | 2022-12-26 12:38 | 17.2 | 21.9 | 41.3 | 39.3 | 1.827 | 826
759 | 2022-12-26 12:39 | 17.2 | 21.7 | 41.7 | 39.6 | 1.832 | 828
760 | 2022-12-26 12:40 | 17.5 | 21.4 | 42.2 | 40 | 1.775 | 826
761 | 2022-12-26 12:41 | 18 | 21.1 | 42.6 | 40.4 | 1.506 | 825
762 | 2022-12-26 12:42 | 18.1 | 21 | 43 | 40.5 | 1.506 | 824
763 | 2022-12-26 12:43 | 17.5 | 21 | 43.4 | 40.9 | 1.513 | 828
764 | 2022-12-26 12:44 | 16.8 | 20.9 | 43.7 | 41.3 | 1.508 | 827
765 | 2022-12-26 12:45 | 17.3 | 20.7 | 44 | 41.5 | 1.511 | 829
766 | 2022-12-26 12:46 | 17.2 | 20.7 | 44.4 | 42.4 | 1.509 | 830
767 | 2022-12-26 12:47 | 17 | 20.6 | 44.7 | 43 | 1.511 | 827
768 | 2022-12-26 12:48 | 17.2 | 20.6 | 45.4 | 43.5 | 1.511 | 829
769 | 2022-12-26 12:49 | 17.1 | 20.6 | 45.8 | 43.9 | 1.399 | 828
770 | 2022-12-26 12:50 | 17.2 | 20.5 | 46.2 | 44.3 | 0 | 827
771 | 2022-12-26 12:51 | 17.6 | 20.5 | 46.4 | 44.2 | 0 | 829
772 | 2022-12-26 12:52 | 17.7 | 20.5 | 46.2 | 43.8 | 0 | 830
773 | 2022-12-26 12:53 | 17.4 | 20.5 | 46 | 43.3 | 0 | 831
774 | 2022-12-26 12:54 | 16.8 | 20.5 | 45.7 | 42.9 | 1.086 | 831
775 | 2022-12-26 12:55 | 17.4 | 20.4 | 46.7 | 42.3 | 1.018 | 831
776 | 2022-12-26 12:56 | 17.7 | 20.5 | 46.5 | 46.1 | 1.212 | 830
777 | 2022-12-26 12:57 | 18 | 20.6 | 46.4 | 40.2 | 1.086 | 830
778 | 2022-12-26 12:58 | 18.2 | 20.6 | 46.2 | 43.6 | 1.495 | 830
779 | 2022-12-26 12:59 | 17.6 | 21 | 46.3 | 44 | 1.57 | 829
780 | 2022-12-26 13:00 | 17.9 | 21.3 | 45.8 | 43.3 | 1.571 | 828
781 | 2022-12-26 13:01 | 17.7 | 21.7 | 45.6 | 43 | 1.822 | 828
782 | 2022-12-26 13:02 | 18 | 21.9 | 45.5 | 41.3 | 1.839 | 828
783 | 2022-12-26 13:03 | 18.3 | 22.1 | 45.4 | 42.2 | 1.839 | 827
784 | 2022-12-26 13:04 | 17.6 | 22.2 | 45.2 | 42.1 | 1.838 | 828
785 | 2022-12-26 13:05 | 17 | 22.3 | 45 | 42.8 | 1.84 | 828
786 | 2022-12-26 13:06 | 17.2 | 22 | 44.8 | 42.9 | 1.839 | 826
787 | 2022-12-26 13:07 | 17.8 | 21.7 | 44.6 | 42.8 | 1.835 | 824
788 | 2022-12-26 13:08 | 18 | 21.5 | 44.6 | 42.6 | 1.711 | 823
789 | 2022-12-26 13:09 | 18 | 21.3 | 44.5 | 42.4 | 1.512 | 823
790 | 2022-12-26 13:10 | 18.3 | 21.1 | 44.4 | 42.6 | 1.513 | 824
791 | 2022-12-26 13:11 | 18.3 | 21 | 44.2 | 42.9 | 1.513 | 824
792 | 2022-12-26 13:12 | 18.6 | 20.9 | 44 | 42.8 | 1.506 | 821
793 | 2022-12-26 13:13 | 18.8 | 20.8 | 44 | 42.6 | 1.382 | 819
794 | 2022-12-26 13:14 | 18.3 | 20.8 | 43.9 | 42.5 | 1.093 | 818
795 | 2022-12-26 13:15 | 18.1 | 20.8 | 43.9 | 42.2 | 1.093 | 816
796 | 2022-12-26 13:16 | 18.4 | 20.7 | 43.9 | 42.1 | 1.096 | 814
797 | 2022-12-26 13:17 | 18.5 | 20.7 | 43.8 | 42.1 | 1.096 | 814
798 | 2022-12-26 13:18 | 18.5 | 20.7 | 43.7 | 42 | 1.096 | 815
799 | 2022-12-26 13:19 | 18.4 | 20.6 | 43.5 | 41.9 | 1.093 | 814
800 | 2022-12-26 13:20 | 18.3 | 20.7 | 43.4 | 41.7 | 1.093 | 814
801 | 2022-12-26 13:21 | 18.3 | 20.6 | 43.3 | 41.6 | 1.091 | 813
802 | 2022-12-26 13:22 | 18.2 | 20.6 | 43.2 | 41.5 | 1.485 | 812
803 | 2022-12-26 13:23 | 18.3 | 20.5 | 43.1 | 38.7 | 1.507 | 809
804 | 2022-12-26 13:24 | 18.2 | 20.5 | 42.9 | 40.9 | 1.505 | 806
805 | 2022-12-26 13:25 | 18.2 | 20.5 | 42.9 | 41.1 | 1.508 | 804
806 | 2022-12-26 13:26 | 18 | 20.6 | 42.7 | 41.6 | 1.513 | 802
807 | 2022-12-26 13:27 | 18.1 | 20.6 | 42.6 | 41.5 | 1.508 | 801
808 | 2022-12-26 13:28 | 17.9 | 20.5 | 42.6 | 41.5 | 1.505 | 801
809 | 2022-12-26 13:29 | 17.7 | 20.5 | 42.6 | 41.5 | 1.492 | 800
810 | 2022-12-26 13:30 | 17.9 | 20.6 | 42.5 | 41.4 | 1.728 | 800
811 | 2022-12-26 13:31 | 17.8 | 20.6 | 42.5 | 37.7 | 1.605 | 799
812 | 2022-12-26 13:32 | 18 | 20.6 | 42.4 | 40 | 1.565 | 797
813 | 2022-12-26 13:33 | 17.9 | 20.9 | 42.1 | 39.9 | 1.559 | 796
814 | 2022-12-26 13:34 | 18.2 | 21.3 | 42 | 39.7 | 1.558 | 796
815 | 2022-12-26 13:35 | 17.8 | 21.6 | 42.5 | 39.7 | 1.559 | 795
816 | 2022-12-26 13:36 | 18.2 | 21.9 | 42.9 | 40.1 | 1.742 | 793
817 | 2022-12-26 13:37 | 18.4 | 22 | 43.3 | 41.2 | 1.833 | 792
818 | 2022-12-26 13:38 | 17.9 | 22.2 | 43.5 | 40.8 | 1.837 | 790
819 | 2022-12-26 13:39 | 18.4 | 22.3 | 43.7 | 41.9 | 1.83 | 788
820 | 2022-12-26 13:40 | 17.9 | 22 | 43.6 | 42.4 | 1.654 | 786
821 | 2022-12-26 13:41 | 18.1 | 21.6 | 43.6 | 42.3 | 1.609 | 783
822 | 2022-12-26 13:42 | 18.1 | 21.3 | 43.6 | 42.2 | 1.414 | 781
823 | 2022-12-26 13:43 | 18.6 | 21.2 | 43.5 | 42.1 | 1.093 | 780
824 | 2022-12-26 13:44 | 18.5 | 21.1 | 43.5 | 41.7 | 1.092 | 779
825 | 2022-12-26 13:45 | 18.4 | 21 | 43.4 | 41.7 | 1.096 | 777
826 | 2022-12-26 13:46 | 18.5 | 20.8 | 43.4 | 41.6 | 1.095 | 775
827 | 2022-12-26 13:47 | 18.8 | 20.8 | 43.2 | 41.6 | 1.089 | 774
828 | 2022-12-26 13:48 | 18.9 | 20.8 | 43.1 | 41.5 | 1.09 | 773
829 | 2022-12-26 13:49 | 18.8 | 20.7 | 43 | 41.3 | 1.448 | 771
830 | 2022-12-26 13:50 | 18.7 | 20.7 | 42.9 | 40.9 | 1.508 | 769
831 | 2022-12-26 13:51 | 18.9 | 20.6 | 42.8 | 40.7 | 1.504 | 767
832 | 2022-12-26 13:52 | 18.5 | 20.6 | 42.7 | 40.6 | 1.511 | 766
833 | 2022-12-26 13:53 | 18.4 | 20.6 | 42.4 | 40.5 | 1.511 | 765
834 | 2022-12-26 13:54 | 18.8 | 20.6 | 42.3 | 40.3 | 1.507 | 763
835 | 2022-12-26 13:55 | 18.1 | 20.6 | 42.2 | 40.2 | 1.508 | 763
836 | 2022-12-26 13:56 | 18.5 | 20.6 | 42.1 | 40.2 | 1.5 | 762
837 | 2022-12-26 13:57 | 18.5 | 20.6 | 42 | 40 | 1.508 | 761
838 | 2022-12-26 13:58 | 19 | 20.5 | 41.9 | 39.9 | 1.508 | 757
839 | 2022-12-26 13:59 | 19.2 | 20.5 | 41.7 | 39.8 | 1.507 | 754
840 | 2022-12-26 14:00 | 18.7 | 20.5 | 41.7 | 40.5 | 1.515 | 752
841 | 2022-12-26 14:01 | 18.3 | 20.5 | 41.5 | 40.5 | 1.508 | 750
842 | 2022-12-26 14:02 | 18 | 20.5 | 41.4 | 40.3 | 1.503 | 748
843 | 2022-12-26 14:03 | 17.9 | 20.4 | 41.4 | 40.4 | 1.492 | 745
844 | 2022-12-26 14:04 | 17.9 | 20.6 | 41.7 | 41.1 | 1.545 | 744
845 | 2022-12-26 14:05 | 17.8 | 20.6 | 42.2 | 41.3 | 1.666 | 741
846 | 2022-12-26 14:06 | 18 | 20.6 | 42.7 | 40.3 | 1.507 | 738
847 | 2022-12-26 14:07 | 18.4 | 20.7 | 42.7 | 41 | 0.955 | 737
848 | 2022-12-26 14:08 | 18.2 | 21 | 42.5 | 40.2 | 0.952 | 735
849 | 2022-12-26 14:09 | 17.9 | 21.4 | 42.4 | 40 | 0.957 | 733
850 | 2022-12-26 14:10 | 18.4 | 21.8 | 42.3 | 39.9 | 0.953 | 731
851 | 2022-12-26 14:11 | 18.6 | 22 | 42.2 | 39.9 | 0.952 | 729
852 | 2022-12-26 14:12 | 17.6 | 22.2 | 42.1 | 39.8 | 1.447 | 727
853 | 2022-12-26 14:13 | 18 | 22.3 | 41.9 | 40.9 | 1.618 | 725
854 | 2022-12-26 14:14 | 18.1 | 21.9 | 41.8 | 40.5 | 1.621 | 724
855 | 2022-12-26 14:15 | 17.7 | 21.6 | 41.7 | 40.5 | 1.611 | 722
856 | 2022-12-26 14:16 | 18 | 21.3 | 41.7 | 40.5 | 1.593 | 720
857 | 2022-12-26 14:17 | 18 | 21.1 | 41.7 | 40.2 | 1.503 | 717
858 | 2022-12-26 14:18 | 18.2 | 21 | 41.6 | 39.5 | 1.504 | 715
859 | 2022-12-26 14:19 | 18.3 | 21 | 41.5 | 39.5 | 1.503 | 712
860 | 2022-12-26 14:20 | 18.6 | 20.8 | 41.3 | 39.5 | 1.504 | 711
861 | 2022-12-26 14:21 | 18.5 | 20.8 | 41.1 | 39.3 | 1.504 | 708
862 | 2022-12-26 14:22 | 18.6 | 20.7 | 41.1 | 39.1 | 1.504 | 706
863 | 2022-12-26 14:23 | 18.4 | 20.7 | 40.9 | 39.1 | 1.5 | 704
864 | 2022-12-26 14:24 | 18.3 | 20.8 | 40.8 | 38.9 | 1.504 | 701
865 | 2022-12-26 14:25 | 18.1 | 20.7 | 40.7 | 38.8 | 1.5 | 699
866 | 2022-12-26 14:26 | 18.2 | 20.7 | 40.5 | 38.7 | 1.503 | 695
867 | 2022-12-26 14:27 | 17.9 | 20.6 | 40.4 | 38.6 | 1.499 | 693
868 | 2022-12-26 14:28 | 17.6 | 20.6 | 40.3 | 38.5 | 1.5 | 691
869 | 2022-12-26 14:29 | 17.6 | 20.6 | 40.2 | 38.4 | 1.502 | 688
870 | 2022-12-26 14:30 | 17.3 | 20.5 | 40 | 38.3 | 1.503 | 686
871 | 2022-12-26 14:31 | 17.7 | 20.5 | 39.9 | 38.7 | 1.502 | 684
872 | 2022-12-26 14:32 | 17.5 | 20.6 | 39.9 | 38.8 | 1.498 | 681
873 | 2022-12-26 14:33 | 17.8 | 20.5 | 39.8 | 38.7 | 1.486 | 678
874 | 2022-12-26 14:34 | 17.8 | 20.6 | 40 | 38.7 | 1.091 | 676
875 | 2022-12-26 14:35 | 18 | 20.5 | 40.5 | 38.7 | 1.088 | 674
876 | 2022-12-26 14:36 | 17.9 | 20.5 | 40.8 | 39 | 1.088 | 670
877 | 2022-12-26 14:37 | 17.4 | 20.7 | 41.4 | 39.3 | 1.58 | 667
878 | 2022-12-26 14:38 | 17.4 | 20.8 | 41.7 | 36.7 | 1.622 | 665
879 | 2022-12-26 14:39 | 17 | 20.9 | 42 | 40.1 | 1.62 | 661
880 | 2022-12-26 14:40 | 17.5 | 20.9 | 42.2 | 40.4 | 1.619 | 658
881 | 2022-12-26 14:41 | 17.1 | 21.3 | 42.7 | 40.6 | 1.61 | 655
882 | 2022-12-26 14:42 | 16.8 | 21.5 | 43.1 | 41.1 | 1.547 | 653
883 | 2022-12-26 14:43 | 16.9 | 21.9 | 43.5 | 41.4 | 1.3 | 650
884 | 2022-12-26 14:44 | 16.9 | 22 | 43.9 | 41.5 | 1.44 | 648
885 | 2022-12-26 14:45 | 17.1 | 22.2 | 44.3 | 41.8 | 1.567 | 645
886 | 2022-12-26 14:46 | 17.1 | 22.4 | 44.8 | 41.5 | 1.563 | 641
887 | 2022-12-26 14:47 | 17 | 22.2 | 45.3 | 43.4 | 1.566 | 639
888 | 2022-12-26 14:48 | 16.9 | 21.9 | 45.8 | 44 | 1.56 | 636
889 | 2022-12-26 14:49 | 17.5 | 21.5 | 46 | 44.5 | 1.514 | 632
890 | 2022-12-26 14:50 | 17.2 | 21.2 | 46.4 | 44.7 | 1.055 | 628
891 | 2022-12-26 14:51 | 17.6 | 21.1 | 46.9 | 44.7 | 0.979 | 625
892 | 2022-12-26 14:52 | 17 | 21 | 47.3 | 44.9 | 1.137 | 623
893 | 2022-12-26 14:53 | 17.4 | 20.9 | 47.7 | 45.4 | 1.509 | 620
894 | 2022-12-26 14:54 | 17.5 | 20.8 | 47.8 | 44.9 | 1.512 | 616
895 | 2022-12-26 14:55 | 17.6 | 20.7 | 48.4 | 46.1 | 1.516 | 614
896 | 2022-12-26 14:56 | 17.5 | 20.7 | 47.9 | 46.8 | 1.514 | 610
897 | 2022-12-26 14:57 | 17.7 | 20.6 | 48 | 46.3 | 1.488 | 607
898 | 2022-12-26 14:58 | 17.5 | 20.6 | 48 | 46.3 | 1.093 | 603
899 | 2022-12-26 14:59 | 17.8 | 20.6 | 48.2 | 46 | 1.092 | 600
900 | 2022-12-26 15:00 | 18 | 20.6 | 48.5 | 46.1 | 1.1 | 596
901 | 2022-12-26 15:01 | 18 | 20.6 | 48.7 | 46.4 | 1.098 | 593
902 | 2022-12-26 15:02 | 17.7 | 20.6 | 48.8 | 46.6 | 1.091 | 591
903 | 2022-12-26 15:03 | 17.3 | 20.6 | 48.3 | 46.5 | 1.103 | 588
904 | 2022-12-26 15:04 | 17.5 | 20.6 | 48.4 | 46.3 | 1.093 | 584
905 | 2022-12-26 15:05 | 17.3 | 20.6 | 48.2 | 46.2 | 0 | 581
906 | 2022-12-26 15:06 | 17.1 | 20.6 | 48.2 | 46 | 0 | 576
907 | 2022-12-26 15:07 | 17.3 | 20.6 | 48 | 45.6 | 1.099 | 573
908 | 2022-12-26 15:08 | 17.4 | 20.6 | 48 | 46.1 | 1.102 | 569
909 | 2022-12-26 15:09 | 17.5 | 20.5 | 47.8 | 47.4 | 1.507 | 566
910 | 2022-12-26 15:10 | 17.3 | 20.5 | 47.8 | 45.7 | 1.487 | 562
911 | 2022-12-26 15:11 | 17.4 | 20.5 | 47.8 | 46.3 | 1.367 | 558
912 | 2022-12-26 15:12 | 17.2 | 20.4 | 47.8 | 46.4 | 1.061 | 555
913 | 2022-12-26 15:13 | 17 | 20.4 | 47.7 | 46.1 | 0.988 | 551
914 | 2022-12-26 15:14 | 17.2 | 20.5 | 47.7 | 45.8 | 1.504 | 548
915 | 2022-12-26 15:15 | 17 | 20.6 | 47.6 | 40.2 | 1.57 | 545
916 | 2022-12-26 15:16 | 17.3 | 20.6 | 47.4 | 44.5 | 1.565 | 540
917 | 2022-12-26 15:17 | 17.4 | 20.8 | 47 | 45 | 1.572 | 533
918 | 2022-12-26 15:18 | 16.9 | 21.2 | 46.7 | 44.8 | 1.569 | 533
919 | 2022-12-26 15:19 | 17.3 | 21.5 | 46.7 | 44.7 | 1.558 | 530
920 | 2022-12-26 15:20 | 17.2 | 21.7 | 46.7 | 44.7 | 0.964 | 526
921 | 2022-12-26 15:21 | 16.9 | 22 | 46.6 | 44 | 0.959 | 521
922 | 2022-12-26 15:22 | 16.9 | 22.1 | 46.5 | 43.7 | 0.955 | 516
923 | 2022-12-26 15:23 | 16.9 | 22.2 | 46.4 | 43.6 | 0 | 513
924 | 2022-12-26 15:24 | 17.1 | 22.3 | 46.3 | 43.5 | 0.965 | 510
925 | 2022-12-26 15:25 | 17.1 | 21.9 | 46.2 | 45 | 1.235 | 506
926 | 2022-12-26 15:26 | 17.2 | 21.6 | 46.1 | 45.6 | 1.618 | 501
927 | 2022-12-26 15:27 | 16.6 | 21.4 | 45.9 | 44 | 1.526 | 497
928 | 2022-12-26 15:28 | 16.4 | 21.2 | 45.9 | 44.2 | 1.092 | 493
929 | 2022-12-26 15:29 | 16.7 | 21.1 | 45.7 | 44 | 1.095 | 489
930 | 2022-12-26 15:30 | 16.8 | 21 | 45.6 | 43.7 | 1.093 | 485
931 | 2022-12-26 15:31 | 16.6 | 20.9 | 45.5 | 43.7 | 1.09 | 481
932 | 2022-12-26 15:32 | 16.7 | 20.8 | 45.5 | 43.6 | 1.094 | 477
933 | 2022-12-26 15:33 | 16.2 | 20.8 | 45.4 | 43.5 | 1.461 | 473
934 | 2022-12-26 15:34 | 16.1 | 20.7 | 45.2 | 43.3 | 1.516 | 469
935 | 2022-12-26 15:35 | 16.1 | 20.7 | 45 | 42.7 | 1.511 | 465
936 | 2022-12-26 15:36 | 16 | 20.7 | 44.9 | 42.7 | 1.513 | 461
937 | 2022-12-26 15:37 | 16.3 | 20.6 | 44.6 | 42.5 | 1.516 | 457
938 | 2022-12-26 15:38 | 16.6 | 20.6 | 44.6 | 42.3 | 1.512 | 454
939 | 2022-12-26 15:39 | 17 | 20.6 | 44.4 | 43.2 | 1.51 | 449
940 | 2022-12-26 15:40 | 16.7 | 20.6 | 44.3 | 43.2 | 1.508 | 444
941 | 2022-12-26 15:41 | 16.8 | 20.5 | 44.3 | 43.1 | 1.507 | 440
942 | 2022-12-26 15:42 | 16.3 | 20.6 | 44.2 | 43.1 | 1.496 | 435
943 | 2022-12-26 15:43 | 16.2 | 20.5 | 44.2 | 42.9 | 0 | 432
944 | 2022-12-26 15:44 | 15.9 | 20.5 | 44.1 | 42.9 | 0 | 428
945 | 2022-12-26 15:45 | 15.9 | 20.5 | 43.9 | 42.5 | 0 | 424
946 | 2022-12-26 15:46 | 15.9 | 20.4 | 43.6 | 42.1 | 0.933 | 420
947 | 2022-12-26 15:47 | 16.2 | 20.4 | 44 | 41.8 | 0 | 416
948 | 2022-12-26 15:48 | 16.3 | 20.4 | 44 | 42.2 | 0.672 | 411
949 | 2022-12-26 15:49 | 16.3 | 20.5 | 44 | 41.8 | 0.952 | 407
950 | 2022-12-26 15:50 | 16 | 20.5 | 43.8 | 40.8 | 0.957 | 402
951 | 2022-12-26 15:51 | 15.8 | 20.6 | 43.7 | 41 | 0.953 | 398
952 | 2022-12-26 15:52 | 15.6 | 21 | 43.7 | 41.1 | 0.962 | 394
953 | 2022-12-26 15:53 | 15.1 | 21.2 | 43.5 | 41.1 | 0.952 | 388
954 | 2022-12-26 15:54 | 15.2 | 21.4 | 43.3 | 40.8 | 1.143 | 382
955 | 2022-12-26 15:55 | 15.6 | 21.6 | 43.1 | 40.6 | 1.614 | 378
956 | 2022-12-26 15:56 | 15.4 | 21.7 | 42.8 | 39.6 | 1.614 | 374
957 | 2022-12-26 15:57 | 15.5 | 21.8 | 42.6 | 40.2 | 1.625 | 370
958 | 2022-12-26 15:58 | 15.5 | 21.9 | 42.4 | 40.1 | 1.624 | 366
959 | 2022-12-26 15:59 | 15.5 | 22 | 42.4 | 39.9 | 1.626 | 362
960 | 2022-12-26 16:00 | 15.5 | 22.1 | 42.3 | 40.5 | 1.823 | 356
961 | 2022-12-26 16:01 | 15.7 | 21.9 | 42.2 | 39.2 | 1.829 | 351
962 | 2022-12-26 16:02 | 15.2 | 21.6 | 42.1 | 40.3 | 1.834 | 346
963 | 2022-12-26 16:03 | 15.3 | 21.3 | 41.8 | 40.3 | 1.776 | 341
964 | 2022-12-26 16:04 | 15.5 | 21.1 | 41.8 | 40 | 1.501 | 336
965 | 2022-12-26 16:05 | 15.2 | 21 | 41.7 | 39.7 | 1.505 | 331
966 | 2022-12-26 16:06 | 14.7 | 20.9 | 41.6 | 39.6 | 1.507 | 325
967 | 2022-12-26 16:07 | 14.9 | 20.9 | 41.4 | 39.5 | 1.512 | 321
968 | 2022-12-26 16:08 | 15 | 20.8 | 41.3 | 39.4 | 1.506 | 316
969 | 2022-12-26 16:09 | 14.5 | 20.8 | 41.2 | 40.2 | 1.504 | 311
970 | 2022-12-26 16:10 | 14.6 | 20.7 | 41 | 40.1 | 1.506 | 306
971 | 2022-12-26 16:11 | 14.4 | 20.7 | 40.9 | 39.9 | 0 | 301
972 | 2022-12-26 16:12 | 14.4 | 20.7 | 41 | 39.8 | 0 | 296
973 | 2022-12-26 16:13 | 14.3 | 20.6 | 40.9 | 39.7 | 0 | 291
974 | 2022-12-26 16:14 | 14.1 | 20.5 | 40.6 | 39.3 | 0 | 287
975 | 2022-12-26 16:15 | 14.2 | 20.6 | 40.4 | 38.8 | 0 | 282
976 | 2022-12-26 16:16 | 14 | 20.4 | 40.2 | 38.5 | 0 | 277
977 | 2022-12-26 16:17 | 13.9 | 20.4 | 40 | 38.1 | 0 | 272
978 | 2022-12-26 16:18 | 13.7 | 20.4 | 39.7 | 37.8 | 0 | 267
979 | 2022-12-26 16:19 | 13.6 | 20.4 | 39.5 | 37.4 | 0.233 | 262
980 | 2022-12-26 16:20 | 13.4 | 20.3 | 39.4 | 39.6 | 0.957 | 257
981 | 2022-12-26 16:21 | 13.2 | 20.3 | 40.7 | 35.1 | 0.999 | 248
982 | 2022-12-26 16:22 | 13.2 | 20.4 | 40.4 | 38.2 | 1.539 | 233
983 | 2022-12-26 16:23 | 13.3 | 20.5 | 40.3 | 37.1 | 1.545 | 241
984 | 2022-12-26 16:24 | 13.3 | 20.7 | 39.7 | 37.3 | 1.877 | 238
985 | 2022-12-26 16:25 | 13.2 | 21.1 | 39.6 | 35.1 | 1.883 | 232
986 | 2022-12-26 16:26 | 13.2 | 21.3 | 39.5 | 36.7 | 1.886 | 228
987 | 2022-12-26 16:27 | 13.2 | 21.6 | 39.2 | 36.6 | 1.982 | 222
988 | 2022-12-26 16:28 | 12.8 | 21.8 | 39 | 37.2 | 1.997 | 217
989 | 2022-12-26 16:29 | 12.8 | 22 | 38.9 | 36.6 | 1.991 | 211
990 | 2022-12-26 16:30 | 12.8 | 22 | 38.8 | 36.6 | 1.82 | 206
991 | 2022-12-26 16:31 | 12.4 | 22.1 | 38.6 | 36.9 | 1.823 | 201
992 | 2022-12-26 16:32 | 12.1 | 21.8 | 38.5 | 37 | 1.823 | 195
993 | 2022-12-26 16:33 | 12.2 | 21.6 | 38.3 | 36.9 | 1.812 | 189
994 | 2022-12-26 16:34 | 11.9 | 21.3 | 38.5 | 36.8 | 1.652 | 185
995 | 2022-12-26 16:35 | 12.3 | 21.1 | 38.8 | 36.8 | 1.503 | 181
996 | 2022-12-26 16:36 | 12.1 | 20.9 | 39.2 | 37.1 | 1.502 | 176
997 | 2022-12-26 16:37 | 12.1 | 20.8 | 39.6 | 37.4 | 1.507 | 157
998 | 2022-12-26 16:38 | 12.1 | 20.8 | 39.9 | 37.8 | 1.501 | 108
999 | 2022-12-26 16:39 | 12.1 | 20.6 | 40.2 | 38.1 | 1.504 | 58
1000 | 2022-12-26 16:40 | 11.9 | 20.7 | 40.6 | 38.4 | 1.501 | 40
1001 | 2022-12-26 16:41 | 11.9 | 20.6 | 40.9 | 38.7 | 1.51 | 20
1002 | 2022-12-26 16:42 | 11.8 | 20.6 | 41.2 | 39 | 1.506 | 16
1003 | 2022-12-26 16:43 | 11.6 | 20.5 | 41.7 | 39.2 | 1.505 | 16
1004 | 2022-12-26 16:44 | 11.6 | 20.5 | 41.9 | 40.2 | 0 | 15
1005 | 2022-12-26 16:45 | 11.4 | 20.5 | 41.8 | 40.2 | 0 | 13
1006 | 2022-12-26 16:46 | 11.7 | 20.5 | 41.5 | 39.7 | 0 | 13
1007 | 2022-12-26 16:47 | 11.6 | 20.5 | 41.3 | 39.2 | 0 | 13
1008 | 2022-12-26 16:48 | 11.9 | 20.5 | 41 | 38.8 | 0 | 12
1009 | 2022-12-26 16:49 | 11.6 | 20.4 | 40.7 | 38.4 | 0.838 | 11
1010 | 2022-12-26 16:50 | 11.8 | 20.4 | 42.7 | 38.7 | 0.232 | 11
1011 | 2022-12-26 16:51 | 11.7 | 20.4 | 42.8 | 40.3 | 0.778 | 10
1012 | 2022-12-26 16:52 | 11.3 | 20.5 | 42.9 | 39 | 0.953 | 9
1013 | 2022-12-26 16:53 | 11.4 | 20.4 | 42.2 | 39.5 | 0.956 | 9
1014 | 2022-12-26 16:54 | 11.3 | 20.6 | 42.4 | 39.8 | 0.955 | 9
1015 | 2022-12-26 16:55 | 11.2 | 20.9 | 42.4 | 39.8 | 0.954 | 9
1016 | 2022-12-26 16:56 | 11.3 | 21.2 | 42.2 | 39.9 | 0.956 | 8
1017 | 2022-12-26 16:57 | 11.3 | 21.4 | 42 | 39.7 | 0.955 | 7
1018 | 2022-12-26 16:58 | 10.9 | 21.5 | 41.9 | 39.5 | 1.623 | 7
1019 | 2022-12-26 16:59 | 10.8 | 21.6 | 41.6 | 38.1 | 1.828 | 6
1020 | 2022-12-26 17:00 | 10.7 | 21.6 | 41.5 | 38.5 | 1.827 | 5
1021 | 2022-12-26 17:01 | 10.7 | 21.7 | 41.3 | 38.6 | 1.827 | 5
1022 | 2022-12-26 17:02 | 10.7 | 21.9 | 41.3 | 38.5 | 1.823 | 4
1023 | 2022-12-26 17:03 | 10.6 | 22 | 41.2 | 38.5 | 1.826 | 4
1024 | 2022-12-26 17:04 | 10.4 | 22.1 | 41 | 38.5 | 1.833 | 3
1025 | 2022-12-26 17:05 | 10.6 | 21.9 | 40.8 | 39.2 | 1.831 | 3
1026 | 2022-12-26 17:06 | 10.6 | 21.6 | 40.7 | 39 | 1.823 | 2
1027 | 2022-12-26 17:07 | 11.3 | 21.3 | 40.7 | 38.9 | 1.781 | 2
1028 | 2022-12-26 17:08 | 11.2 | 21.1 | 40.6 | 38.9 | 1.506 | 2
1029 | 2022-12-26 17:09 | 10.9 | 21 | 40.4 | 38.5 | 1.508 | 1
1030 | 2022-12-26 17:10 | 10.6 | 20.9 | 40.3 | 38.5 | 1.504 | 1
1031 | 2022-12-26 17:11 | 10.7 | 20.8 | 40.2 | 38.3 | 1.508 | 1
1032 | 2022-12-26 17:12 | 10.7 | 20.8 | 40 | 38.6 | 1.506 | 0
1033 | 2022-12-26 17:13 | 10.5 | 20.8 | 40 | 38.8 | 1.498 | 0
1034 | 2022-12-26 17:14 | 10.3 | 20.7 | 39.9 | 38.7 | 1.498 | 0
1035 | 2022-12-26 17:15 | 10 | 20.6 | 39.8 | 38.6 | 1.342 | 0
1036 | 2022-12-26 17:16 | 10 | 20.6 | 39.7 | 38.5 | 1.091 | 0
1037 | 2022-12-26 17:17 | 9.9 | 20.6 | 39.7 | 38.2 | 1.462 | 0
1038 | 2022-12-26 17:18 | 9.8 | 20.5 | 39.6 | 36.5 | 1.63 | 0
1039 | 2022-12-26 17:19 | 9.9 | 20.5 | 39.6 | 37.2 | 1.631 | 0
1040 | 2022-12-26 17:20 | 9.6 | 20.4 | 39.3 | 38 | 1.622 | 0
1041 | 2022-12-26 17:21 | 9.5 | 20.1 | 38.9 | 37.8 | 1.631 | 0
1042 | 2022-12-26 17:22 | 9.5 | 20.5 | 38.9 | 37.6 | 1.624 | 0
1043 | 2022-12-26 17:23 | 9.5 | 20.3 | 38.9 | 37.5 | 1.608 | 0
1044 | 2022-12-26 17:24 | 9.5 | 20.3 | 38.8 | 37.5 | 1.465 | 0
1045 | 2022-12-26 17:25 | 9.3 | 17.3 | 38.7 | 37.3 | 1.073 | 0
1046 | 2022-12-26 17:26 | 9.2 | 17.5 | 38.7 | 38.1 | 1.556 | 0
1047 | 2022-12-26 17:27 | 9.3 | 20.7 | 38.6 | 36.9 | 1.571 | 0
1048 | 2022-12-26 17:28 | 9.3 | 20.6 | 38.5 | 37.6 | 1.529 | 0
1049 | 2022-12-26 17:29 | 9.1 | 20.4 | 38.4 | 37.5 | 0.988 | 0
1050 | 2022-12-26 17:30 | 9.1 | 20.5 | 38.4 | 37.1 | 0.974 | 0
1051 | 2022-12-26 17:31 | 9.1 | 20.4 | 38.4 | 37.1 | 0.968 | 0
1052 | 2022-12-26 17:32 | 9.1 | 20.5 | 38.2 | 37 | 1.124 | 0
1053 | 2022-12-26 17:33 | 8.9 | 20.4 | 38.1 | 36.9 | 1.543 | 0
1054 | 2022-12-26 17:34 | 8.9 | 20.4 | 38.2 | 35.7 | 1.7 | 0
1055 | 2022-12-26 17:35 | 8.7 | 20.6 | 38.5 | 36.2 | 1.817 | 0
1056 | 2022-12-26 17:36 | 8.6 | 20.6 | 38.7 | 35.9 | 1.823 | 0
1057 | 2022-12-26 17:37 | 8.6 | 21 | 39.1 | 36.3 | 1.824 | 0
1058 | 2022-12-26 17:38 | 8.6 | 21.3 | 39.3 | 36.6 | 1.828 | 0
1059 | 2022-12-26 17:39 | 8.4 | 21.4 | 39.7 | 36.8 | 1.822 | 0
1060 | 2022-12-26 17:40 | 8.6 | 21.6 | 39.9 | 37.2 | 1.82 | 0
1061 | 2022-12-26 17:41 | 8.6 | 21.6 | 40.3 | 37.4 | 1.831 | 0
1062 | 2022-12-26 17:42 | 8.5 | 21.8 | 40.6 | 37.7 | 1.824 | 0
1063 | 2022-12-26 17:43 | 8.4 | 21.9 | 40.8 | 38 | 1.835 | 0
1064 | 2022-12-26 17:44 | 8.5 | 22.1 | 41.2 | 38.7 | 1.827 | 0
1065 | 2022-12-26 17:45 | 8.3 | 21.9 | 41.5 | 39.7 | 1.827 | 0
1066 | 2022-12-26 17:46 | 8.4 | 21.8 | 41.7 | 40.3 | 1.777 | 0
1067 | 2022-12-26 17:47 | 8.1 | 21.4 | 41.7 | 40.5 | 1.606 | 0
1068 | 2022-12-26 17:48 | 8.2 | 21.3 | 41.8 | 40.4 | 1.432 | 0
1069 | 2022-12-26 17:49 | 8.1 | 21.1 | 41.7 | 40.3 | 1.096 | 0
1070 | 2022-12-26 17:50 | 8 | 21 | 41.6 | 40 | 1.093 | 0
1071 | 2022-12-26 17:51 | 8 | 20.9 | 41.7 | 39.9 | 1.088 | 0
1072 | 2022-12-26 17:52 | 8.1 | 20.8 | 41.6 | 40 | 0 | 0
1073 | 2022-12-26 17:53 | 8.1 | 20.8 | 41.5 | 39.9 | 0 | 0
1074 | 2022-12-26 17:54 | 8 | 20.7 | 41.2 | 39.6 | 0 | 0
1075 | 2022-12-26 17:55 | 7.8 | 20.2 | 41 | 39.1 | 0 | 0
1076 | 2022-12-26 17:56 | 8 | 19.7 | 40.7 | 38.6 | 1.076 | 0
1077 | 2022-12-26 17:57 | 7.8 | 19.2 | 41.1 | 38.5 | 0.978 | 0
1078 | 2022-12-26 17:58 | 7.8 | 19.1 | 40.9 | 40.7 | 1.244 | 0
1079 | 2022-12-26 17:59 | 7.8 | 19.1 | 40.9 | 38.5 | 0.978 | 0
1080 | 2022-12-26 18:00 | 7.7 | 19.3 | 40.9 | 39.3 | 0.977 | 0
1081 | 2022-12-26 18:01 | 7.6 | 19.6 | 40.9 | 39.3 | 0.973 | 0
1082 | 2022-12-26 18:02 | 7.7 | 19.7 | 40.9 | 39.4 | 1.55 | 0
1083 | 2022-12-26 18:03 | 7.6 | 20.2 | 40.8 | 36 | 1.572 | 0
1084 | 2022-12-26 18:04 | 7.6 | 20.3 | 40.6 | 38.3 | 1.835 | 0
1085 | 2022-12-26 18:05 | 7.6 | 20.5 | 40.3 | 36.4 | 1.851 | 0
1086 | 2022-12-26 18:06 | 7.8 | 20.5 | 40.2 | 37.3 | 1.948 | 0
1087 | 2022-12-26 18:07 | 7.8 | 20.9 | 39.9 | 37.3 | 1.998 | 0
1088 | 2022-12-26 18:08 | 7.6 | 21.1 | 39.7 | 36.5 | 1.996 | 0
1089 | 2022-12-26 18:09 | 7.4 | 20.4 | 39.4 | 36.4 | 1.993 | 0
1090 | 2022-12-26 18:10 | 7.5 | 20.4 | 39.1 | 36.4 | 1.988 | 0
1091 | 2022-12-26 18:11 | 7.4 | 20.4 | 38.9 | 36.7 | 1.992 | 0
1092 | 2022-12-26 18:12 | 7.5 | 20.4 | 38.8 | 36.6 | 1.985 | 0
1093 | 2022-12-26 18:13 | 7.5 | 20.4 | 38.6 | 36.5 | 1.835 | 0
1094 | 2022-12-26 18:14 | 7.3 | 20.4 | 38.5 | 36.9 | 1.825 | 0
1095 | 2022-12-26 18:15 | 7.3 | 21.6 | 38.3 | 37.4 | 1.816 | 0
1096 | 2022-12-26 18:16 | 7.4 | 21.6 | 38.3 | 37.3 | 1.772 | 0
1097 | 2022-12-26 18:17 | 7.4 | 21.6 | 38.3 | 37.3 | 1.482 | 0
1098 | 2022-12-26 18:18 | 7.3 | 20.9 | 38.2 | 37.1 | 1.089 | 0
1099 | 2022-12-26 18:19 | 7.5 | 20.8 | 38.1 | 36.9 | 1.089 | 0
1100 | 2022-12-26 18:20 | 7.3 | 20.8 | 38.1 | 36.7 | 1.082 | 0
1101 | 2022-12-26 18:21 | 7.4 | 20.8 | 38 | 36.6 | 1.081 | 0
1102 | 2022-12-26 18:22 | 7.4 | 20.7 | 37.9 | 36.5 | 1.082 | 0
1103 | 2022-12-26 18:23 | 7.3 | 20.6 | 37.8 | 36.5 | 1.088 | 0
1104 | 2022-12-26 18:24 | 7.2 | 20.6 | 37.8 | 36.4 | 1.082 | 0
1105 | 2022-12-26 18:25 | 7.3 | 20.5 | 37.7 | 36.4 | 1.085 | 0
1106 | 2022-12-26 18:26 | 7.3 | 20.5 | 37.5 | 36.2 | 1.086 | 0
1107 | 2022-12-26 18:27 | 7.3 | 20.5 | 37.5 | 36.1 | 1.086 | 0
1108 | 2022-12-26 18:28 | 7.2 | 20.4 | 37.4 | 36.1 | 1.176 | 0
1109 | 2022-12-26 18:29 | 7.3 | 20.4 | 37.3 | 36 | 1.5 | 0
1110 | 2022-12-26 18:30 | 7.2 | 20.4 | 37.3 | 35.5 | 1.498 | 0
1111 | 2022-12-26 18:31 | 7.3 | 20.4 | 37.2 | 35.5 | 1.498 | 0
1112 | 2022-12-26 18:32 | 7.1 | 20.4 | 36.9 | 35.5 | 1.503 | 0
1113 | 2022-12-26 18:33 | 7.1 | 20.4 | 36.9 | 35.2 | 1.495 | 0
1114 | 2022-12-26 18:34 | 7 | 20.5 | 37.2 | 35.3 | 1.789 | 0
1115 | 2022-12-26 18:35 | 7.3 | 20.6 | 37.7 | 33.4 | 1.822 | 0
1116 | 2022-12-26 18:36 | 7 | 20.6 | 38.1 | 35.3 | 1.956 | 0
1117 | 2022-12-26 18:37 | 7.2 | 20.7 | 38.2 | 35 | 1.989 | 0
1118 | 2022-12-26 18:38 | 7 | 21 | 38.5 | 35.1 | 1.983 | 0
1119 | 2022-12-26 18:39 | 7 | 21.2 | 38.7 | 35.4 | 1.992 | 0
1120 | 2022-12-26 18:40 | 6.9 | 21.5 | 38.8 | 35.6 | 1.989 | 0
1121 | 2022-12-26 18:41 | 7.2 | 21.6 | 39.2 | 35.7 | 1.988 | 0
1122 | 2022-12-26 18:42 | 7 | 21.8 | 39.4 | 36.4 | 1.996 | 0
1123 | 2022-12-26 18:43 | 7 | 21.9 | 39.7 | 36.9 | 1.993 | 0
1124 | 2022-12-26 18:44 | 7.2 | 21.9 | 40 | 37.1 | 1.998 | 0
1125 | 2022-12-26 18:45 | 7.3 | 21.9 | 40.3 | 38.5 | 1.99 | 0
1126 | 2022-12-26 18:46 | 7.2 | 21.8 | 40.6 | 39.3 | 1.98 | 0
1127 | 2022-12-26 18:47 | 7.2 | 21.5 | 41.1 | 39.7 | 0 | 0
1128 | 2022-12-26 18:48 | 7.2 | 21.3 | 41.3 | 39.8 | 0 | 0
1129 | 2022-12-26 18:49 | 7.3 | 21 | 41 | 39.3 | 0 | 0
1130 | 2022-12-26 18:50 | 7.2 | 20.8 | 40.6 | 38.6 | 0 | 0
1131 | 2022-12-26 18:51 | 7.2 | 20.7 | 40.4 | 38.1 | 0 | 0
1132 | 2022-12-26 18:52 | 7 | 20.6 | 40.1 | 37.5 | 0 | 0
1133 | 2022-12-26 18:53 | 7.1 | 20.5 | 39.8 | 37 | 0 | 0
1134 | 2022-12-26 18:54 | 7.1 | 20.4 | 39.5 | 36.5 | 0 | 0
1135 | 2022-12-26 18:55 | 7 | 20.4 | 39.2 | 36 | 0 | 0
1136 | 2022-12-26 18:56 | 7.2 | 20.3 | 38.9 | 37.2 | 0.475 | 0
1137 | 2022-12-26 18:57 | 7 | 20.2 | 40.3 | 37.4 | 1.081 | 0
1138 | 2022-12-26 18:58 | 7.2 | 20.3 | 41.1 | 38.2 | 1.089 | 0
1139 | 2022-12-26 18:59 | 7 | 20.2 | 40.6 | 39.2 | 1.094 | 0
1140 | 2022-12-26 19:00 | 7 | 20.2 | 40.7 | 39 | 1.096 | 0
1141 | 2022-12-26 19:01 | 7.1 | 20.2 | 40.6 | 39 | 1.687 | 0
1142 | 2022-12-26 19:02 | 7.1 | 20.4 | 40.5 | 37 | 1.826 | 0
1143 | 2022-12-26 19:03 | 7.1 | 20.5 | 40.6 | 37.5 | 1.826 | 0
1144 | 2022-12-26 19:04 | 7 | 20.6 | 40.7 | 37.8 | 1.831 | 0
1145 | 2022-12-26 19:05 | 6.8 | 20.9 | 40.9 | 37.9 | 1.829 | 0
1146 | 2022-12-26 19:06 | 6.8 | 21.1 | 41.3 | 38.2 | 1.835 | 0
1147 | 2022-12-26 19:07 | 6.8 | 21.4 | 41.5 | 38.5 | 1.824 | 0
1148 | 2022-12-26 19:08 | 6.9 | 21.6 | 41.8 | 38.7 | 1.826 | 0
1149 | 2022-12-26 19:09 | 7.1 | 21.7 | 42 | 39 | 1.827 | 0
1150 | 2022-12-26 19:10 | 6.9 | 21.9 | 42.3 | 39.2 | 1.833 | 0
1151 | 2022-12-26 19:11 | 6.9 | 21.9 | 42.6 | 39.4 | 1.834 | 0
1152 | 2022-12-26 19:12 | 6.9 | 22 | 42.9 | 39.7 | 1.835 | 0
1153 | 2022-12-26 19:13 | 6.9 | 22 | 43.1 | 39.9 | 1.835 | 0
1154 | 2022-12-26 19:14 | 7.2 | 21.9 | 43.3 | 41.2 | 1.83 | 0
1155 | 2022-12-26 19:15 | 7.3 | 21.7 | 43.8 | 41.5 | 0 | 0
1156 | 2022-12-26 19:16 | 7 | 21.3 | 43.8 | 41.8 | 0 | 0
1157 | 2022-12-26 19:17 | 7.2 | 21.1 | 43.5 | 41.2 | 0 | 0
1158 | 2022-12-26 19:18 | 6.9 | 21 | 43.2 | 40.6 | 0 | 0
1159 | 2022-12-26 19:19 | 7 | 20.8 | 42.9 | 40 | 0 | 0
1160 | 2022-12-26 19:20 | 7.1 | 20.8 | 42.6 | 39.4 | 0 | 0
1161 | 2022-12-26 19:21 | 6.9 | 20.6 | 42.2 | 38.9 | 0 | 0
1162 | 2022-12-26 19:22 | 7.1 | 20.5 | 41.9 | 38.4 | 0 | 0
1163 | 2022-12-26 19:23 | 6.9 | 20.4 | 41.6 | 38.1 | 0 | 0
1164 | 2022-12-26 19:24 | 7.1 | 20.3 | 41.3 | 37.5 | 0.058 | 0
1165 | 2022-12-26 19:25 | 7.1 | 20.3 | 41.4 | 40 | 0.97 | 0
1166 | 2022-12-26 19:26 | 6.9 | 20.3 | 45.7 | 39.8 | 1.24 | 0
1167 | 2022-12-26 19:27 | 6.9 | 20.3 | 45.1 | 42.4 | 1.635 | 0
1168 | 2022-12-26 19:28 | 7 | 20.3 | 45 | 41 | 1.632 | 0
1169 | 2022-12-26 19:29 | 7.2 | 20.4 | 44.7 | 42 | 1.633 | 0
1170 | 2022-12-26 19:30 | 7 | 20.4 | 44.4 | 41.8 | 1.84 | 0
1171 | 2022-12-26 19:31 | 6.8 | 20.6 | 44.5 | 40.2 | 1.843 | 0
1172 | 2022-12-26 19:32 | 6.9 | 20.6 | 44.5 | 42.4 | 1.843 | 0
1173 | 2022-12-26 19:33 | 6.8 | 20.6 | 44.3 | 42.4 | 1.841 | 0
1174 | 2022-12-26 19:34 | 6.9 | 20.8 | 44.4 | 42.3 | 1.67 | 0
1175 | 2022-12-26 19:35 | 6.7 | 20.6 | 44.3 | 42.1 | 1.51 | 0
1176 | 2022-12-26 19:36 | 6.9 | 20.6 | 44.1 | 41.9 | 1.514 | 0
1177 | 2022-12-26 19:37 | 6.9 | 20.7 | 44 | 41.8 | 1.509 | 0
1178 | 2022-12-26 19:38 | 6.9 | 20.5 | 43.8 | 41.7 | 1.509 | 0
1179 | 2022-12-26 19:39 | 6.8 | 20.5 | 43.7 | 41.5 | 1.51 | 0
1180 | 2022-12-26 19:40 | 6.9 | 20.7 | 43.5 | 41.4 | 1.772 | 0
1181 | 2022-12-26 19:41 | 6.8 | 20.7 | 43.3 | 38.8 | 1.828 | 0
1182 | 2022-12-26 19:42 | 6.8 | 20.6 | 43.1 | 40.1 | 1.833 | 0
1183 | 2022-12-26 19:43 | 6.7 | 20.9 | 42.8 | 40.8 | 1.836 | 0
1184 | 2022-12-26 19:44 | 6.7 | 21.1 | 42.5 | 41.1 | 1.827 | 0
1185 | 2022-12-26 19:45 | 6.6 | 21.3 | 42.6 | 41 | 1.816 | 0
1186 | 2022-12-26 19:46 | 6.6 | 21.5 | 42.5 | 41 | 1.61 | 0
1187 | 2022-12-26 19:47 | 6.7 | 21.6 | 42.4 | 40.8 | 1.568 | 0
1188 | 2022-12-26 19:48 | 6.7 | 21.6 | 42.3 | 40.7 | 1.475 | 0
1189 | 2022-12-26 19:49 | 6.5 | 21.6 | 42.2 | 40.5 | 0.991 | 0
1190 | 2022-12-26 19:50 | 6.5 | 21.7 | 42 | 39.9 | 0.95 | 0
1191 | 2022-12-26 19:51 | 6.7 | 21.8 | 42 | 39.5 | 0.951 | 0
1192 | 2022-12-26 19:52 | 6.6 | 21.7 | 41.9 | 39.5 | 0.952 | 0
1193 | 2022-12-26 19:53 | 6.5 | 21.8 | 41.8 | 39.4 | 0.953 | 0
1194 | 2022-12-26 19:54 | 6.6 | 21.8 | 41.6 | 39.3 | 0.955 | 0
1195 | 2022-12-26 19:55 | 6.6 | 21.8 | 41.4 | 39.1 | 0.95 | 0
1196 | 2022-12-26 19:56 | 6.5 | 21.7 | 41.3 | 40.9 | 1.529 | 0
1197 | 2022-12-26 19:57 | 6.7 | 21.3 | 41.2 | 39.9 | 1.559 | 0
1198 | 2022-12-26 19:58 | 6.9 | 20.9 | 41.1 | 40 | 1.52 | 0
1199 | 2022-12-26 19:59 | 6.7 | 20.7 | 41.3 | 40 | 1.54 | 0
1200 | 2022-12-26 20:00 | 6.7 | 20.6 | 41 | 38.1 | 1.51 | 0
1201 | 2022-12-26 20:01 | 6.8 | 20.5 | 41 | 39 | 1.503 | 0
1202 | 2022-12-26 20:02 | 6.5 | 20.5 | 40.8 | 38.9 | 1.501 | 0
1203 | 2022-12-26 20:03 | 6.6 | 20.5 | 40.6 | 38.7 | 1.5 | 0
1204 | 2022-12-26 20:04 | 6.7 | 20.5 | 40.7 | 38.6 | 1.501 | 0
1205 | 2022-12-26 20:05 | 6.5 | 20.4 | 40.9 | 38.7 | 1.503 | 0
1206 | 2022-12-26 20:06 | 6.8 | 20.3 | 41.3 | 39 | 1.511 | 0
1207 | 2022-12-26 20:07 | 6.6 | 20.5 | 41.7 | 39.3 | 1.502 | 0
1208 | 2022-12-26 20:08 | 6.7 | 20.5 | 42 | 39.7 | 1.798 | 0
1209 | 2022-12-26 20:09 | 6.7 | 20.5 | 42.3 | 36.9 | 1.838 | 0
1210 | 2022-12-26 20:10 | 6.8 | 20.4 | 42.7 | 39.3 | 1.837 | 0
1211 | 2022-12-26 20:11 | 6.8 | 20.4 | 42.7 | 40 | 1.838 | 0
1212 | 2022-12-26 20:12 | 6.6 | 20.6 | 43 | 40.3 | 1.84 | 0
1213 | 2022-12-26 20:13 | 6.7 | 20.7 | 43.4 | 40.8 | 1.834 | 0
1214 | 2022-12-26 20:14 | 6.7 | 20.7 | 43.7 | 41 | 1.752 | 0
1215 | 2022-12-26 20:15 | 6.8 | 20.8 | 44 | 41.3 | 1.64 | 0
1216 | 2022-12-26 20:16 | 6.8 | 20.8 | 43.9 | 42.5 | 1.639 | 0
1217 | 2022-12-26 20:17 | 6.6 | 20.8 | 43.9 | 42.5 | 1.625 | 0
1218 | 2022-12-26 20:18 | 6.6 | 20.8 | 43.9 | 42.5 | 0 | 0
1219 | 2022-12-26 20:19 | 6.7 | 20.7 | 43.9 | 42.4 | 0 | 0
1220 | 2022-12-26 20:20 | 6.5 | 20.7 | 43.6 | 41.9 | 0 | 0
1221 | 2022-12-26 20:21 | 6.5 | 20.6 | 43.3 | 41.3 | 0 | 0
1222 | 2022-12-26 20:22 | 6.6 | 20.6 | 43 | 40.7 | 1.083 | 0
1223 | 2022-12-26 20:23 | 6.6 | 20.5 | 43.5 | 40.8 | 1.002 | 0
1224 | 2022-12-26 20:24 | 6.5 | 20.4 | 43.5 | 42.9 | 0.731 | 0
1225 | 2022-12-26 20:25 | 6.7 | 20.5 | 43.1 | 43.1 | 0.934 | 0
1226 | 2022-12-26 20:26 | 6.6 | 20.4 | 43.3 | 38.1 | 1.547 | 0
1227 | 2022-12-26 20:27 | 6.5 | 20.5 | 43.3 | 38.3 | 1.56 | 0
1228 | 2022-12-26 20:28 | 6.4 | 20.6 | 43.2 | 40.6 | 1.565 | 0
1229 | 2022-12-26 20:29 | 6.4 | 20.9 | 42.7 | 40.5 | 1.565 | 0
1230 | 2022-12-26 20:30 | 6.7 | 21.1 | 42.6 | 40.2 | 1.559 | 0
1231 | 2022-12-26 20:31 | 6.7 | 21.3 | 42.6 | 40.1 | 1.56 | 0
1232 | 2022-12-26 20:32 | 6.6 | 21.4 | 42.4 | 40.1 | 1.727 | 0
1233 | 2022-12-26 20:33 | 6.8 | 21.5 | 42.3 | 39.9 | 1.828 | 0
1234 | 2022-12-26 20:34 | 6.5 | 21.7 | 42.1 | 39.2 | 1.825 | 0
1235 | 2022-12-26 20:35 | 6.7 | 21.8 | 41.9 | 39.2 | 1.829 | 0
1236 | 2022-12-26 20:36 | 6.4 | 21.8 | 41.6 | 38.9 | 1.827 | 0
1237 | 2022-12-26 20:37 | 6.5 | 21.9 | 41.4 | 38.7 | 1.828 | 0
1238 | 2022-12-26 20:38 | 6.6 | 21.9 | 41.2 | 38.5 | 1.828 | 0
1239 | 2022-12-26 20:39 | 6.5 | 22 | 40.9 | 38.5 | 1.828 | 0
1240 | 2022-12-26 20:40 | 6.5 | 21.8 | 40.8 | 39.5 | 1.826 | 0
1241 | 2022-12-26 20:41 | 6.5 | 21.6 | 40.7 | 39.6 | 1.823 | 0
1242 | 2022-12-26 20:42 | 6.6 | 21.3 | 40.7 | 39.5 | 1.783 | 0
1243 | 2022-12-26 20:43 | 6.6 | 21.1 | 40.7 | 39.5 | 1.178 | 0
1244 | 2022-12-26 20:44 | 6.5 | 21 | 40.6 | 39.3 | 1.089 | 0
1245 | 2022-12-26 20:45 | 6.8 | 20.9 | 40.5 | 39 | 1.086 | 0
1246 | 2022-12-26 20:46 | 6.7 | 20.8 | 40.4 | 38.8 | 1.089 | 0
1247 | 2022-12-26 20:47 | 6.6 | 20.8 | 40.4 | 38.8 | 1.089 | 0
1248 | 2022-12-26 20:48 | 6.6 | 20.8 | 40.3 | 38.8 | 1.089 | 0
1249 | 2022-12-26 20:49 | 6.5 | 20.6 | 40.1 | 38.7 | 1.088 | 0
1250 | 2022-12-26 20:50 | 6.5 | 20.6 | 40.1 | 38.5 | 1.09 | 0
1251 | 2022-12-26 20:51 | 6.5 | 20.6 | 39.9 | 38.4 | 1.087 | 0
1252 | 2022-12-26 20:52 | 6.6 | 20.5 | 39.9 | 38.3 | 1.089 | 0
1253 | 2022-12-26 20:53 | 6.6 | 20.5 | 39.7 | 38.2 | 1.613 | 0
1254 | 2022-12-26 20:54 | 6.5 | 20.5 | 39.7 | 36.4 | 1.806 | 0
1255 | 2022-12-26 20:55 | 6.4 | 20.5 | 39.5 | 37.3 | 1.835 | 0
1256 | 2022-12-26 20:56 | 6.6 | 20.5 | 39.2 | 36.8 | 1.827 | 0
1257 | 2022-12-26 20:57 | 6.6 | 20.6 | 39.1 | 37.1 | 1.836 | 0
1258 | 2022-12-26 20:58 | 6.5 | 20.7 | 38.8 | 37.1 | 1.838 | 0
1259 | 2022-12-26 20:59 | 6.4 | 20.7 | 38.7 | 36.9 | 0 | 0
1260 | 2022-12-26 21:00 | 6.5 | 20.7 | 38.7 | 36.9 | 0 | 0
1261 | 2022-12-26 21:01 | 6.5 | 20.7 | 38.5 | 36.5 | 0 | 0
1262 | 2022-12-26 21:02 | 6.6 | 20.6 | 38.2 | 36 | 0 | 0
1263 | 2022-12-26 21:03 | 6.4 | 20.5 | 38 | 35.5 | 0 | 0
1264 | 2022-12-26 21:04 | 6.6 | 20.4 | 37.7 | 35 | 0 | 0
1265 | 2022-12-26 21:05 | 6.4 | 20.4 | 37.5 | 34.6 | 0 | 0
1266 | 2022-12-26 21:06 | 6.5 | 20.3 | 37.2 | 34.1 | 0 | 0
1267 | 2022-12-26 21:07 | 6.4 | 20.3 | 37 | 33.7 | 0 | 0
1268 | 2022-12-26 21:08 | 6.4 | 20.2 | 36.7 | 33.3 | 0 | 0
1269 | 2022-12-26 21:09 | 6.3 | 20.1 | 36.5 | 32.9 | 0 | 0
1270 | 2022-12-26 21:10 | 6.4 | 20.1 | 36.2 | 32.6 | 0 | 0
1271 | 2022-12-26 21:11 | 6.5 | 20.1 | 36 | 32.2 | 0 | 0
1272 | 2022-12-26 21:12 | 6.5 | 20.1 | 35.8 | 31.9 | 0 | 0
1273 | 2022-12-26 21:13 | 6.4 | 20.1 | 35.5 | 31.5 | 0 | 0
1274 | 2022-12-26 21:14 | 6.3 | 20 | 35.3 | 31.2 | 0 | 0
1275 | 2022-12-26 21:15 | 6.5 | 20 | 35 | 30.9 | 0 | 0
1276 | 2022-12-26 21:16 | 6.3 | 20 | 34.8 | 30.6 | 0 | 0
1277 | 2022-12-26 21:17 | 6.3 | 20 | 34.6 | 30.3 | 0 | 0
1278 | 2022-12-26 21:18 | 6.3 | 20 | 34.3 | 30 | 0 | 0
1279 | 2022-12-26 21:19 | 6.4 | 20 | 34.1 | 29.7 | 0 | 0
1280 | 2022-12-26 21:20 | 6.6 | 19.9 | 33.9 | 29.4 | 0 | 0
1281 | 2022-12-26 21:21 | 6.6 | 20 | 33.7 | 29.2 | 0 | 0
1282 | 2022-12-26 21:22 | 6.4 | 19.9 | 33.4 | 28.9 | 0 | 0
1283 | 2022-12-26 21:23 | 6.3 | 19.9 | 33.2 | 28.6 | 0 | 0
1284 | 2022-12-26 21:24 | 6.4 | 19.9 | 33 | 28.4 | 0 | 0
1285 | 2022-12-26 21:25 | 6.4 | 19.9 | 32.8 | 28.1 | 0 | 0
1286 | 2022-12-26 21:26 | 6.3 | 19.9 | 32.6 | 27.9 | 0 | 0
1287 | 2022-12-26 21:27 | 6.5 | 19.9 | 32.3 | 27.6 | 0 | 0
1288 | 2022-12-26 21:28 | 6.4 | 19.8 | 32.1 | 27.4 | 0 | 0
1289 | 2022-12-26 21:29 | 6.5 | 19.8 | 31.9 | 27.2 | 0 | 0
1290 | 2022-12-26 21:30 | 6.3 | 19.8 | 31.7 | 27 | 0 | 0
1291 | 2022-12-26 21:31 | 6.4 | 19.9 | 31.5 | 26.7 | 0 | 0
1292 | 2022-12-26 21:32 | 6.4 | 19.9 | 31.3 | 26.5 | 0 | 0
1293 | 2022-12-26 21:33 | 6.3 | 19.8 | 31.1 | 26.3 | 0 | 0
1294 | 2022-12-26 21:34 | 6.4 | 19.8 | 30.9 | 26.1 | 0 | 0
1295 | 2022-12-26 21:35 | 6.4 | 19.8 | 30.7 | 25.9 | 0 | 0
1296 | 2022-12-26 21:36 | 6.4 | 19.8 | 30.5 | 25.7 | 0 | 0
1297 | 2022-12-26 21:37 | 6.6 | 19.8 | 30.3 | 25.5 | 0 | 0
1298 | 2022-12-26 21:38 | 6.4 | 19.8 | 30.1 | 25.3 | 0 | 0
1299 | 2022-12-26 21:39 | 6.5 | 19.8 | 29.9 | 25.1 | 0 | 0
1300 | 2022-12-26 21:40 | 6.5 | 19.7 | 29.7 | 25 | 0 | 0
1301 | 2022-12-26 21:41 | 6.4 | 19.7 | 29.5 | 24.8 | 0 | 0
1302 | 2022-12-26 21:42 | 6.5 | 19.7 | 29.3 | 24.6 | 0 | 0
1303 | 2022-12-26 21:43 | 6.4 | 19.7 | 29.1 | 24.4 | 0 | 0
1304 | 2022-12-26 21:44 | 6.4 | 19.6 | 28.9 | 24.3 | 0 | 0
1305 | 2022-12-26 21:45 | 6.5 | 19.7 | 28.7 | 24.1 | 0 | 0
1306 | 2022-12-26 21:46 | 6.5 | 19.6 | 28.6 | 23.9 | 0 | 0
1307 | 2022-12-26 21:47 | 6.4 | 19.7 | 28.4 | 23.7 | 0 | 0
1308 | 2022-12-26 21:48 | 6.3 | 19.6 | 28.2 | 23.6 | 0 | 0
1309 | 2022-12-26 21:49 | 6.4 | 19.7 | 28 | 23.4 | 0 | 0
1310 | 2022-12-26 21:50 | 6.3 | 19.7 | 27.8 | 23.3 | 0 | 0
1311 | 2022-12-26 21:51 | 6.4 | 19.7 | 27.7 | 23.1 | 0 | 0
1312 | 2022-12-26 21:52 | 6.5 | 19.6 | 27.5 | 23 | 0 | 0
1313 | 2022-12-26 21:53 | 6.5 | 19.6 | 27.3 | 22.8 | 0 | 0
1314 | 2022-12-26 21:54 | 6.4 | 19.6 | 27.1 | 22.7 | 0 | 0
1315 | 2022-12-26 21:55 | 6.4 | 19.6 | 27 | 22.5 | 0 | 0
1316 | 2022-12-26 21:56 | 6.4 | 19.5 | 26.8 | 22.4 | 0 | 0
1317 | 2022-12-26 21:57 | 6.5 | 19.5 | 26.6 | 22.2 | 0 | 0
1318 | 2022-12-26 21:58 | 6.2 | 19.5 | 26.5 | 22.1 | 0 | 0
1319 | 2022-12-26 21:59 | 6.2 | 19.6 | 26.3 | 22 | 0 | 0
1320 | 2022-12-26 22:00 | 6.2 | 19.5 | 26.1 | 21.8 | 0 | 0
1321 | 2022-12-26 22:01 | 6.3 | 19.5 | 26 | 21.7 | 0 | 0
1322 | 2022-12-26 22:02 | 6.3 | 19.5 | 25.8 | 21.6 | 0 | 0
1323 | 2022-12-26 22:03 | 6.3 | 19.5 | 25.7 | 21.4 | 0 | 0
1324 | 2022-12-26 22:04 | 6.2 | 19.5 | 25.5 | 21.3 | 0 | 0
1325 | 2022-12-26 22:05 | 6.1 | 19.5 | 25.3 | 21.2 | 0 | 0
1326 | 2022-12-26 22:06 | 6.4 | 19.5 | 25.2 | 21 | 0 | 0
1327 | 2022-12-26 22:07 | 6.2 | 19.5 | 25 | 20.9 | 0 | 0
1328 | 2022-12-26 22:08 | 6.4 | 19.5 | 24.9 | 20.8 | 0 | 0
1329 | 2022-12-26 22:09 | 6.4 | 19.5 | 24.7 | 20.7 | 0 | 0
1330 | 2022-12-26 22:10 | 6.2 | 19.5 | 24.6 | 20.6 | 0 | 0
1331 | 2022-12-26 22:11 | 6.4 | 19.5 | 24.4 | 20.4 | 0 | 0
1332 | 2022-12-26 22:12 | 6.1 | 19.4 | 24.3 | 20.3 | 0 | 0
1333 | 2022-12-26 22:13 | 6.4 | 19.5 | 24.2 | 20.2 | 0 | 0
1334 | 2022-12-26 22:14 | 6.4 | 19.4 | 24 | 20.1 | 0 | 0
1335 | 2022-12-26 22:15 | 6.2 | 19.4 | 23.9 | 20 | 0 | 0
1336 | 2022-12-26 22:16 | 6.4 | 19.5 | 23.7 | 19.9 | 0 | 0
1337 | 2022-12-26 22:17 | 6.5 | 19.4 | 23.6 | 19.8 | 0 | 0
1338 | 2022-12-26 22:18 | 6.3 | 19.4 | 23.5 | 19.6 | 0 | 0
1339 | 2022-12-26 22:19 | 6.3 | 19.4 | 23.3 | 19.5 | 0 | 0
1340 | 2022-12-26 22:20 | 6.5 | 19.4 | 23.2 | 19.4 | 0 | 0
1341 | 2022-12-26 22:21 | 6.4 | 19.4 | 23.1 | 19.3 | 0 | 0
1342 | 2022-12-26 22:22 | 6.1 | 19.4 | 22.9 | 19.2 | 0 | 0
1343 | 2022-12-26 22:23 | 6.2 | 19.4 | 22.8 | 19.1 | 0 | 0
1344 | 2022-12-26 22:24 | 6.2 | 19.4 | 22.6 | 19 | 0 | 0
1345 | 2022-12-26 22:25 | 6.4 | 19.5 | 22.5 | 18.9 | 0 | 0
1346 | 2022-12-26 22:26 | 6.2 | 19.4 | 22.4 | 18.8 | 0 | 0
1347 | 2022-12-26 22:27 | 6.2 | 19.4 | 22.3 | 18.7 | 0 | 0
1348 | 2022-12-26 22:28 | 6.2 | 19.4 | 22.1 | 18.6 | 0 | 0
1349 | 2022-12-26 22:29 | 6.3 | 19.4 | 22 | 18.5 | 0 | 0
1350 | 2022-12-26 22:30 | 6.2 | 19.4 | 21.9 | 18.4 | 0 | 0
1351 | 2022-12-26 22:31 | 6.1 | 19.4 | 21.7 | 18.3 | 0 | 0
1352 | 2022-12-26 22:32 | 6.1 | 19.3 | 21.6 | 18.3 | 0 | 0
1353 | 2022-12-26 22:33 | 6.1 | 19.4 | 21.5 | 18.2 | 0 | 0
1354 | 2022-12-26 22:34 | 6.2 | 19.4 | 21.4 | 18.1 | 0 | 0
1355 | 2022-12-26 22:35 | 6.1 | 19.4 | 21.3 | 18 | 0 | 0
1356 | 2022-12-26 22:36 | 6.1 | 19.3 | 21.1 | 17.9 | 0 | 0
1357 | 2022-12-26 22:37 | 6.3 | 19.3 | 21 | 17.8 | 0 | 0
1358 | 2022-12-26 22:38 | 6.5 | 19.4 | 20.9 | 17.7 | 0 | 0
1359 | 2022-12-26 22:39 | 6.4 | 19.3 | 20.8 | 17.7 | 0 | 0
1360 | 2022-12-26 22:40 | 6.4 | 19.3 | 20.7 | 17.6 | 0 | 0
1361 | 2022-12-26 22:41 | 6.4 | 19.3 | 20.6 | 17.5 | 0 | 0
1362 | 2022-12-26 22:42 | 6.2 | 19.3 | 20.5 | 17.4 | 0 | 0
1363 | 2022-12-26 22:43 | 6.2 | 19.3 | 20.4 | 17.4 | 0 | 0
1364 | 2022-12-26 22:44 | 6.2 | 19.3 | 20.3 | 17.3 | 0 | 0
1365 | 2022-12-26 22:45 | 6.2 | 19.3 | 20.2 | 17.2 | 0 | 0
1366 | 2022-12-26 22:46 | 6.2 | 19.4 | 20.1 | 17.1 | 0 | 0
1367 | 2022-12-26 22:47 | 6.1 | 19.3 | 20 | 17 | 0 | 0
1368 | 2022-12-26 22:48 | 6.2 | 19.2 | 19.9 | 17 | 0 | 0
1369 | 2022-12-26 22:49 | 6.2 | 19.2 | 19.8 | 16.9 | 0 | 0
1370 | 2022-12-26 22:50 | 6.3 | 19.3 | 19.7 | 16.8 | 0 | 0
1371 | 2022-12-26 22:51 | 6.1 | 19.2 | 19.6 | 16.8 | 0 | 0
1372 | 2022-12-26 22:52 | 6.1 | 19.2 | 19.6 | 16.7 | 0 | 0
1373 | 2022-12-26 22:53 | 6.1 | 19.3 | 19.5 | 16.6 | 0 | 0
1374 | 2022-12-26 22:54 | 6.1 | 19.2 | 19.4 | 16.5 | 0 | 0
1375 | 2022-12-26 22:55 | 6.1 | 19.3 | 19.3 | 16.5 | 0 | 0
1376 | 2022-12-26 22:56 | 6.2 | 19.3 | 19.2 | 16.4 | 0 | 0
1377 | 2022-12-26 22:57 | 6.2 | 19.3 | 19.1 | 16.3 | 0 | 0
1378 | 2022-12-26 22:58 | 6.1 | 19.2 | 19 | 16.3 | 0 | 0
1379 | 2022-12-26 22:59 | 6 | 19.2 | 19 | 16.2 | 0 | 0
1380 | 2022-12-26 23:00 | 6.1 | 19.1 | 18.9 | 16.1 | 0 | 0
1381 | 2022-12-26 23:01 | 6.1 | 19.2 | 18.8 | 16.1 | 0 | 0
1382 | 2022-12-26 23:02 | 6.1 | 19.2 | 18.7 | 16 | 0 | 0
1383 | 2022-12-26 23:03 | 6.1 | 19.2 | 18.7 | 16 | 0 | 0
1384 | 2022-12-26 23:04 | 6.1 | 19.2 | 18.6 | 15.9 | 0 | 0
1385 | 2022-12-26 23:05 | 6.1 | 19.2 | 18.5 | 15.8 | 0 | 0
1386 | 2022-12-26 23:06 | 6.1 | 19.2 | 18.4 | 15.8 | 0 | 0
1387 | 2022-12-26 23:07 | 6.2 | 19.2 | 18.4 | 15.7 | 0 | 0
1388 | 2022-12-26 23:08 | 6.2 | 19.2 | 18.3 | 15.6 | 0 | 0
1389 | 2022-12-26 23:09 | 6.1 | 19.1 | 18.2 | 15.6 | 0 | 0
1390 | 2022-12-26 23:10 | 6.1 | 19.1 | 18.1 | 15.5 | 0 | 0
1391 | 2022-12-26 23:11 | 6.3 | 19.1 | 18 | 15.5 | 0 | 0
1392 | 2022-12-26 23:12 | 6.1 | 19.1 | 18 | 15.4 | 0 | 0
1393 | 2022-12-26 23:13 | 6.1 | 19.1 | 17.9 | 15.3 | 0 | 0
1394 | 2022-12-26 23:14 | 6.2 | 19.1 | 17.8 | 15.3 | 0 | 0
1395 | 2022-12-26 23:15 | 6.2 | 19.1 | 17.8 | 15.2 | 0 | 0
1396 | 2022-12-26 23:16 | 6.2 | 19.1 | 17.7 | 15.2 | 0 | 0
1397 | 2022-12-26 23:17 | 6.2 | 19.1 | 17.6 | 15.1 | 0 | 0
1398 | 2022-12-26 23:18 | 6.2 | 19.1 | 17.6 | 15.1 | 0 | 0
1399 | 2022-12-26 23:19 | 6.3 | 19.1 | 17.5 | 15 | 0 | 0
1400 | 2022-12-26 23:20 | 6.1 | 19.1 | 17.5 | 15 | 0 | 0
1401 | 2022-12-26 23:21 | 6.3 | 19.1 | 17.4 | 14.9 | 0 | 0
1402 | 2022-12-26 23:22 | 6.3 | 19.1 | 17.4 | 14.9 | 0 | 0
1403 | 2022-12-26 23:23 | 6.2 | 19.1 | 17.3 | 14.8 | 0 | 0
1404 | 2022-12-26 23:24 | 6.4 | 19.1 | 17.3 | 14.7 | 0 | 0
1405 | 2022-12-26 23:25 | 6.4 | 19.1 | 17.2 | 14.7 | 0 | 0
1406 | 2022-12-26 23:26 | 6.5 | 19 | 17.2 | 14.6 | 0 | 0
1407 | 2022-12-26 23:27 | 6.6 | 19.1 | 17.1 | 14.6 | 0 | 0
1408 | 2022-12-26 23:28 | 6.8 | 19 | 17.1 | 14.6 | 0 | 0
1409 | 2022-12-26 23:29 | 6.7 | 19.1 | 17 | 14.5 | 0 | 0
1410 | 2022-12-26 23:30 | 6.7 | 19.1 | 17 | 14.5 | 0 | 0
1411 | 2022-12-26 23:31 | 7.2 | 19 | 16.9 | 14.4 | 0 | 0
1412 | 2022-12-26 23:32 | 7.4 | 19 | 16.9 | 14.4 | 0 | 0
1413 | 2022-12-26 23:33 | 7.3 | 19.1 | 16.8 | 14.3 | 0 | 0
1414 | 2022-12-26 23:34 | 7.7 | 19 | 16.8 | 14.3 | 0 | 0
1415 | 2022-12-26 23:35 | 7.8 | 19 | 16.7 | 14.2 | 0 | 0
1416 | 2022-12-26 23:36 | 9 | 19.1 | 16.7 | 14.2 | 0 | 0
1417 | 2022-12-26 23:37 | 8.5 | 19 | 16.6 | 14.1 | 0 | 0
1418 | 2022-12-26 23:38 | 9.1 | 19.1 | 16.6 | 14.1 | 0 | 0
1419 | 2022-12-26 23:39 | 9 | 19 | 16.5 | 14.1 | 0 | 0
1420 | 2022-12-26 23:40 | 9.4 | 19 | 16.5 | 14 | 0 | 0
1421 | 2022-12-26 23:41 | 9.6 | 19 | 16.4 | 14 | 0 | 0
1422 | 2022-12-26 23:42 | 9.5 | 19 | 16.4 | 13.9 | 0 | 0
1423 | 2022-12-26 23:43 | 9.7 | 19.1 | 16.4 | 13.9 | 0 | 0
1424 | 2022-12-26 23:44 | 9.6 | 19 | 16.3 | 13.9 | 0 | 0
1425 | 2022-12-26 23:45 | 9.9 | 19 | 16.3 | 13.8 | 0 | 0
1426 | 2022-12-26 23:46 | 9.9 | 19 | 16.3 | 13.8 | 0 | 0
1427 | 2022-12-26 23:47 | 10.4 | 19 | 16.3 | 13.8 | 0 | 0
1428 | 2022-12-26 23:48 | 10.4 | 19 | 16.3 | 13.8 | 0 | 0
1429 | 2022-12-26 23:49 | 10.3 | 18.9 | 16.3 | 13.7 | 0 | 0
1430 | 2022-12-26 23:50 | 10.8 | 18.9 | 16.2 | 13.7 | 0 | 0
1431 | 2022-12-26 23:51 | 10.4 | 19 | 16.2 | 13.7 | 0 | 0
1432 | 2022-12-26 23:52 | 10.4 | 18.9 | 16.2 | 13.7 | 0 | 0
1433 | 2022-12-26 23:53 | 10.5 | 18.9 | 16.2 | 13.6 | 0 | 0
1434 | 2022-12-26 23:54 | 11.1 | 18.9 | 16.2 | 13.6 | 0 | 0
1435 | 2022-12-26 23:55 | 10.8 | 19 | 16.2 | 13.6 | 0 | 0
1436 | 2022-12-26 23:56 | 10.9 | 19 | 16.2 | 13.6 | 0 | 0
1437 | 2022-12-26 23:57 | 11 | 18.9 | 16.2 | 13.5 | 0 | 0
1438 | 2022-12-26 23:58 | 10.9 | 19 | 16.2 | 13.5 | 0 | 0
1439 | 2022-12-26 23:59 | 11.1 | 19 | 16.1 | 13.5 | 0 | 0

## 27-12-2022_WITH HEAT
| Date&time_x | OUTDOOR_TEMP | INDOOR_TEMP | SH_INLET | SH_RETURN | FLOW_FAN_COILS_INDOOR | PYRANOMETER
0 | 2022-12-27 | 11.1 | 18.9 | 16.1 | 13.5 | 0 | 0
1 | 2022-12-27 00:01 | 10.9 | 18.9 | 16.1 | 13.5 | 0 | 0
2 | 2022-12-27 00:02 | 11.2 | 19 | 16.1 | 13.5 | 0 | 0
3 | 2022-12-27 00:03 | 11.2 | 18.9 | 16.1 | 13.4 | 0 | 0
4 | 2022-12-27 00:04 | 11 | 19 | 16.1 | 13.4 | 0 | 0
5 | 2022-12-27 00:05 | 10.9 | 18.9 | 16.1 | 13.4 | 0 | 0
6 | 2022-12-27 00:06 | 11.2 | 18.9 | 16.1 | 13.4 | 0 | 0
7 | 2022-12-27 00:07 | 11.6 | 18.9 | 16.1 | 13.4 | 0 | 0
8 | 2022-12-27 00:08 | 11.5 | 18.9 | 16.1 | 13.4 | 0 | 0
9 | 2022-12-27 00:09 | 11.1 | 18.9 | 16.1 | 13.4 | 0 | 0
10 | 2022-12-27 00:10 | 10.7 | 18.9 | 16.1 | 13.4 | 0 | 0
11 | 2022-12-27 00:11 | 10.6 | 18.9 | 16.1 | 13.3 | 0 | 0
12 | 2022-12-27 00:12 | 10.2 | 18.9 | 16.1 | 13.3 | 0 | 0
13 | 2022-12-27 00:13 | 9.9 | 19 | 16 | 13.3 | 0 | 0
14 | 2022-12-27 00:14 | 9.9 | 18.9 | 16 | 13.3 | 0 | 0
15 | 2022-12-27 00:15 | 10.3 | 18.9 | 16 | 13.3 | 0 | 0
16 | 2022-12-27 00:16 | 10.6 | 18.8 | 16 | 13.3 | 0 | 0
17 | 2022-12-27 00:17 | 10.4 | 18.9 | 16 | 13.3 | 0 | 0
18 | 2022-12-27 00:18 | 10.6 | 18.8 | 16 | 13.2 | 0 | 0
19 | 2022-12-27 00:19 | 10.3 | 18.9 | 16 | 13.2 | 0 | 0
20 | 2022-12-27 00:20 | 10.7 | 18.9 | 15.9 | 13.2 | 0 | 0
21 | 2022-12-27 00:21 | 10.8 | 18.9 | 15.9 | 13.2 | 0 | 0
22 | 2022-12-27 00:22 | 10.7 | 18.9 | 15.9 | 13.2 | 0 | 0
23 | 2022-12-27 00:23 | 10.8 | 18.8 | 15.9 | 13.2 | 0 | 0
24 | 2022-12-27 00:24 | 10.2 | 18.8 | 15.9 | 13.2 | 0 | 0
25 | 2022-12-27 00:25 | 10.4 | 18.9 | 15.9 | 13.1 | 0 | 0
26 | 2022-12-27 00:26 | 10.8 | 18.9 | 15.9 | 13.1 | 0 | 0
27 | 2022-12-27 00:27 | 10.2 | 18.9 | 15.8 | 13.1 | 0 | 0
28 | 2022-12-27 00:28 | 9.4 | 18.8 | 15.8 | 13.1 | 0 | 0
29 | 2022-12-27 00:29 | 9.5 | 18.9 | 15.8 | 13.1 | 0 | 0
30 | 2022-12-27 00:30 | 9.7 | 18.9 | 15.8 | 13.1 | 0 | 0
31 | 2022-12-27 00:31 | 9.6 | 18.8 | 15.8 | 13.1 | 0 | 0
32 | 2022-12-27 00:32 | 10 | 18.8 | 15.8 | 13 | 0 | 0
33 | 2022-12-27 00:33 | 10.2 | 18.9 | 15.8 | 13 | 0 | 0
34 | 2022-12-27 00:34 | 10.3 | 18.9 | 15.7 | 13 | 0 | 0
35 | 2022-12-27 00:35 | 10.3 | 18.9 | 15.7 | 13 | 0 | 0
36 | 2022-12-27 00:36 | 10.5 | 18.8 | 15.7 | 13 | 0 | 0
37 | 2022-12-27 00:37 | 10.7 | 18.7 | 15.7 | 13 | 0 | 0
38 | 2022-12-27 00:38 | 10.8 | 18.8 | 15.7 | 13 | 0 | 0
39 | 2022-12-27 00:39 | 11 | 18.8 | 15.7 | 13 | 0 | 0
40 | 2022-12-27 00:40 | 10.5 | 18.8 | 15.6 | 12.9 | 0 | 0
41 | 2022-12-27 00:41 | 11.1 | 18.8 | 15.6 | 12.9 | 0 | 0
42 | 2022-12-27 00:42 | 10.8 | 18.8 | 15.6 | 12.9 | 0 | 0
43 | 2022-12-27 00:43 | 11.2 | 18.8 | 15.6 | 12.9 | 0 | 0
44 | 2022-12-27 00:44 | 11.4 | 18.8 | 15.6 | 12.9 | 0 | 0
45 | 2022-12-27 00:45 | 11.5 | 18.8 | 15.6 | 12.9 | 0 | 0
46 | 2022-12-27 00:46 | 11.3 | 18.8 | 15.6 | 12.9 | 0 | 0
47 | 2022-12-27 00:47 | 11.4 | 18.8 | 15.6 | 12.9 | 0 | 0
48 | 2022-12-27 00:48 | 11.1 | 18.7 | 15.6 | 12.9 | 0 | 0
49 | 2022-12-27 00:49 | 11.4 | 18.8 | 15.6 | 12.9 | 0 | 0
50 | 2022-12-27 00:50 | 11.7 | 18.8 | 15.6 | 12.9 | 0 | 0
51 | 2022-12-27 00:51 | 11.8 | 18.8 | 15.6 | 12.9 | 0 | 0
52 | 2022-12-27 00:52 | 11.6 | 18.8 | 15.6 | 12.9 | 0 | 0
53 | 2022-12-27 00:53 | 11.7 | 18.8 | 15.6 | 12.9 | 0 | 0
54 | 2022-12-27 00:54 | 11.8 | 18.7 | 15.6 | 12.9 | 0 | 0
55 | 2022-12-27 00:55 | 11.7 | 18.7 | 15.6 | 12.9 | 0 | 0
56 | 2022-12-27 00:56 | 11.9 | 18.7 | 15.6 | 12.9 | 0 | 0
57 | 2022-12-27 00:57 | 12 | 18.7 | 15.6 | 12.9 | 0 | 0
58 | 2022-12-27 00:58 | 11.7 | 18.7 | 15.6 | 12.8 | 0 | 0
59 | 2022-12-27 00:59 | 11.3 | 18.7 | 15.6 | 12.8 | 0 | 0
60 | 2022-12-27 01:00 | 11.5 | 18.7 | 15.6 | 12.8 | 0 | 0
61 | 2022-12-27 01:01 | 11.6 | 18.7 | 15.6 | 12.8 | 0 | 0
62 | 2022-12-27 01:02 | 11.6 | 18.7 | 15.7 | 12.8 | 0 | 0
63 | 2022-12-27 01:03 | 11 | 18.7 | 15.7 | 12.8 | 0 | 0
64 | 2022-12-27 01:04 | 11.2 | 18.7 | 15.7 | 12.8 | 0 | 0
65 | 2022-12-27 01:05 | 11.3 | 18.7 | 15.6 | 12.8 | 0 | 0
66 | 2022-12-27 01:06 | 11.4 | 18.7 | 15.6 | 12.8 | 0 | 0
67 | 2022-12-27 01:07 | 11.5 | 18.7 | 15.6 | 12.8 | 0 | 0
68 | 2022-12-27 01:08 | 11.7 | 18.7 | 15.6 | 12.8 | 0 | 0
69 | 2022-12-27 01:09 | 11.4 | 18.7 | 15.6 | 12.8 | 0 | 0
70 | 2022-12-27 01:10 | 11.5 | 18.7 | 15.6 | 12.8 | 0 | 0
71 | 2022-12-27 01:11 | 11.4 | 18.7 | 15.7 | 12.8 | 0 | 0
72 | 2022-12-27 01:12 | 11.7 | 18.7 | 15.6 | 12.8 | 0 | 0
73 | 2022-12-27 01:13 | 11.7 | 18.6 | 15.6 | 12.8 | 0 | 0
74 | 2022-12-27 01:14 | 11.6 | 18.7 | 15.7 | 12.8 | 0 | 0
75 | 2022-12-27 01:15 | 11.4 | 18.7 | 15.7 | 12.8 | 0 | 0
76 | 2022-12-27 01:16 | 11.3 | 18.7 | 15.7 | 12.8 | 0 | 0
77 | 2022-12-27 01:17 | 11.6 | 18.7 | 15.7 | 12.8 | 0 | 0
78 | 2022-12-27 01:18 | 11.7 | 18.6 | 15.6 | 12.8 | 0 | 0
79 | 2022-12-27 01:19 | 11.6 | 18.6 | 15.7 | 12.8 | 0 | 0
80 | 2022-12-27 01:20 | 11.8 | 18.7 | 15.6 | 12.8 | 0 | 0
81 | 2022-12-27 01:21 | 12 | 18.6 | 15.6 | 12.8 | 0 | 0
82 | 2022-12-27 01:22 | 11.6 | 18.8 | 15.6 | 12.8 | 0 | 0
83 | 2022-12-27 01:23 | 11.3 | 18.7 | 15.6 | 12.8 | 0 | 0
84 | 2022-12-27 01:24 | 11.9 | 18.6 | 15.6 | 12.8 | 0 | 0
85 | 2022-12-27 01:25 | 11.9 | 18.7 | 15.7 | 12.8 | 0 | 0
86 | 2022-12-27 01:26 | 11.9 | 18.6 | 15.7 | 12.8 | 0 | 0
87 | 2022-12-27 01:27 | 11.5 | 18.7 | 15.7 | 13.1 | 0 | 0
88 | 2022-12-27 01:28 | 11.4 | 18.7 | 15.7 | 13.2 | 0 | 0
89 | 2022-12-27 01:29 | 11.6 | 18.6 | 15.7 | 13.2 | 0.116 | 0
90 | 2022-12-27 01:30 | 11.5 | 18.6 | 31.7 | 13.6 | 0.916 | 0
91 | 2022-12-27 01:31 | 11.5 | 18.6 | 39.3 | 33.2 | 0.96 | 0
92 | 2022-12-27 01:32 | 11.5 | 18.7 | 38.6 | 36.1 | 0.933 | 0
93 | 2022-12-27 01:33 | 11.6 | 18.7 | 38.2 | 35.9 | 0.98 | 0
94 | 2022-12-27 01:34 | 11.6 | 18.7 | 38 | 35.8 | 0.977 | 0
95 | 2022-12-27 01:35 | 11.7 | 18.7 | 38.6 | 36 | 0.978 | 0
96 | 2022-12-27 01:36 | 11.9 | 18.8 | 39 | 36.5 | 0 | 0
97 | 2022-12-27 01:37 | 11.5 | 18.8 | 39 | 36.6 | 0 | 0
98 | 2022-12-27 01:38 | 11.8 | 18.8 | 38.6 | 36 | 0 | 0
99 | 2022-12-27 01:39 | 11.6 | 18.9 | 38.2 | 35.2 | 0 | 0
100 | 2022-12-27 01:40 | 11.5 | 18.8 | 37.9 | 34.6 | 0 | 0
101 | 2022-12-27 01:41 | 11.7 | 18.9 | 37.6 | 34 | 0 | 0
102 | 2022-12-27 01:42 | 11.5 | 18.8 | 37.3 | 33.4 | 0 | 0
103 | 2022-12-27 01:43 | 11.7 | 18.8 | 37 | 32.9 | 0 | 0
104 | 2022-12-27 01:44 | 11.8 | 18.8 | 36.7 | 32.4 | 0 | 0
105 | 2022-12-27 01:45 | 12.1 | 18.7 | 36.4 | 32 | 0 | 0
106 | 2022-12-27 01:46 | 12.1 | 18.7 | 36.2 | 31.5 | 0 | 0
107 | 2022-12-27 01:47 | 11.9 | 18.7 | 35.9 | 31.1 | 0 | 0
108 | 2022-12-27 01:48 | 12 | 18.7 | 35.7 | 30.7 | 0 | 0
109 | 2022-12-27 01:49 | 11.9 | 18.6 | 35.5 | 30.4 | 0 | 0
110 | 2022-12-27 01:50 | 11.8 | 18.6 | 35.3 | 30 | 0 | 0
111 | 2022-12-27 01:51 | 11.7 | 18.6 | 35 | 29.7 | 0 | 0
112 | 2022-12-27 01:52 | 12 | 18.7 | 34.8 | 29.3 | 0 | 0
113 | 2022-12-27 01:53 | 12.1 | 18.7 | 34.6 | 29 | 0 | 0
114 | 2022-12-27 01:54 | 11.8 | 18.6 | 34.4 | 28.7 | 0 | 0
115 | 2022-12-27 01:55 | 11.9 | 18.6 | 34.2 | 28.4 | 0 | 0
116 | 2022-12-27 01:56 | 11.9 | 18.7 | 34 | 28.2 | 0 | 0
117 | 2022-12-27 01:57 | 11.9 | 18.7 | 33.8 | 27.9 | 0 | 0
118 | 2022-12-27 01:58 | 12 | 18.6 | 33.6 | 27.7 | 0 | 0
119 | 2022-12-27 01:59 | 12.1 | 18.6 | 33.4 | 27.4 | 0 | 0
120 | 2022-12-27 02:00 | 12.2 | 18.6 | 33.2 | 27.2 | 0 | 0
121 | 2022-12-27 02:01 | 12.2 | 18.6 | 33 | 27 | 0 | 0
122 | 2022-12-27 02:02 | 11.9 | 18.7 | 32.9 | 26.7 | 0 | 0
123 | 2022-12-27 02:03 | 11.9 | 18.6 | 32.7 | 26.5 | 0 | 0
124 | 2022-12-27 02:04 | 11.9 | 18.6 | 32.5 | 26.3 | 0 | 0
125 | 2022-12-27 02:05 | 12.1 | 18.5 | 32.3 | 26.1 | 0 | 0
126 | 2022-12-27 02:06 | 11.9 | 18.6 | 32.1 | 25.9 | 0 | 0
127 | 2022-12-27 02:07 | 11.9 | 18.5 | 31.9 | 25.7 | 0 | 0
128 | 2022-12-27 02:08 | 12 | 18.5 | 31.7 | 25.5 | 0 | 0
129 | 2022-12-27 02:09 | 11.7 | 18.6 | 31.6 | 25.3 | 0 | 0
130 | 2022-12-27 02:10 | 11.8 | 18.5 | 31.4 | 25.2 | 0 | 0
131 | 2022-12-27 02:11 | 11.9 | 18.6 | 31.2 | 25 | 0 | 0
132 | 2022-12-27 02:12 | 11.8 | 18.6 | 31.1 | 24.8 | 0 | 0
133 | 2022-12-27 02:13 | 11.9 | 18.6 | 30.9 | 24.7 | 0 | 0
134 | 2022-12-27 02:14 | 11.9 | 18.6 | 30.7 | 24.5 | 0 | 0
135 | 2022-12-27 02:15 | 11.6 | 18.6 | 30.6 | 24.3 | 0 | 0
136 | 2022-12-27 02:16 | 11.8 | 18.6 | 30.4 | 24.2 | 0 | 0
137 | 2022-12-27 02:17 | 12.1 | 18.5 | 30.2 | 24 | 0 | 0
138 | 2022-12-27 02:18 | 11.9 | 18.5 | 30.1 | 23.9 | 0 | 0
139 | 2022-12-27 02:19 | 11.9 | 18.5 | 29.9 | 23.8 | 0 | 0
140 | 2022-12-27 02:20 | 11.9 | 18.6 | 29.8 | 23.6 | 0 | 0
141 | 2022-12-27 02:21 | 12.1 | 18.6 | 29.6 | 23.5 | 0 | 0
142 | 2022-12-27 02:22 | 12 | 18.5 | 29.4 | 23.3 | 0 | 0
143 | 2022-12-27 02:23 | 12 | 18.6 | 29.3 | 23.2 | 0 | 0
144 | 2022-12-27 02:24 | 12 | 18.6 | 29.1 | 23.1 | 0 | 0
145 | 2022-12-27 02:25 | 12 | 18.6 | 29 | 22.9 | 0 | 0
146 | 2022-12-27 02:26 | 12 | 18.6 | 28.8 | 22.8 | 0 | 0
147 | 2022-12-27 02:27 | 12 | 18.6 | 28.7 | 25.4 | 0 | 0
148 | 2022-12-27 02:28 | 12.1 | 18.5 | 28.5 | 24.8 | 0.399 | 0
149 | 2022-12-27 02:29 | 11.8 | 18.5 | 39.3 | 27.1 | 0.974 | 0
150 | 2022-12-27 02:30 | 11.7 | 18.5 | 42.3 | 37.9 | 0.987 | 0
151 | 2022-12-27 02:31 | 11.8 | 18.5 | 41.7 | 39.1 | 0.986 | 0
152 | 2022-12-27 02:32 | 11.4 | 18.6 | 42 | 39 | 0.986 | 0
153 | 2022-12-27 02:33 | 11.8 | 18.5 | 42.2 | 39.4 | 0.982 | 0
154 | 2022-12-27 02:34 | 11.9 | 18.6 | 42.5 | 39.7 | 0 | 0
155 | 2022-12-27 02:35 | 11.9 | 18.8 | 42.3 | 39.4 | 0 | 0
156 | 2022-12-27 02:36 | 11.9 | 18.8 | 41.9 | 38.6 | 0 | 0
157 | 2022-12-27 02:37 | 11.7 | 18.8 | 41.6 | 37.9 | 0 | 0
158 | 2022-12-27 02:38 | 11.8 | 18.7 | 41.2 | 37.3 | 0 | 0
159 | 2022-12-27 02:39 | 11.9 | 18.8 | 40.9 | 36.6 | 0 | 0
160 | 2022-12-27 02:40 | 11.6 | 18.7 | 40.6 | 36.1 | 0 | 0
161 | 2022-12-27 02:41 | 11.5 | 18.6 | 40.3 | 35.6 | 0 | 0
162 | 2022-12-27 02:42 | 11.6 | 18.6 | 40 | 35.1 | 0 | 0
163 | 2022-12-27 02:43 | 11.4 | 18.6 | 39.7 | 34.6 | 0 | 0
164 | 2022-12-27 02:44 | 11.4 | 18.5 | 39.4 | 34.2 | 0 | 0
165 | 2022-12-27 02:45 | 11.4 | 18.5 | 39.2 | 33.7 | 0 | 0
166 | 2022-12-27 02:46 | 11.3 | 18.5 | 38.9 | 33.3 | 0 | 0
167 | 2022-12-27 02:47 | 11.3 | 18.5 | 38.7 | 33 | 0 | 0
168 | 2022-12-27 02:48 | 11.6 | 18.6 | 38.4 | 32.6 | 0 | 0
169 | 2022-12-27 02:49 | 11 | 18.6 | 38.2 | 32.2 | 0 | 0
170 | 2022-12-27 02:50 | 11 | 18.5 | 37.9 | 31.9 | 0 | 0
171 | 2022-12-27 02:51 | 11.2 | 18.5 | 37.7 | 31.6 | 0 | 0
172 | 2022-12-27 02:52 | 10.8 | 18.5 | 37.5 | 31.3 | 0 | 0
173 | 2022-12-27 02:53 | 10.8 | 18.5 | 37.2 | 31 | 0 | 0
174 | 2022-12-27 02:54 | 10.5 | 18.5 | 37 | 30.7 | 0 | 0
175 | 2022-12-27 02:55 | 10 | 18.5 | 36.8 | 30.4 | 0 | 0
176 | 2022-12-27 02:56 | 10.5 | 18.5 | 36.5 | 30.1 | 0 | 0
177 | 2022-12-27 02:57 | 10.1 | 18.5 | 36.3 | 29.9 | 0 | 0
178 | 2022-12-27 02:58 | 10.3 | 18.5 | 36.1 | 29.6 | 0 | 0
179 | 2022-12-27 02:59 | 10.3 | 18.5 | 35.9 | 29.4 | 0 | 0
180 | 2022-12-27 03:00 | 9.8 | 18.5 | 35.7 | 29.1 | 0 | 0
181 | 2022-12-27 03:01 | 10 | 18.5 | 35.4 | 28.9 | 0 | 0
182 | 2022-12-27 03:02 | 9.6 | 18.5 | 35.2 | 28.6 | 0 | 0
183 | 2022-12-27 03:03 | 10 | 18.5 | 35 | 28.4 | 0 | 0
184 | 2022-12-27 03:04 | 10 | 18.5 | 34.8 | 28.2 | 0 | 0
185 | 2022-12-27 03:05 | 10.1 | 18.5 | 34.6 | 27.9 | 0 | 0
186 | 2022-12-27 03:06 | 10.1 | 18.5 | 34.4 | 27.7 | 0 | 0
187 | 2022-12-27 03:07 | 10.4 | 18.5 | 34.2 | 27.5 | 0 | 0
188 | 2022-12-27 03:08 | 10.3 | 18.4 | 34 | 27.3 | 0 | 0
189 | 2022-12-27 03:09 | 10.2 | 18.5 | 33.8 | 27.1 | 0 | 0
190 | 2022-12-27 03:10 | 9.5 | 18.4 | 33.6 | 26.9 | 0 | 0
191 | 2022-12-27 03:11 | 10.2 | 18.4 | 33.4 | 26.7 | 0 | 0
192 | 2022-12-27 03:12 | 10.5 | 18.4 | 33.2 | 26.5 | 0 | 0
193 | 2022-12-27 03:13 | 10.7 | 18.5 | 33 | 26.3 | 0 | 0
194 | 2022-12-27 03:14 | 9.9 | 18.4 | 32.7 | 26.1 | 0 | 0
195 | 2022-12-27 03:15 | 10 | 18.4 | 32.6 | 25.9 | 0 | 0
196 | 2022-12-27 03:16 | 9.9 | 18.4 | 32.4 | 29.2 | 0 | 0
197 | 2022-12-27 03:17 | 9.8 | 18.4 | 32.2 | 28.8 | 0.304 | 0
198 | 2022-12-27 03:18 | 9.2 | 18.5 | 39.3 | 30.5 | 0.973 | 0
199 | 2022-12-27 03:19 | 9.7 | 18.4 | 41.3 | 37.4 | 0.981 | 0
200 | 2022-12-27 03:20 | 9.8 | 18.4 | 40.4 | 38.2 | 0.982 | 0
201 | 2022-12-27 03:21 | 9.9 | 18.5 | 40.5 | 37.9 | 0.982 | 0
202 | 2022-12-27 03:22 | 9.5 | 18.5 | 40.5 | 38.2 | 0.982 | 0
203 | 2022-12-27 03:23 | 9.3 | 18.5 | 40.4 | 38.1 | 0 | 0
204 | 2022-12-27 03:24 | 9.5 | 18.6 | 40.2 | 38 | 0 | 0
205 | 2022-12-27 03:25 | 9.6 | 18.7 | 39.9 | 37.4 | 0 | 0
206 | 2022-12-27 03:26 | 10.1 | 18.6 | 39.6 | 36.8 | 0 | 0
207 | 2022-12-27 03:27 | 9.4 | 18.6 | 39.3 | 36.2 | 0 | 0
208 | 2022-12-27 03:28 | 10 | 18.6 | 39 | 35.7 | 0 | 0
209 | 2022-12-27 03:29 | 9.9 | 18.5 | 38.7 | 35.1 | 0 | 0
210 | 2022-12-27 03:30 | 9.2 | 18.5 | 38.5 | 34.6 | 0 | 0
211 | 2022-12-27 03:31 | 9.5 | 18.5 | 38.2 | 34.2 | 0 | 0
212 | 2022-12-27 03:32 | 9 | 18.5 | 37.9 | 33.7 | 0 | 0
213 | 2022-12-27 03:33 | 9 | 18.5 | 37.7 | 33.3 | 0 | 0
214 | 2022-12-27 03:34 | 9.2 | 18.4 | 37.4 | 32.9 | 0 | 0
215 | 2022-12-27 03:35 | 8.9 | 18.5 | 37.2 | 32.5 | 0 | 0
216 | 2022-12-27 03:36 | 8.8 | 18.4 | 36.9 | 32.1 | 0 | 0
217 | 2022-12-27 03:37 | 9.7 | 18.4 | 36.7 | 31.8 | 0 | 0
218 | 2022-12-27 03:38 | 9.7 | 18.4 | 36.4 | 31.5 | 0 | 0
219 | 2022-12-27 03:39 | 9.3 | 18.4 | 36.2 | 31.1 | 0 | 0
220 | 2022-12-27 03:40 | 9 | 18.4 | 36 | 30.8 | 0 | 0
221 | 2022-12-27 03:41 | 9.4 | 18.4 | 35.7 | 30.5 | 0 | 0
222 | 2022-12-27 03:42 | 9.3 | 18.4 | 35.5 | 30.3 | 0 | 0
223 | 2022-12-27 03:43 | 9.7 | 18.4 | 35.3 | 30 | 0 | 0
224 | 2022-12-27 03:44 | 9.8 | 18.4 | 35.1 | 29.7 | 0 | 0
225 | 2022-12-27 03:45 | 9.5 | 18.4 | 34.8 | 29.5 | 0 | 0
226 | 2022-12-27 03:46 | 9.9 | 18.4 | 34.6 | 29.2 | 0 | 0
227 | 2022-12-27 03:47 | 9.7 | 18.4 | 34.4 | 28.9 | 0 | 0
228 | 2022-12-27 03:48 | 9.7 | 18.4 | 34.2 | 28.7 | 0 | 0
229 | 2022-12-27 03:49 | 9.8 | 18.4 | 34 | 28.5 | 0 | 0
230 | 2022-12-27 03:50 | 9.2 | 18.4 | 33.8 | 28.2 | 0 | 0
231 | 2022-12-27 03:51 | 9.6 | 18.4 | 33.5 | 28 | 0 | 0
232 | 2022-12-27 03:52 | 10.2 | 18.4 | 33.3 | 27.8 | 0 | 0
233 | 2022-12-27 03:53 | 10 | 18.4 | 33.1 | 27.6 | 0 | 0
234 | 2022-12-27 03:54 | 10.3 | 18.4 | 32.9 | 27.4 | 0 | 0
235 | 2022-12-27 03:55 | 9.9 | 18.4 | 32.7 | 27.1 | 0 | 0
236 | 2022-12-27 03:56 | 9.6 | 18.4 | 32.6 | 27.7 | 0 | 0
237 | 2022-12-27 03:57 | 9.4 | 18.4 | 32.4 | 28.8 | 0 | 0
238 | 2022-12-27 03:58 | 8.9 | 18.3 | 32.2 | 28.2 | 0.861 | 0
239 | 2022-12-27 03:59 | 8.4 | 18.3 | 44 | 27.9 | 0.986 | 0
240 | 2022-12-27 04:00 | 8.7 | 18.3 | 44 | 40.8 | 0.984 | 0
241 | 2022-12-27 04:01 | 8.8 | 18.3 | 43.7 | 40.7 | 0.986 | 0
242 | 2022-12-27 04:02 | 8.3 | 18.3 | 44.1 | 41 | 0.984 | 0
243 | 2022-12-27 04:03 | 8.2 | 18.4 | 44.3 | 41.3 | 0 | 0
244 | 2022-12-27 04:04 | 8.3 | 18.6 | 44 | 41.1 | 0 | 0
245 | 2022-12-27 04:05 | 8.8 | 18.6 | 43.6 | 40.3 | 0 | 0
246 | 2022-12-27 04:06 | 8.6 | 18.6 | 43.3 | 39.6 | 0 | 0
247 | 2022-12-27 04:07 | 8.3 | 18.5 | 42.9 | 38.9 | 0 | 0
248 | 2022-12-27 04:08 | 8.2 | 18.5 | 42.6 | 38.2 | 0 | 0
249 | 2022-12-27 04:09 | 8.3 | 18.5 | 42.2 | 37.6 | 0 | 0
250 | 2022-12-27 04:10 | 8.1 | 18.5 | 41.9 | 37 | 0 | 0
251 | 2022-12-27 04:11 | 7.8 | 18.5 | 41.6 | 36.5 | 0 | 0
252 | 2022-12-27 04:12 | 7.9 | 18.4 | 41.3 | 36 | 0 | 0
253 | 2022-12-27 04:13 | 7.9 | 18.4 | 41 | 35.6 | 0 | 0
254 | 2022-12-27 04:14 | 7.7 | 18.4 | 40.7 | 35.1 | 0 | 0
255 | 2022-12-27 04:15 | 7.9 | 18.4 | 40.4 | 34.7 | 0 | 0
256 | 2022-12-27 04:16 | 8 | 18.3 | 40.1 | 34.2 | 0 | 0
257 | 2022-12-27 04:17 | 8.4 | 18.4 | 39.8 | 33.8 | 0 | 0
258 | 2022-12-27 04:18 | 7.9 | 18.3 | 39.6 | 33.4 | 0 | 0
259 | 2022-12-27 04:19 | 7.7 | 18.4 | 39.3 | 33.1 | 0 | 0
260 | 2022-12-27 04:20 | 7.8 | 18.3 | 39 | 32.7 | 0 | 0
261 | 2022-12-27 04:21 | 7.8 | 18.3 | 38.8 | 32.4 | 0 | 0
262 | 2022-12-27 04:22 | 7.8 | 18.4 | 38.5 | 32 | 0 | 0
263 | 2022-12-27 04:23 | 7.8 | 18.3 | 38.2 | 31.7 | 0 | 0
264 | 2022-12-27 04:24 | 7.7 | 18.4 | 38 | 31.4 | 0 | 0
265 | 2022-12-27 04:25 | 7.7 | 18.3 | 37.7 | 31.1 | 0 | 0
266 | 2022-12-27 04:26 | 7.6 | 18.3 | 37.5 | 30.8 | 0 | 0
267 | 2022-12-27 04:27 | 7.6 | 18.3 | 37.2 | 30.5 | 0 | 0
268 | 2022-12-27 04:28 | 7.7 | 18.3 | 37 | 30.2 | 0 | 0
269 | 2022-12-27 04:29 | 7.6 | 18.3 | 36.7 | 29.9 | 0 | 0
270 | 2022-12-27 04:30 | 7.6 | 18.3 | 36.5 | 29.7 | 0 | 0
271 | 2022-12-27 04:31 | 7.7 | 18.2 | 36.2 | 29.4 | 0 | 0
272 | 2022-12-27 04:32 | 7.4 | 18.3 | 36 | 31.9 | 0 | 0
273 | 2022-12-27 04:33 | 7.9 | 18.3 | 35.8 | 31.9 | 0 | 0
274 | 2022-12-27 04:34 | 7.6 | 18.3 | 36.3 | 33.4 | 0.96 | 0
275 | 2022-12-27 04:35 | 7.5 | 18.3 | 43.4 | 37.2 | 0.986 | 0
276 | 2022-12-27 04:36 | 7.6 | 18.2 | 42.8 | 40.4 | 0.986 | 0
277 | 2022-12-27 04:37 | 7.4 | 18.3 | 42.7 | 39.9 | 0.982 | 0
278 | 2022-12-27 04:38 | 7.8 | 18.4 | 42.7 | 40.1 | 0.982 | 0
279 | 2022-12-27 04:39 | 8.3 | 18.4 | 42.6 | 40 | 0 | 0
280 | 2022-12-27 04:40 | 8.7 | 18.6 | 42.4 | 39.8 | 0 | 0
281 | 2022-12-27 04:41 | 8.5 | 18.6 | 42 | 39.1 | 0 | 0
282 | 2022-12-27 04:42 | 8.6 | 18.6 | 41.7 | 38.4 | 0 | 0
283 | 2022-12-27 04:43 | 8.6 | 18.5 | 41.4 | 37.8 | 0 | 0
284 | 2022-12-27 04:44 | 8.1 | 18.4 | 41.1 | 37.2 | 0 | 0
285 | 2022-12-27 04:45 | 8 | 18.4 | 40.8 | 36.6 | 0 | 0
286 | 2022-12-27 04:46 | 8.5 | 18.4 | 40.5 | 36.1 | 0 | 0
287 | 2022-12-27 04:47 | 8.2 | 18.4 | 40.2 | 35.6 | 0 | 0
288 | 2022-12-27 04:48 | 8.3 | 18.4 | 39.9 | 35.1 | 0 | 0
289 | 2022-12-27 04:49 | 8.2 | 18.3 | 39.6 | 34.7 | 0 | 0
290 | 2022-12-27 04:50 | 9 | 18.4 | 39.3 | 34.2 | 0 | 0
291 | 2022-12-27 04:51 | 8.5 | 18.3 | 39 | 33.8 | 0 | 0
292 | 2022-12-27 04:52 | 9.1 | 18.3 | 38.8 | 33.4 | 0 | 0
293 | 2022-12-27 04:53 | 9 | 18.2 | 38.5 | 33 | 0 | 0
294 | 2022-12-27 04:54 | 9.5 | 18.3 | 38.2 | 32.6 | 0 | 0
295 | 2022-12-27 04:55 | 9.3 | 18.3 | 38 | 32.3 | 0 | 0
296 | 2022-12-27 04:56 | 9 | 18.3 | 37.7 | 31.9 | 0 | 0
297 | 2022-12-27 04:57 | 9.5 | 18.2 | 37.5 | 31.6 | 0 | 0
298 | 2022-12-27 04:58 | 9.1 | 18.2 | 37.2 | 31.3 | 0 | 0
299 | 2022-12-27 04:59 | 8.8 | 18.2 | 37 | 31 | 0 | 0
300 | 2022-12-27 05:00 | 8.7 | 18.3 | 36.8 | 30.7 | 0 | 0
301 | 2022-12-27 05:01 | 8.7 | 18.3 | 36.5 | 30.4 | 0 | 0
302 | 2022-12-27 05:02 | 8.3 | 18.3 | 36.3 | 30.1 | 0 | 0
303 | 2022-12-27 05:03 | 8 | 18.2 | 36.1 | 29.8 | 0 | 0
304 | 2022-12-27 05:04 | 8.5 | 18.2 | 35.8 | 29.6 | 0 | 0
305 | 2022-12-27 05:05 | 8.2 | 18.1 | 35.6 | 29.3 | 0 | 0
306 | 2022-12-27 05:06 | 8.2 | 18.2 | 35.3 | 32.3 | 0 | 0
307 | 2022-12-27 05:07 | 8 | 18.3 | 35.1 | 32 | 0.661 | 0
308 | 2022-12-27 05:08 | 8.4 | 18.2 | 41.1 | 32 | 0.978 | 0
309 | 2022-12-27 05:09 | 9 | 18.2 | 41.4 | 38.3 | 0.982 | 0
310 | 2022-12-27 05:10 | 8.9 | 18.2 | 40.4 | 38.3 | 0.981 | 0
311 | 2022-12-27 05:11 | 8.6 | 18.3 | 40.7 | 38 | 0.976 | 0
312 | 2022-12-27 05:12 | 8.7 | 18.4 | 40.5 | 38.3 | 0.979 | 0
313 | 2022-12-27 05:13 | 9.1 | 18.5 | 40.5 | 38.1 | 0.983 | 0
314 | 2022-12-27 05:14 | 9.1 | 18.6 | 40.5 | 39.9 | 1.456 | 0
315 | 2022-12-27 05:15 | 8.8 | 18.5 | 40.3 | 32.2 | 1.619 | 0
316 | 2022-12-27 05:16 | 8.5 | 18.5 | 40.1 | 37.9 | 1.374 | 0
317 | 2022-12-27 05:17 | 8.1 | 18.5 | 40.2 | 38.4 | 1.094 | 0
318 | 2022-12-27 05:18 | 8.3 | 18.4 | 39.3 | 38.3 | 1.087 | 0
319 | 2022-12-27 05:19 | 8.3 | 18.4 | 39.3 | 37.6 | 1.095 | 0
320 | 2022-12-27 05:20 | 8.3 | 18.4 | 39.3 | 37.7 | 1.089 | 0
321 | 2022-12-27 05:21 | 8.5 | 18.4 | 39.3 | 37.6 | 1.091 | 0
322 | 2022-12-27 05:22 | 8.5 | 18.3 | 39.2 | 37.6 | 1.096 | 0
323 | 2022-12-27 05:23 | 8.1 | 18.4 | 39.1 | 37.5 | 1.091 | 0
324 | 2022-12-27 05:24 | 7.8 | 18.3 | 39 | 37.4 | 1.092 | 0
325 | 2022-12-27 05:25 | 7.6 | 18.4 | 38.9 | 37.3 | 1.095 | 0
326 | 2022-12-27 05:26 | 7.5 | 18.4 | 38.8 | 37.2 | 1.085 | 0
327 | 2022-12-27 05:27 | 7.6 | 18.4 | 38.7 | 37.2 | 1.091 | 0
328 | 2022-12-27 05:28 | 7.5 | 18.4 | 38.7 | 37.1 | 1.091 | 0
329 | 2022-12-27 05:29 | 7.9 | 18.4 | 38.6 | 37.1 | 1.086 | 0
330 | 2022-12-27 05:30 | 7.6 | 18.4 | 38.5 | 37 | 1.089 | 0
331 | 2022-12-27 05:31 | 7.4 | 18.4 | 38.5 | 36.9 | 1.085 | 0
332 | 2022-12-27 05:32 | 7.5 | 18.4 | 38.7 | 36.9 | 1.089 | 0
333 | 2022-12-27 05:33 | 7.5 | 18.4 | 40.1 | 37.4 | 1.095 | 0
334 | 2022-12-27 05:34 | 7.6 | 18.4 | 40.2 | 38.5 | 1.085 | 0
335 | 2022-12-27 05:35 | 7.3 | 18.4 | 40.4 | 38.5 | 1.089 | 0
336 | 2022-12-27 05:36 | 7.4 | 18.4 | 40.6 | 38.7 | 1.088 | 0
337 | 2022-12-27 05:37 | 7.5 | 18.3 | 41 | 38.9 | 1.09 | 0
338 | 2022-12-27 05:38 | 7.3 | 18.4 | 41.4 | 39.3 | 1.084 | 0
339 | 2022-12-27 05:39 | 7.2 | 18.3 | 41.8 | 39.6 | 1.087 | 0
340 | 2022-12-27 05:40 | 7.2 | 18.3 | 42.2 | 40 | 1.09 | 0
341 | 2022-12-27 05:41 | 7.3 | 18.3 | 42.5 | 40.2 | 0 | 0
342 | 2022-12-27 05:42 | 7.2 | 18.3 | 42.3 | 39.9 | 0 | 0
343 | 2022-12-27 05:43 | 7.3 | 18.4 | 42 | 39.3 | 1.099 | 0
344 | 2022-12-27 05:44 | 7.3 | 18.4 | 42.9 | 40.9 | 1.076 | 0
345 | 2022-12-27 05:45 | 7.3 | 18.3 | 42.5 | 42.3 | 1.495 | 0
346 | 2022-12-27 05:46 | 7.2 | 18.3 | 42.5 | 36.2 | 1.377 | 0
347 | 2022-12-27 05:47 | 7.3 | 18.3 | 42.6 | 40.3 | 0.983 | 0
348 | 2022-12-27 05:48 | 7.3 | 18.3 | 42.5 | 40 | 0.98 | 0
349 | 2022-12-27 05:49 | 7.2 | 18.3 | 42.2 | 39.9 | 0.982 | 0
350 | 2022-12-27 05:50 | 7.1 | 18.4 | 42 | 39.6 | 0 | 0
351 | 2022-12-27 05:51 | 7.3 | 18.5 | 42 | 39.4 | 0 | 0
352 | 2022-12-27 05:52 | 7.2 | 18.6 | 41.7 | 39 | 0 | 0
353 | 2022-12-27 05:53 | 7.4 | 18.7 | 41.4 | 38.4 | 0 | 0
354 | 2022-12-27 05:54 | 7.1 | 18.5 | 41.2 | 37.9 | 0 | 0
355 | 2022-12-27 05:55 | 7.1 | 18.5 | 40.9 | 37.3 | 0 | 0
356 | 2022-12-27 05:56 | 7.2 | 18.4 | 40.6 | 36.8 | 0 | 0
357 | 2022-12-27 05:57 | 7.1 | 18.4 | 40.4 | 36.3 | 0 | 0
358 | 2022-12-27 05:58 | 7.2 | 18.4 | 40.1 | 35.9 | 0 | 0
359 | 2022-12-27 05:59 | 7 | 18.4 | 39.8 | 35.4 | 0 | 0
360 | 2022-12-27 06:00 | 6.9 | 18.4 | 39.5 | 35 | 0 | 0
361 | 2022-12-27 06:01 | 6.8 | 18.3 | 39.3 | 34.5 | 0 | 0
362 | 2022-12-27 06:02 | 6.8 | 18.4 | 39 | 34.1 | 0 | 0
363 | 2022-12-27 06:03 | 6.7 | 18.4 | 38.8 | 33.7 | 0 | 0
364 | 2022-12-27 06:04 | 7.1 | 18.3 | 38.5 | 33.3 | 0 | 0
365 | 2022-12-27 06:05 | 7.1 | 18.4 | 38.2 | 33 | 0 | 0
366 | 2022-12-27 06:06 | 7.1 | 18.4 | 38 | 32.6 | 0 | 0
367 | 2022-12-27 06:07 | 6.9 | 18.3 | 37.7 | 32.3 | 0 | 0
368 | 2022-12-27 06:08 | 6.7 | 18.3 | 37.5 | 31.9 | 0 | 0
369 | 2022-12-27 06:09 | 6.9 | 18.3 | 37.2 | 31.6 | 0 | 0
370 | 2022-12-27 06:10 | 6.8 | 18.2 | 37 | 31.3 | 0 | 0
371 | 2022-12-27 06:11 | 6.8 | 18.2 | 36.8 | 31 | 0 | 0
372 | 2022-12-27 06:12 | 6.8 | 18.3 | 36.5 | 30.7 | 0 | 0
373 | 2022-12-27 06:13 | 7 | 18.2 | 36.3 | 30.4 | 0 | 0
374 | 2022-12-27 06:14 | 6.7 | 18.3 | 36 | 30.1 | 0 | 0
375 | 2022-12-27 06:15 | 6.7 | 18.2 | 35.8 | 31.8 | 0 | 0
376 | 2022-12-27 06:16 | 6.7 | 18.2 | 35.6 | 32.7 | 0 | 0
377 | 2022-12-27 06:17 | 6.6 | 18.2 | 35.5 | 33.4 | 0.951 | 0
378 | 2022-12-27 06:18 | 6.7 | 18.3 | 40.9 | 34.2 | 0.982 | 0
379 | 2022-12-27 06:19 | 6.7 | 18.3 | 40.3 | 38.2 | 0.979 | 0
380 | 2022-12-27 06:20 | 6.6 | 18.3 | 40.2 | 37.6 | 0.981 | 0
381 | 2022-12-27 06:21 | 6.6 | 18.3 | 40.4 | 37.9 | 0.981 | 0
382 | 2022-12-27 06:22 | 6.5 | 18.3 | 40.4 | 38 | 0 | 0
383 | 2022-12-27 06:23 | 6.7 | 18.4 | 40.5 | 37.9 | 0 | 0
384 | 2022-12-27 06:24 | 6.7 | 18.5 | 40.2 | 37.5 | 0.979 | 0
385 | 2022-12-27 06:25 | 6.7 | 18.5 | 40.1 | 39.6 | 0.904 | 0
386 | 2022-12-27 06:26 | 7 | 18.5 | 40 | 39.7 | 0.024 | 0
387 | 2022-12-27 06:27 | 6.9 | 18.4 | 39.8 | 39.8 | 0.661 | 0
388 | 2022-12-27 06:28 | 7 | 18.3 | 39.9 | 38 | 0.97 | 0
389 | 2022-12-27 06:29 | 6.6 | 18.3 | 39.7 | 36.6 | 0.974 | 0
390 | 2022-12-27 06:30 | 6.5 | 18.3 | 39.7 | 37.9 | 0.98 | 0
391 | 2022-12-27 06:31 | 6.6 | 18.2 | 39.6 | 38 | 0.981 | 0
392 | 2022-12-27 06:32 | 6.7 | 18.3 | 39.2 | 38 | 0.976 | 0
393 | 2022-12-27 06:33 | 6.7 | 18.3 | 39 | 37.6 | 0.979 | 0
394 | 2022-12-27 06:34 | 6.5 | 18.3 | 39 | 37.5 | 0.976 | 0
395 | 2022-12-27 06:35 | 6.6 | 18.2 | 39 | 37.5 | 0.976 | 0
396 | 2022-12-27 06:36 | 6.5 | 18.2 | 38.9 | 37.4 | 0.976 | 0
397 | 2022-12-27 06:37 | 6.9 | 18.1 | 38.8 | 37.4 | 0.975 | 0
398 | 2022-12-27 06:38 | 6.8 | 18.1 | 38.7 | 37.3 | 0.973 | 0
399 | 2022-12-27 06:39 | 6.7 | 18.1 | 38.7 | 37.2 | 0.979 | 0
400 | 2022-12-27 06:40 | 6.6 | 18.1 | 38.6 | 37.1 | 0.973 | 0
401 | 2022-12-27 06:41 | 6.6 | 18.1 | 38.5 | 37.1 | 0.976 | 0
402 | 2022-12-27 06:42 | 6.6 | 18.1 | 38.4 | 37 | 0.975 | 0
403 | 2022-12-27 06:43 | 6.6 | 18.1 | 38.3 | 36.9 | 0.975 | 0
404 | 2022-12-27 06:44 | 6.7 | 18.1 | 38.3 | 36.9 | 0.978 | 0
405 | 2022-12-27 06:45 | 6.7 | 18.1 | 38.2 | 36.8 | 0.974 | 0
406 | 2022-12-27 06:46 | 6.5 | 18.1 | 38.1 | 36.7 | 0.971 | 0
407 | 2022-12-27 06:47 | 6.5 | 18.1 | 38.1 | 36.6 | 0.978 | 0
408 | 2022-12-27 06:48 | 6.6 | 18.1 | 38 | 36.6 | 1.55 | 0
409 | 2022-12-27 06:49 | 6.5 | 18.1 | 38 | 35.7 | 1.571 | 0
410 | 2022-12-27 06:50 | 6.4 | 18.1 | 38.1 | 36.5 | 1.56 | 0
411 | 2022-12-27 06:51 | 6.4 | 18.1 | 38.2 | 36.6 | 1.34 | 0
412 | 2022-12-27 06:52 | 6.7 | 18.2 | 38.2 | 36.3 | 0.975 | 0
413 | 2022-12-27 06:53 | 6.5 | 18.2 | 38.1 | 36.1 | 0.97 | 0
414 | 2022-12-27 06:54 | 6.8 | 18.3 | 38 | 36 | 0.021 | 0
415 | 2022-12-27 06:55 | 6.6 | 18.4 | 38 | 35.9 | 0 | 0
416 | 2022-12-27 06:56 | 6.5 | 18.5 | 37.8 | 35.6 | 0 | 0
417 | 2022-12-27 06:57 | 6.5 | 18.4 | 37.6 | 35.1 | 0 | 0
418 | 2022-12-27 06:58 | 6.5 | 18.4 | 37.3 | 34.6 | 0 | 0
419 | 2022-12-27 06:59 | 6.6 | 18.3 | 37.1 | 34.1 | 0 | 0
420 | 2022-12-27 07:00 | 6.6 | 18.2 | 36.8 | 33.7 | 0 | 0
421 | 2022-12-27 07:01 | 7 | 18.2 | 36.6 | 33.2 | 0 | 0
422 | 2022-12-27 07:02 | 6.9 | 18.2 | 36.3 | 32.8 | 0 | 0
423 | 2022-12-27 07:03 | 6.7 | 18.1 | 36.1 | 32.4 | 0 | 0
424 | 2022-12-27 07:04 | 6.7 | 18.1 | 35.8 | 32 | 0 | 0
425 | 2022-12-27 07:05 | 6.7 | 18.1 | 35.6 | 31.6 | 0 | 0
426 | 2022-12-27 07:06 | 6.8 | 18.1 | 35.4 | 31.2 | 0 | 0
427 | 2022-12-27 07:07 | 6.9 | 18.1 | 35.1 | 30.9 | 0 | 0
428 | 2022-12-27 07:08 | 6.8 | 18.1 | 34.9 | 30.6 | 0 | 0
429 | 2022-12-27 07:09 | 6.9 | 18.1 | 34.7 | 30.3 | 0 | 0
430 | 2022-12-27 07:10 | 6.9 | 18.1 | 34.5 | 30 | 0 | 0
431 | 2022-12-27 07:11 | 7.1 | 18.1 | 34.2 | 29.7 | 0.014 | 0
432 | 2022-12-27 07:12 | 6.9 | 18.1 | 34 | 32.4 | 0 | 0
433 | 2022-12-27 07:13 | 7 | 18.1 | 33.8 | 32.1 | 0.044 | 0
434 | 2022-12-27 07:14 | 7 | 18.1 | 35.5 | 33 | 1.041 | 0
435 | 2022-12-27 07:15 | 6.8 | 18.1 | 39.5 | 31.4 | 1.087 | 0
436 | 2022-12-27 07:16 | 7 | 18.1 | 38.7 | 37.5 | 1.085 | 0
437 | 2022-12-27 07:17 | 7 | 18 | 38.9 | 37 | 1.594 | 0
438 | 2022-12-27 07:18 | 6.8 | 18.1 | 38.8 | 33.9 | 1.632 | 0
439 | 2022-12-27 07:19 | 6.7 | 18.1 | 38.8 | 36.3 | 1.63 | 0
440 | 2022-12-27 07:20 | 6.9 | 18.1 | 38.7 | 36.5 | 1.629 | 0
441 | 2022-12-27 07:21 | 6.6 | 18.2 | 38.7 | 36.3 | 1.629 | 0
442 | 2022-12-27 07:22 | 6.7 | 18.3 | 38.7 | 36.4 | 1.637 | 0
443 | 2022-12-27 07:23 | 6.6 | 18.4 | 38.6 | 36.4 | 1.631 | 0
444 | 2022-12-27 07:24 | 6.6 | 18.5 | 38.5 | 36.5 | 1.633 | 0
445 | 2022-12-27 07:25 | 6.6 | 18.5 | 38.4 | 37.3 | 1.635 | 0
446 | 2022-12-27 07:26 | 6.7 | 18.6 | 38.3 | 37.2 | 1.62 | 0
447 | 2022-12-27 07:27 | 6.8 | 18.6 | 38.3 | 37.1 | 1.359 | 0
448 | 2022-12-27 07:28 | 6.6 | 18.5 | 38.3 | 36.9 | 1.088 | 0
449 | 2022-12-27 07:29 | 6.7 | 18.5 | 38.2 | 36.7 | 1.088 | 0
450 | 2022-12-27 07:30 | 6.6 | 18.4 | 38.1 | 36.6 | 1.087 | 0
451 | 2022-12-27 07:31 | 6.6 | 18.4 | 38 | 36.6 | 1.084 | 0
452 | 2022-12-27 07:32 | 6.6 | 18.3 | 37.9 | 36.5 | 1.08 | 0
453 | 2022-12-27 07:33 | 6.7 | 18.3 | 37.7 | 36.3 | 1.081 | 0
454 | 2022-12-27 07:34 | 6.4 | 18.3 | 37.9 | 36.2 | 1.086 | 1
455 | 2022-12-27 07:35 | 6.6 | 18.3 | 38.3 | 36.4 | 1.09 | 1
456 | 2022-12-27 07:36 | 6.4 | 18.2 | 38.7 | 36.7 | 1.086 | 2
457 | 2022-12-27 07:37 | 6.6 | 18.2 | 39 | 37.1 | 1.088 | 2
458 | 2022-12-27 07:38 | 6.5 | 18.3 | 39.4 | 37.4 | 1.085 | 2
459 | 2022-12-27 07:39 | 6.5 | 18.2 | 39.8 | 37.8 | 1.091 | 3
460 | 2022-12-27 07:40 | 6.4 | 18.2 | 40.1 | 38.2 | 1.094 | 3
461 | 2022-12-27 07:41 | 6.4 | 18.2 | 40.5 | 38.4 | 1.092 | 3
462 | 2022-12-27 07:42 | 6.6 | 18.2 | 40.9 | 38.8 | 1.084 | 4
463 | 2022-12-27 07:43 | 6.4 | 18.1 | 41.3 | 39.2 | 1.088 | 4
464 | 2022-12-27 07:44 | 6.4 | 18.3 | 41.7 | 39.5 | 0 | 5
465 | 2022-12-27 07:45 | 6.6 | 18.2 | 41.8 | 39.5 | 0 | 5
466 | 2022-12-27 07:46 | 6.3 | 18.2 | 42.1 | 39.1 | 1.092 | 5
467 | 2022-12-27 07:47 | 6.5 | 18.2 | 42.8 | 41.6 | 1.094 | 6
468 | 2022-12-27 07:48 | 6.5 | 18.1 | 43.1 | 42.2 | 1.61 | 6
469 | 2022-12-27 07:49 | 6.3 | 18.2 | 43.7 | 40.9 | 1.502 | 7
470 | 2022-12-27 07:50 | 6.3 | 18.2 | 43.5 | 41.5 | 1.191 | 7
471 | 2022-12-27 07:51 | 6.6 | 18.1 | 43.7 | 41.1 | 0.981 | 8
472 | 2022-12-27 07:52 | 6.3 | 18.2 | 44.3 | 41.1 | 0 | 8
473 | 2022-12-27 07:53 | 6.5 | 18.4 | 44.6 | 41.3 | 0 | 9
474 | 2022-12-27 07:54 | 6.4 | 18.6 | 44.3 | 40.9 | 0 | 9
475 | 2022-12-27 07:55 | 6.6 | 18.4 | 44 | 40.2 | 0 | 10
476 | 2022-12-27 07:56 | 6.5 | 18.3 | 43.6 | 39.6 | 0.02 | 10
477 | 2022-12-27 07:57 | 6.5 | 18.2 | 46 | 40.5 | 0.749 | 11
478 | 2022-12-27 07:58 | 6.5 | 17.9 | 46.7 | 40.1 | 1.09 | 11
479 | 2022-12-27 07:59 | 6.5 | 17.7 | 46.7 | 43.3 | 1.097 | 12
480 | 2022-12-27 08:00 | 6.4 | 17.7 | 46.7 | 44 | 1.632 | 12
481 | 2022-12-27 08:01 | 6.3 | 17.6 | 47.1 | 42.3 | 1.65 | 13
482 | 2022-12-27 08:02 | 6.3 | 17.3 | 46.7 | 43.2 | 1.955 | 13
483 | 2022-12-27 08:03 | 6.2 | 17.2 | 46.4 | 34.1 | 2.012 | 14
484 | 2022-12-27 08:04 | 6.1 | 17.1 | 46.4 | 40.6 | 2.009 | 14
485 | 2022-12-27 08:05 | 6.1 | 17.4 | 45.7 | 41 | 2.013 | 14
486 | 2022-12-27 08:06 | 6.4 | 17.7 | 45.9 | 40.4 | 2.008 | 15
487 | 2022-12-27 08:07 | 6.2 | 18 | 46.1 | 40.6 | 2.012 | 15
488 | 2022-12-27 08:08 | 6.2 | 18.2 | 46.1 | 40.8 | 2.017 | 15
489 | 2022-12-27 08:09 | 6.3 | 18.2 | 46.2 | 40.8 | 2.009 | 16
490 | 2022-12-27 08:10 | 6.5 | 18.3 | 46.3 | 40.9 | 2.01 | 16
491 | 2022-12-27 08:11 | 6.6 | 18.3 | 46.3 | 41 | 2.007 | 17
492 | 2022-12-27 08:12 | 6.5 | 18.4 | 46.5 | 41.1 | 2.012 | 17
493 | 2022-12-27 08:13 | 6.5 | 18.5 | 46.4 | 41.1 | 2.024 | 17
494 | 2022-12-27 08:14 | 6.5 | 18.7 | 46.3 | 41.1 | 2.007 | 18
495 | 2022-12-27 08:15 | 6.5 | 18.8 | 46 | 41 | 2.014 | 18
496 | 2022-12-27 08:16 | 6.5 | 18.7 | 45.5 | 40.7 | 2.013 | 19
497 | 2022-12-27 08:17 | 6.6 | 18.6 | 45.1 | 40.3 | 2.009 | 19
498 | 2022-12-27 08:18 | 6.5 | 18.6 | 44.7 | 40 | 2.01 | 19
499 | 2022-12-27 08:19 | 6.7 | 18.6 | 44.3 | 39.6 | 2.008 | 20
500 | 2022-12-27 08:20 | 6.6 | 18.7 | 44 | 39.3 | 2.006 | 20
501 | 2022-12-27 08:21 | 6.6 | 18.6 | 43.6 | 39 | 2.003 | 21
502 | 2022-12-27 08:22 | 6.5 | 18.5 | 43.2 | 38.7 | 2.007 | 21
503 | 2022-12-27 08:23 | 6.8 | 18.3 | 42.8 | 38.3 | 2.005 | 21
504 | 2022-12-27 08:24 | 6.7 | 18.3 | 42.4 | 38 | 2.002 | 22
505 | 2022-12-27 08:25 | 6.9 | 18.3 | 42.1 | 37.7 | 2.001 | 23
506 | 2022-12-27 08:26 | 6.7 | 18.2 | 41.6 | 37.4 | 2 | 23
507 | 2022-12-27 08:27 | 6.9 | 18.4 | 41.4 | 37.2 | 2.005 | 23
508 | 2022-12-27 08:28 | 7.1 | 18.6 | 41 | 37 | 2.001 | 24
509 | 2022-12-27 08:29 | 6.9 | 18.8 | 40.7 | 36.9 | 2.002 | 24
510 | 2022-12-27 08:30 | 7 | 19.1 | 40.4 | 36.7 | 2.001 | 24
511 | 2022-12-27 08:31 | 6.8 | 19.4 | 40.1 | 36.6 | 2.004 | 25
512 | 2022-12-27 08:32 | 6.9 | 19.6 | 39.8 | 36.4 | 1.992 | 25
513 | 2022-12-27 08:33 | 6.8 | 20 | 39.7 | 36.1 | 2.001 | 25
514 | 2022-12-27 08:34 | 6.9 | 19.9 | 39.8 | 36.1 | 2 | 25
515 | 2022-12-27 08:35 | 6.7 | 20.1 | 40.1 | 36.2 | 2 | 26
516 | 2022-12-27 08:36 | 6.8 | 20.3 | 40.2 | 36.5 | 2.003 | 26
517 | 2022-12-27 08:37 | 7 | 20.3 | 40.3 | 36.5 | 2.001 | 26
518 | 2022-12-27 08:38 | 7 | 20.5 | 40.6 | 36.7 | 1.998 | 27
519 | 2022-12-27 08:39 | 7.1 | 20.5 | 40.8 | 36.9 | 2.004 | 27
520 | 2022-12-27 08:40 | 6.9 | 20.5 | 41 | 37.1 | 1.998 | 27
521 | 2022-12-27 08:41 | 6.9 | 20.6 | 41.1 | 37.3 | 2.003 | 28
522 | 2022-12-27 08:42 | 6.9 | 20.6 | 41.3 | 37.3 | 1.996 | 28
523 | 2022-12-27 08:43 | 6.9 | 20.6 | 41.6 | 37.6 | 2.003 | 29
524 | 2022-12-27 08:44 | 7 | 20.8 | 41.6 | 37.7 | 1.998 | 29
525 | 2022-12-27 08:45 | 7.2 | 20.8 | 41.4 | 37.8 | 2.001 | 29
526 | 2022-12-27 08:46 | 7.3 | 20.9 | 41.1 | 37.6 | 2.002 | 30
527 | 2022-12-27 08:47 | 7.3 | 20.9 | 40.9 | 37.4 | 1.999 | 30
528 | 2022-12-27 08:48 | 7.1 | 20.9 | 40.5 | 37.2 | 1.989 | 31
529 | 2022-12-27 08:49 | 7 | 21 | 40.3 | 36.8 | 1.997 | 31
530 | 2022-12-27 08:50 | 7.1 | 21 | 40 | 36.7 | 1.999 | 31
531 | 2022-12-27 08:51 | 8 | 21.1 | 39.7 | 36.5 | 2.002 | 32
532 | 2022-12-27 08:52 | 7.8 | 21.1 | 39.4 | 36.2 | 2.001 | 32
533 | 2022-12-27 08:53 | 7.7 | 21 | 39.1 | 36 | 1.993 | 32
534 | 2022-12-27 08:54 | 7.5 | 21 | 38.9 | 35.8 | 1.997 | 32
535 | 2022-12-27 08:55 | 7.6 | 21 | 38.7 | 35.6 | 1.993 | 32
536 | 2022-12-27 08:56 | 7.5 | 21.1 | 38.4 | 35.4 | 1.996 | 32
537 | 2022-12-27 08:57 | 7.6 | 21 | 38.2 | 35.2 | 1.989 | 32
538 | 2022-12-27 08:58 | 7.6 | 21 | 38 | 35 | 1.995 | 32
539 | 2022-12-27 08:59 | 7.5 | 21 | 37.7 | 34.8 | 1.997 | 32
540 | 2022-12-27 09:00 | 7.3 | 21 | 37.5 | 34.6 | 1.992 | 32
541 | 2022-12-27 09:01 | 7.2 | 21 | 37.2 | 34.4 | 1.996 | 33
542 | 2022-12-27 09:02 | 7.2 | 21 | 37.1 | 34.2 | 1.99 | 33
543 | 2022-12-27 09:03 | 7.4 | 21 | 36.9 | 34 | 1.988 | 33
544 | 2022-12-27 09:04 | 7.2 | 20.9 | 37.1 | 34 | 1.991 | 33
545 | 2022-12-27 09:05 | 7.2 | 21 | 37.5 | 34.1 | 1.998 | 33
546 | 2022-12-27 09:06 | 7.3 | 21 | 37.6 | 34.4 | 1.993 | 34
547 | 2022-12-27 09:07 | 7.2 | 21 | 37.8 | 34.6 | 1.993 | 34
548 | 2022-12-27 09:08 | 7.5 | 21.1 | 38.2 | 34.7 | 1.997 | 34
549 | 2022-12-27 09:09 | 7.5 | 21.1 | 38.4 | 35 | 1.992 | 35
550 | 2022-12-27 09:10 | 7.4 | 21.1 | 38.6 | 35.2 | 1.995 | 35
551 | 2022-12-27 09:11 | 7.4 | 21.2 | 38.9 | 35.4 | 1.992 | 35
552 | 2022-12-27 09:12 | 7.6 | 21.1 | 39 | 35.6 | 2 | 35
553 | 2022-12-27 09:13 | 7.7 | 21.2 | 39.3 | 36.5 | 1.996 | 36
554 | 2022-12-27 09:14 | 7.4 | 21.2 | 39.5 | 36.8 | 2 | 36
555 | 2022-12-27 09:15 | 7.5 | 21.2 | 39.7 | 37 | 1.994 | 36
556 | 2022-12-27 09:16 | 7.6 | 21.1 | 39.7 | 37.1 | 1.834 | 36
557 | 2022-12-27 09:17 | 7.5 | 21.1 | 39.4 | 36.7 | 1.829 | 37
558 | 2022-12-27 09:18 | 7.5 | 21.1 | 39.3 | 36.7 | 1.826 | 37
559 | 2022-12-27 09:19 | 7.4 | 21.1 | 39.1 | 36.6 | 1.829 | 37
560 | 2022-12-27 09:20 | 7.6 | 21.1 | 38.9 | 36.3 | 1.821 | 37
561 | 2022-12-27 09:21 | 7.6 | 21.1 | 38.8 | 36.2 | 1.821 | 38
562 | 2022-12-27 09:22 | 7.5 | 21.2 | 38.5 | 36.1 | 1.826 | 38
563 | 2022-12-27 09:23 | 7.3 | 21.1 | 38.3 | 35.9 | 1.826 | 39
564 | 2022-12-27 09:24 | 7.3 | 21.1 | 38.1 | 35.7 | 1.931 | 39
565 | 2022-12-27 09:25 | 7.4 | 21 | 38 | 35.7 | 1.992 | 40
566 | 2022-12-27 09:26 | 7.3 | 21 | 37.8 | 34.8 | 1.981 | 40
567 | 2022-12-27 09:27 | 7.5 | 21 | 37.5 | 34.7 | 1.993 | 41
568 | 2022-12-27 09:28 | 7.3 | 21.1 | 37.3 | 34.4 | 1.992 | 41
569 | 2022-12-27 09:29 | 7.4 | 21.1 | 37.1 | 34.2 | 1.998 | 63
570 | 2022-12-27 09:30 | 7.4 | 21.2 | 36.8 | 34.1 | 1.987 | 194
571 | 2022-12-27 09:31 | 7.8 | 21.2 | 36.6 | 33.8 | 1.982 | 385
572 | 2022-12-27 09:32 | 7.5 | 21.2 | 36.4 | 33.7 | 1.985 | 523
573 | 2022-12-27 09:33 | 7.9 | 21.3 | 36.3 | 33.5 | 1.99 | 534
574 | 2022-12-27 09:34 | 8.1 | 21.2 | 36.5 | 33.5 | 1.99 | 539
575 | 2022-12-27 09:35 | 8.6 | 21.1 | 36.8 | 33.7 | 1.992 | 540
576 | 2022-12-27 09:36 | 8.4 | 21.2 | 37 | 33.9 | 1.992 | 542
577 | 2022-12-27 09:37 | 8.5 | 21.1 | 37.5 | 34.1 | 1.994 | 546
578 | 2022-12-27 09:38 | 8.5 | 21.2 | 37.8 | 34.5 | 1.991 | 549
579 | 2022-12-27 09:39 | 8.5 | 21.2 | 37.9 | 34.7 | 1.99 | 550
580 | 2022-12-27 09:40 | 9 | 21.3 | 38.2 | 34.8 | 1.992 | 552
581 | 2022-12-27 09:41 | 9.1 | 21.3 | 38.4 | 35.1 | 1.997 | 555
582 | 2022-12-27 09:42 | 9 | 21.3 | 38.6 | 35.3 | 1.995 | 557
583 | 2022-12-27 09:43 | 9.1 | 21.3 | 38.9 | 36.3 | 1.991 | 571
584 | 2022-12-27 09:44 | 9.6 | 21.4 | 39.2 | 36.5 | 1.993 | 575
585 | 2022-12-27 09:45 | 9.9 | 21.4 | 39.6 | 36.8 | 1.986 | 579
586 | 2022-12-27 09:46 | 9.4 | 21.3 | 39.8 | 37.1 | 1.828 | 581
587 | 2022-12-27 09:47 | 9.6 | 21.3 | 39.9 | 37 | 1.827 | 585
588 | 2022-12-27 09:48 | 9.5 | 21.4 | 39.9 | 37.2 | 1.822 | 587
589 | 2022-12-27 09:49 | 9.8 | 21.4 | 39.6 | 37.1 | 1.823 | 591
590 | 2022-12-27 09:50 | 9.7 | 21.4 | 39.4 | 36.9 | 1.818 | 595
591 | 2022-12-27 09:51 | 9.7 | 21.5 | 39.2 | 36.8 | 1.824 | 600
592 | 2022-12-27 09:52 | 9.7 | 21.4 | 39 | 36.6 | 1.824 | 603
593 | 2022-12-27 09:53 | 9.9 | 21.4 | 38.9 | 36.4 | 1.826 | 607
594 | 2022-12-27 09:54 | 10.1 | 21.4 | 38.7 | 36.3 | 1.82 | 610
595 | 2022-12-27 09:55 | 10.9 | 21.4 | 38.5 | 36.1 | 1.826 | 614
596 | 2022-12-27 09:56 | 10.5 | 21.5 | 38.3 | 36 | 1.824 | 619
597 | 2022-12-27 09:57 | 10.6 | 21.4 | 38.2 | 35.8 | 1.826 | 624
598 | 2022-12-27 09:58 | 10.5 | 21.5 | 38 | 35.7 | 1.825 | 628
599 | 2022-12-27 09:59 | 10.5 | 21.5 | 37.8 | 35.5 | 1.988 | 633
600 | 2022-12-27 10:00 | 10.5 | 21.4 | 37.6 | 34.3 | 1.992 | 637
601 | 2022-12-27 10:01 | 10.5 | 21.4 | 37.4 | 34.6 | 1.989 | 640
602 | 2022-12-27 10:02 | 10.8 | 21.5 | 37.2 | 34.4 | 1.994 | 645
603 | 2022-12-27 10:03 | 10.6 | 21.5 | 37 | 34.2 | 1.99 | 649
604 | 2022-12-27 10:04 | 10.7 | 21.4 | 37.2 | 34.1 | 1.993 | 652
605 | 2022-12-27 10:05 | 10.9 | 21.4 | 37.6 | 34.3 | 1.991 | 656
606 | 2022-12-27 10:06 | 11.3 | 21.5 | 37.9 | 34.7 | 1.999 | 659
607 | 2022-12-27 10:07 | 11.6 | 21.5 | 38.1 | 34.8 | 1.994 | 661
608 | 2022-12-27 10:08 | 12 | 21.6 | 38.3 | 35 | 1.992 | 665
609 | 2022-12-27 10:09 | 11.6 | 21.6 | 38.6 | 35.3 | 1.994 | 667
610 | 2022-12-27 10:10 | 11.7 | 21.6 | 38.9 | 35.5 | 1.997 | 670
611 | 2022-12-27 10:11 | 11.9 | 21.7 | 39.1 | 36.5 | 1.993 | 673
612 | 2022-12-27 10:12 | 12.6 | 21.7 | 39.4 | 36.7 | 1.994 | 675
613 | 2022-12-27 10:13 | 12.7 | 21.8 | 39.5 | 37 | 1.977 | 677
614 | 2022-12-27 10:14 | 12.4 | 21.7 | 39.3 | 37 | 1.818 | 679
615 | 2022-12-27 10:15 | 12.3 | 21.9 | 39.3 | 36.7 | 1.829 | 682
616 | 2022-12-27 10:16 | 12.3 | 21.8 | 39.1 | 36.6 | 1.827 | 683
617 | 2022-12-27 10:17 | 12.1 | 21.8 | 38.9 | 36.5 | 1.821 | 685
618 | 2022-12-27 10:18 | 12.3 | 21.8 | 38.7 | 36.3 | 1.821 | 687
619 | 2022-12-27 10:19 | 12.8 | 21.8 | 38.6 | 36.2 | 1.817 | 688
620 | 2022-12-27 10:20 | 13.6 | 21.8 | 38.5 | 36.1 | 1.822 | 689
621 | 2022-12-27 10:21 | 13.5 | 21.9 | 38.3 | 36 | 1.82 | 691
622 | 2022-12-27 10:22 | 13.1 | 21.6 | 38.1 | 36.7 | 1.821 | 694
623 | 2022-12-27 10:23 | 13.1 | 21.2 | 38 | 36.5 | 1.819 | 695
624 | 2022-12-27 10:24 | 13.3 | 20.9 | 38 | 36.5 | 1.79 | 698
625 | 2022-12-27 10:25 | 13.8 | 20.7 | 37.9 | 36.4 | 1.491 | 699
626 | 2022-12-27 10:26 | 13.8 | 20.5 | 37.8 | 36 | 1.504 | 700
627 | 2022-12-27 10:27 | 14.3 | 20.3 | 37.6 | 36 | 1.498 | 703
628 | 2022-12-27 10:28 | 14 | 20.3 | 37.5 | 35.9 | 1.776 | 705
629 | 2022-12-27 10:29 | 13.9 | 20.2 | 37.4 | 34.4 | 1.98 | 707
630 | 2022-12-27 10:30 | 14.6 | 20.3 | 37.2 | 34.1 | 1.984 | 710
631 | 2022-12-27 10:31 | 14.6 | 20.6 | 36.9 | 34.3 | 1.985 | 712
632 | 2022-12-27 10:32 | 14.8 | 20.7 | 36.7 | 34 | 1.987 | 715
633 | 2022-12-27 10:33 | 15 | 21 | 36.6 | 33.8 | 1.988 | 718
634 | 2022-12-27 10:34 | 15.5 | 21.2 | 36.7 | 33.8 | 1.985 | 720
635 | 2022-12-27 10:35 | 16 | 21.3 | 37.1 | 33.9 | 1.988 | 723
636 | 2022-12-27 10:36 | 15.4 | 21.4 | 37.3 | 34.3 | 1.984 | 725
637 | 2022-12-27 10:37 | 15.7 | 21.5 | 37.5 | 34.4 | 1.989 | 727
638 | 2022-12-27 10:38 | 15.5 | 21.6 | 37.8 | 34.6 | 1.99 | 729
639 | 2022-12-27 10:39 | 15.4 | 21.7 | 38.1 | 34.9 | 1.985 | 733
640 | 2022-12-27 10:40 | 15.9 | 21.7 | 38.3 | 35.8 | 1.988 | 733
641 | 2022-12-27 10:41 | 16.3 | 21.7 | 38.7 | 36.1 | 1.995 | 736
642 | 2022-12-27 10:42 | 15.9 | 21.8 | 38.9 | 36.4 | 1.981 | 739
643 | 2022-12-27 10:43 | 15.6 | 21.8 | 39.3 | 36.6 | 1.826 | 741
644 | 2022-12-27 10:44 | 16 | 21.9 | 39.6 | 36.6 | 1.822 | 743
645 | 2022-12-27 10:45 | 16.1 | 21.9 | 39.7 | 36.9 | 1.827 | 746
646 | 2022-12-27 10:46 | 15.8 | 21.8 | 39.6 | 37.6 | 1.826 | 748
647 | 2022-12-27 10:47 | 16.1 | 21.6 | 39.3 | 37.9 | 1.824 | 749
648 | 2022-12-27 10:48 | 16 | 21.2 | 39.3 | 37.7 | 1.818 | 753
649 | 2022-12-27 10:49 | 16.2 | 21 | 39.3 | 37.7 | 1.732 | 755
650 | 2022-12-27 10:50 | 16.3 | 20.7 | 39.2 | 37.6 | 1.502 | 757
651 | 2022-12-27 10:51 | 16.6 | 20.6 | 39.1 | 37.3 | 1.501 | 757
652 | 2022-12-27 10:52 | 16.8 | 20.5 | 39 | 37.3 | 1.503 | 762
653 | 2022-12-27 10:53 | 16.9 | 20.4 | 38.9 | 37.2 | 1.497 | 763
654 | 2022-12-27 10:54 | 16.6 | 20.3 | 38.8 | 37.1 | 1.499 | 762
655 | 2022-12-27 10:55 | 16.3 | 20.3 | 38.7 | 37 | 1.812 | 764
656 | 2022-12-27 10:56 | 16.2 | 20.5 | 38.6 | 36 | 1.818 | 765
657 | 2022-12-27 10:57 | 16.9 | 20.6 | 38.4 | 36.1 | 1.815 | 769
658 | 2022-12-27 10:58 | 16.4 | 20.9 | 38.1 | 35.9 | 1.817 | 769
659 | 2022-12-27 10:59 | 16.5 | 21.1 | 38 | 35.7 | 1.817 | 771
660 | 2022-12-27 11:00 | 16.3 | 21.4 | 37.8 | 35.6 | 1.821 | 772
661 | 2022-12-27 11:01 | 16.4 | 21.5 | 37.6 | 35.4 | 1.818 | 774
662 | 2022-12-27 11:02 | 16.2 | 21.6 | 37.5 | 35.3 | 1.822 | 776
663 | 2022-12-27 11:03 | 16.8 | 21.7 | 37.5 | 35.1 | 1.817 | 779
664 | 2022-12-27 11:04 | 16.8 | 21.7 | 37.8 | 35.1 | 1.82 | 781
665 | 2022-12-27 11:05 | 16.8 | 21.7 | 38.1 | 35.4 | 1.818 | 785
666 | 2022-12-27 11:06 | 17 | 21.7 | 38.4 | 35.8 | 1.827 | 785
667 | 2022-12-27 11:07 | 17.2 | 21.7 | 38.7 | 36 | 1.825 | 786
668 | 2022-12-27 11:08 | 17.3 | 21.8 | 39.1 | 36.3 | 1.823 | 787
669 | 2022-12-27 11:09 | 17.5 | 21.8 | 39.3 | 36.6 | 1.824 | 790
670 | 2022-12-27 11:10 | 17 | 21.9 | 39.6 | 36.8 | 1.821 | 790
671 | 2022-12-27 11:11 | 16.7 | 21.9 | 39.9 | 37.6 | 1.826 | 794
672 | 2022-12-27 11:12 | 16.7 | 21.6 | 40.3 | 38.3 | 1.826 | 794
673 | 2022-12-27 11:13 | 16.3 | 21.2 | 40.7 | 38.7 | 1.823 | 798
674 | 2022-12-27 11:14 | 16.3 | 21 | 41.1 | 39 | 1.736 | 800
675 | 2022-12-27 11:15 | 16.3 | 20.8 | 41.4 | 39.2 | 1.509 | 802
676 | 2022-12-27 11:16 | 16.4 | 20.6 | 41.8 | 39.5 | 1.51 | 804
677 | 2022-12-27 11:17 | 16.2 | 20.5 | 42.1 | 39.7 | 1.509 | 806
678 | 2022-12-27 11:18 | 16.4 | 20.4 | 42.4 | 40 | 1.818 | 807
679 | 2022-12-27 11:19 | 16.8 | 20.4 | 42.7 | 37.9 | 1.843 | 810
680 | 2022-12-27 11:20 | 16.9 | 20.3 | 43 | 40.4 | 1.84 | 812
681 | 2022-12-27 11:21 | 16.7 | 20.4 | 43 | 40.6 | 1.922 | 811
682 | 2022-12-27 11:22 | 16.6 | 20.6 | 43.6 | 40.6 | 1.892 | 812
683 | 2022-12-27 11:23 | 17.3 | 20.9 | 43.9 | 39.9 | 1.89 | 816
684 | 2022-12-27 11:24 | 17 | 21.1 | 43.9 | 40.5 | 1.893 | 817
685 | 2022-12-27 11:25 | 16.9 | 21.4 | 43.6 | 40.4 | 1.893 | 819
686 | 2022-12-27 11:26 | 16.4 | 21.8 | 43.5 | 41.2 | 1.887 | 821
687 | 2022-12-27 11:27 | 16.6 | 22.1 | 43.2 | 41.1 | 1.89 | 823
688 | 2022-12-27 11:28 | 16.9 | 22.3 | 43.1 | 40.9 | 1.748 | 824
689 | 2022-12-27 11:29 | 16.7 | 22.3 | 43 | 40.5 | 1.83 | 826
690 | 2022-12-27 11:30 | 16.7 | 22.2 | 42.9 | 40.9 | 1.826 | 827
691 | 2022-12-27 11:31 | 16.7 | 21.8 | 42.7 | 41 | 1.826 | 828
692 | 2022-12-27 11:32 | 16.7 | 21.5 | 42.5 | 40.8 | 1.798 | 831
693 | 2022-12-27 11:33 | 16.7 | 21.2 | 42.5 | 40.6 | 1.505 | 830
694 | 2022-12-27 11:34 | 17.1 | 21 | 42.3 | 40.2 | 1.507 | 832
695 | 2022-12-27 11:35 | 17 | 20.8 | 42.2 | 40.2 | 1.505 | 832
696 | 2022-12-27 11:36 | 17.1 | 20.7 | 42.1 | 40.1 | 1.502 | 833
697 | 2022-12-27 11:37 | 17.3 | 20.6 | 42 | 39.9 | 1.507 | 834
698 | 2022-12-27 11:38 | 17.3 | 20.5 | 41.9 | 39.9 | 1.507 | 837
699 | 2022-12-27 11:39 | 17.4 | 20.5 | 41.7 | 39.8 | 1.503 | 837
700 | 2022-12-27 11:40 | 16.9 | 20.5 | 41.6 | 39.6 | 1.504 | 840
701 | 2022-12-27 11:41 | 16.6 | 20.4 | 41.5 | 39.5 | 1.511 | 838
702 | 2022-12-27 11:42 | 16.9 | 20.4 | 41.3 | 39.4 | 1.499 | 841
703 | 2022-12-27 11:43 | 17 | 20.5 | 41.2 | 39.3 | 1.816 | 841
704 | 2022-12-27 11:44 | 17.4 | 20.7 | 41.1 | 37.8 | 1.822 | 841
705 | 2022-12-27 11:45 | 17.3 | 20.8 | 40.8 | 38.2 | 1.829 | 842
706 | 2022-12-27 11:46 | 17.4 | 21 | 40.5 | 38.1 | 1.827 | 840
707 | 2022-12-27 11:47 | 17.8 | 21.3 | 40.3 | 37.8 | 1.824 | 844
708 | 2022-12-27 11:48 | 17.6 | 21.6 | 40.1 | 38.2 | 1.828 | 843
709 | 2022-12-27 11:49 | 17.8 | 21.8 | 40 | 38 | 1.824 | 845
710 | 2022-12-27 11:50 | 18 | 21.9 | 39.9 | 37.9 | 1.817 | 845
711 | 2022-12-27 11:51 | 18.1 | 21.9 | 39.7 | 37.8 | 1.616 | 850
712 | 2022-12-27 11:52 | 18 | 22 | 39.6 | 37.5 | 1.611 | 849
713 | 2022-12-27 11:53 | 18.3 | 22.1 | 39.5 | 37.4 | 1.613 | 851
714 | 2022-12-27 11:54 | 18.4 | 22 | 39.3 | 38.3 | 1.616 | 850
715 | 2022-12-27 11:55 | 17.6 | 21.6 | 39.2 | 38.2 | 1.614 | 849
716 | 2022-12-27 11:56 | 17.7 | 21.3 | 39.3 | 38.1 | 1.57 | 851
717 | 2022-12-27 11:57 | 17.4 | 21 | 39.2 | 38.1 | 1.2 | 850
718 | 2022-12-27 11:58 | 17.5 | 20.9 | 39.2 | 37.7 | 1.502 | 847
719 | 2022-12-27 11:59 | 17.8 | 20.8 | 39.1 | 37.2 | 1.498 | 846
720 | 2022-12-27 12:00 | 17.5 | 20.7 | 38.9 | 37.2 | 1.504 | 850
721 | 2022-12-27 12:01 | 17.6 | 20.6 | 38.7 | 37.1 | 1.5 | 850
722 | 2022-12-27 12:02 | 17.7 | 20.5 | 38.6 | 36.9 | 1.495 | 852
723 | 2022-12-27 12:03 | 18 | 20.5 | 38.6 | 36.8 | 1.497 | 853
724 | 2022-12-27 12:04 | 18.2 | 20.4 | 38.8 | 36.9 | 1.505 | 857
725 | 2022-12-27 12:05 | 17.3 | 20.4 | 39.3 | 37.2 | 1.499 | 853
726 | 2022-12-27 12:06 | 17 | 20.4 | 39.6 | 37.6 | 1.503 | 856
727 | 2022-12-27 12:07 | 17.2 | 20.4 | 40.1 | 37.9 | 1.79 | 853
728 | 2022-12-27 12:08 | 17.1 | 20.6 | 40.3 | 35.6 | 1.825 | 851
729 | 2022-12-27 12:09 | 17.4 | 20.7 | 40.7 | 37.7 | 1.826 | 847
730 | 2022-12-27 12:10 | 17.5 | 20.9 | 40.8 | 38 | 1.828 | 853
731 | 2022-12-27 12:11 | 17.4 | 21.1 | 41.1 | 38.2 | 1.828 | 855
732 | 2022-12-27 12:12 | 17.6 | 21.5 | 41 | 38.3 | 1.832 | 857
733 | 2022-12-27 12:13 | 17.3 | 21.9 | 40.8 | 38.2 | 1.826 | 856
734 | 2022-12-27 12:14 | 17.2 | 22 | 40.6 | 38 | 1.822 | 854
735 | 2022-12-27 12:15 | 17.3 | 22.1 | 40.5 | 37.9 | 1.83 | 853
736 | 2022-12-27 12:16 | 17.7 | 22.2 | 40.3 | 37.8 | 1.83 | 852
737 | 2022-12-27 12:17 | 18.1 | 22.1 | 40.1 | 38.4 | 1.827 | 854
738 | 2022-12-27 12:18 | 18.2 | 21.9 | 40 | 38.5 | 1.825 | 858
739 | 2022-12-27 12:19 | 18.2 | 21.4 | 40 | 38.4 | 1.823 | 855
740 | 2022-12-27 12:20 | 17.6 | 21.2 | 39.9 | 38.3 | 1.642 | 861
741 | 2022-12-27 12:21 | 18.2 | 21 | 39.8 | 38 | 1.503 | 857
742 | 2022-12-27 12:22 | 18.2 | 20.9 | 39.7 | 38.5 | 1.503 | 853
743 | 2022-12-27 12:23 | 18.4 | 20.8 | 39.6 | 38.5 | 1.505 | 855
744 | 2022-12-27 12:24 | 18.5 | 20.6 | 39.5 | 38.4 | 1.491 | 852
745 | 2022-12-27 12:25 | 18.4 | 20.6 | 39.5 | 38.3 | 1.162 | 845
746 | 2022-12-27 12:26 | 18.3 | 20.5 | 39.4 | 38.2 | 1.088 | 849
747 | 2022-12-27 12:27 | 17.9 | 20.5 | 39.4 | 37.9 | 1.085 | 852
748 | 2022-12-27 12:28 | 18 | 20.5 | 39.3 | 37.9 | 1.087 | 845
749 | 2022-12-27 12:29 | 18.2 | 20.5 | 39.3 | 37.8 | 1.088 | 844
750 | 2022-12-27 12:30 | 18 | 20.4 | 39.2 | 37.8 | 1.093 | 847
751 | 2022-12-27 12:31 | 17.6 | 20.5 | 39.1 | 37.7 | 1.578 | 847
752 | 2022-12-27 12:32 | 18.1 | 20.6 | 39 | 35.3 | 1.793 | 848
753 | 2022-12-27 12:33 | 18.1 | 20.7 | 38.9 | 36.6 | 1.825 | 853
754 | 2022-12-27 12:34 | 18.2 | 20.9 | 38.9 | 36.4 | 1.82 | 850
755 | 2022-12-27 12:35 | 17.5 | 21.3 | 39.2 | 36.5 | 1.82 | 838
756 | 2022-12-27 12:36 | 18.3 | 21.6 | 39.7 | 36.7 | 1.823 | 840
757 | 2022-12-27 12:37 | 18.2 | 21.8 | 40 | 37.2 | 1.819 | 845
758 | 2022-12-27 12:38 | 18.4 | 21.9 | 40.3 | 37.4 | 1.828 | 844
759 | 2022-12-27 12:39 | 18.1 | 21.9 | 40.5 | 37.7 | 1.826 | 846
760 | 2022-12-27 12:40 | 17.9 | 22.2 | 41 | 37.9 | 1.83 | 846
761 | 2022-12-27 12:41 | 18.4 | 22.1 | 41.1 | 39.2 | 1.826 | 843
762 | 2022-12-27 12:42 | 18.2 | 21.8 | 41 | 39.4 | 1.833 | 845
763 | 2022-12-27 12:43 | 18.2 | 21.4 | 40.9 | 39.2 | 1.814 | 843
764 | 2022-12-27 12:44 | 18.6 | 21.2 | 40.9 | 39.2 | 1.579 | 840
765 | 2022-12-27 12:45 | 18.5 | 21 | 40.8 | 38.9 | 1.503 | 844
766 | 2022-12-27 12:46 | 18.6 | 20.9 | 40.7 | 38.9 | 1.5 | 836
767 | 2022-12-27 12:47 | 18.6 | 20.9 | 40.6 | 38.8 | 1.502 | 834
768 | 2022-12-27 12:48 | 18.8 | 20.7 | 40.5 | 38.7 | 1.507 | 832
769 | 2022-12-27 12:49 | 18.1 | 20.7 | 40.4 | 38.6 | 1.499 | 835
770 | 2022-12-27 12:50 | 17.9 | 20.6 | 40.3 | 38.5 | 1.503 | 839
771 | 2022-12-27 12:51 | 18 | 20.6 | 40.2 | 38.4 | 1.499 | 833
772 | 2022-12-27 12:52 | 17.7 | 20.6 | 40 | 38.9 | 1.496 | 830
773 | 2022-12-27 12:53 | 18.2 | 20.5 | 39.9 | 38.8 | 1.501 | 822
774 | 2022-12-27 12:54 | 17.9 | 20.5 | 39.8 | 38.7 | 1.499 | 827
775 | 2022-12-27 12:55 | 17.7 | 20.4 | 39.8 | 38.7 | 1.097 | 835
776 | 2022-12-27 12:56 | 18 | 20.4 | 39.8 | 38.5 | 1.089 | 820
777 | 2022-12-27 12:57 | 18.3 | 20.6 | 39.8 | 38.3 | 1.605 | 815
778 | 2022-12-27 12:58 | 18.9 | 20.7 | 39.7 | 36.7 | 1.62 | 820
779 | 2022-12-27 12:59 | 18.9 | 20.7 | 39.6 | 37.4 | 1.793 | 830
780 | 2022-12-27 13:00 | 18.7 | 21 | 39.3 | 34.8 | 1.882 | 834
781 | 2022-12-27 13:01 | 18.5 | 21.4 | 39 | 36.3 | 1.878 | 821
782 | 2022-12-27 13:02 | 18.6 | 21.6 | 38.6 | 36.2 | 1.88 | 823
783 | 2022-12-27 13:03 | 18.5 | 21.9 | 38.5 | 35.8 | 1.988 | 831
784 | 2022-12-27 13:04 | 18.2 | 22 | 38.8 | 34.9 | 1.987 | 839
785 | 2022-12-27 13:05 | 18.7 | 22 | 39.1 | 35.7 | 1.992 | 839
786 | 2022-12-27 13:06 | 18.6 | 22 | 39.2 | 36.8 | 2.002 | 838
787 | 2022-12-27 13:07 | 18.1 | 21.9 | 39.2 | 37.6 | 1.994 | 839
788 | 2022-12-27 13:08 | 18.3 | 21.7 | 39.3 | 37.7 | 1.963 | 831
789 | 2022-12-27 13:09 | 18.1 | 21.4 | 39.5 | 37.7 | 1.569 | 831
790 | 2022-12-27 13:10 | 18.1 | 21.2 | 39.9 | 37.7 | 1.494 | 826
791 | 2022-12-27 13:11 | 18.3 | 21 | 40.3 | 38.2 | 1.498 | 829
792 | 2022-12-27 13:12 | 18.3 | 21 | 40.6 | 38.5 | 1.5 | 829
793 | 2022-12-27 13:13 | 17.8 | 20.9 | 41 | 38.8 | 1.499 | 832
794 | 2022-12-27 13:14 | 17.5 | 20.8 | 41.3 | 39.1 | 1.506 | 827
795 | 2022-12-27 13:15 | 17.9 | 20.7 | 41.8 | 39.4 | 1.502 | 825
796 | 2022-12-27 13:16 | 17.9 | 20.6 | 42.2 | 39.8 | 1.506 | 822
797 | 2022-12-27 13:17 | 17.5 | 20.5 | 42.7 | 40.1 | 1.501 | 822
798 | 2022-12-27 13:18 | 17.8 | 20.6 | 42.9 | 40.6 | 1.501 | 824
799 | 2022-12-27 13:19 | 18.1 | 20.5 | 43.4 | 40.8 | 1.507 | 820
800 | 2022-12-27 13:20 | 18 | 20.4 | 43.9 | 41.3 | 1.506 | 820
801 | 2022-12-27 13:21 | 17.9 | 20.5 | 44.3 | 42.4 | 1.509 | 823
802 | 2022-12-27 13:22 | 18 | 20.4 | 44.2 | 43.1 | 1.511 | 819
803 | 2022-12-27 13:23 | 18.1 | 20.4 | 44.1 | 42.7 | 1.498 | 816
804 | 2022-12-27 13:24 | 18 | 20.5 | 44.2 | 42.7 | 1.141 | 814
805 | 2022-12-27 13:25 | 18.4 | 20.7 | 44.2 | 42.6 | 1.576 | 814
806 | 2022-12-27 13:26 | 18.1 | 20.7 | 44.1 | 37.5 | 1.62 | 810
807 | 2022-12-27 13:27 | 18.6 | 20.7 | 43.9 | 41.2 | 1.621 | 813
808 | 2022-12-27 13:28 | 18.2 | 21 | 43.5 | 41.2 | 1.626 | 812
809 | 2022-12-27 13:29 | 18.2 | 21.4 | 43.2 | 40.8 | 1.619 | 807
810 | 2022-12-27 13:30 | 18.6 | 21.9 | 43.1 | 40.6 | 1.623 | 811
811 | 2022-12-27 13:31 | 18.2 | 22.1 | 43 | 40.6 | 1.621 | 809
812 | 2022-12-27 13:32 | 18.6 | 22.3 | 42.9 | 40.4 | 1.624 | 805
813 | 2022-12-27 13:33 | 18.2 | 22.2 | 42.7 | 42.1 | 1.829 | 807
814 | 2022-12-27 13:34 | 18.4 | 21.8 | 42.6 | 40.3 | 1.828 | 803
815 | 2022-12-27 13:35 | 18.1 | 21.4 | 42.6 | 41.5 | 1.734 | 790
816 | 2022-12-27 13:36 | 18 | 21.2 | 42.5 | 41.5 | 1.499 | 792
817 | 2022-12-27 13:37 | 17.9 | 21.1 | 42.4 | 41.3 | 1.453 | 795
818 | 2022-12-27 13:38 | 18.2 | 20.9 | 42.4 | 41.3 | 1.319 | 796
819 | 2022-12-27 13:39 | 18.5 | 20.8 | 42.3 | 41.2 | 1.011 | 798
820 | 2022-12-27 13:40 | 18.3 | 20.7 | 42.3 | 40.9 | 0.974 | 798
821 | 2022-12-27 13:41 | 18.6 | 20.6 | 42.2 | 40.7 | 0.98 | 797
822 | 2022-12-27 13:42 | 18.3 | 20.5 | 42.1 | 40.6 | 0.975 | 799
823 | 2022-12-27 13:43 | 18.3 | 20.5 | 42 | 40.6 | 0.976 | 799
824 | 2022-12-27 13:44 | 18.2 | 20.4 | 41.9 | 40.5 | 1.386 | 796
825 | 2022-12-27 13:45 | 18.1 | 20.4 | 41.9 | 38.6 | 1.499 | 791
826 | 2022-12-27 13:46 | 18.2 | 20.3 | 41.7 | 39.8 | 1.502 | 788
827 | 2022-12-27 13:47 | 18.2 | 20.4 | 41.6 | 40.4 | 1.506 | 786
828 | 2022-12-27 13:48 | 18.1 | 20.5 | 41.3 | 40.3 | 1.761 | 780
829 | 2022-12-27 13:49 | 18.3 | 20.7 | 41.3 | 37.9 | 1.795 | 779
830 | 2022-12-27 13:50 | 18.4 | 20.7 | 41.3 | 39.1 | 1.619 | 779
831 | 2022-12-27 13:51 | 18.2 | 20.9 | 41 | 38.8 | 1.619 | 779
832 | 2022-12-27 13:52 | 18.3 | 21.4 | 40.8 | 38.6 | 1.617 | 778
833 | 2022-12-27 13:53 | 18.2 | 21.6 | 40.7 | 38.5 | 1.62 | 775
834 | 2022-12-27 13:54 | 18.6 | 21.9 | 40.6 | 38.4 | 1.614 | 773
835 | 2022-12-27 13:55 | 18.6 | 22.1 | 40.4 | 38.3 | 1.616 | 771
836 | 2022-12-27 13:56 | 18.6 | 22.1 | 40.3 | 39.2 | 1.615 | 768
837 | 2022-12-27 13:57 | 18.7 | 21.8 | 40.1 | 39.1 | 1.613 | 769
838 | 2022-12-27 13:58 | 18.3 | 21.5 | 40.1 | 38.9 | 1.543 | 767
839 | 2022-12-27 13:59 | 18.3 | 21.3 | 40.1 | 38.9 | 1.437 | 763
840 | 2022-12-27 14:00 | 18.3 | 21.1 | 40 | 38.5 | 1.499 | 762
841 | 2022-12-27 14:01 | 18.1 | 20.9 | 39.9 | 38.1 | 1.5 | 752
842 | 2022-12-27 14:02 | 18.1 | 20.8 | 39.8 | 38 | 1.505 | 753
843 | 2022-12-27 14:03 | 18.1 | 20.8 | 39.6 | 37.9 | 1.5 | 752
844 | 2022-12-27 14:04 | 18.3 | 20.8 | 39.9 | 37.8 | 1.506 | 751
845 | 2022-12-27 14:05 | 18.7 | 20.7 | 40.3 | 38.1 | 1.504 | 749
846 | 2022-12-27 14:06 | 18.3 | 20.6 | 40.7 | 38.5 | 1.501 | 742
847 | 2022-12-27 14:07 | 18.4 | 20.6 | 41 | 38.8 | 1.504 | 744
848 | 2022-12-27 14:08 | 18.6 | 20.6 | 41.4 | 39.1 | 1.505 | 741
849 | 2022-12-27 14:09 | 18.7 | 20.6 | 41.6 | 39.5 | 1.511 | 737
850 | 2022-12-27 14:10 | 18.7 | 20.6 | 41.7 | 39.6 | 1.502 | 736
851 | 2022-12-27 14:11 | 18.9 | 20.5 | 41.5 | 39.7 | 1.503 | 733
852 | 2022-12-27 14:12 | 18.8 | 20.5 | 41.4 | 39.4 | 1.503 | 732
853 | 2022-12-27 14:13 | 18.7 | 20.5 | 41.3 | 39.4 | 1.506 | 730
854 | 2022-12-27 14:14 | 18.6 | 20.5 | 41.2 | 39.3 | 1.508 | 726
855 | 2022-12-27 14:15 | 18.2 | 20.4 | 41.1 | 39.6 | 1.503 | 723
856 | 2022-12-27 14:16 | 18.5 | 20.6 | 41 | 39.8 | 1.74 | 720
857 | 2022-12-27 14:17 | 18.7 | 20.7 | 40.9 | 38.9 | 1.822 | 721
858 | 2022-12-27 14:18 | 18.9 | 20.7 | 40.8 | 38.6 | 1.778 | 716
859 | 2022-12-27 14:19 | 19.2 | 20.9 | 40.6 | 38.6 | 1.615 | 710
860 | 2022-12-27 14:20 | 19.1 | 21.2 | 40.3 | 38.2 | 1.616 | 709
861 | 2022-12-27 14:21 | 18.2 | 21.6 | 40.2 | 38 | 1.622 | 709
862 | 2022-12-27 14:22 | 18.6 | 21.8 | 40.1 | 38.4 | 1.613 | 705
863 | 2022-12-27 14:23 | 18.5 | 22.1 | 40 | 38.6 | 0 | 704
864 | 2022-12-27 14:24 | 18.4 | 22.1 | 39.9 | 38.5 | 0 | 706
865 | 2022-12-27 14:25 | 18.3 | 21.9 | 39.8 | 38.3 | 0 | 705
866 | 2022-12-27 14:26 | 18.4 | 21.5 | 39.7 | 38.1 | 1.511 | 696
867 | 2022-12-27 14:27 | 18.4 | 21.2 | 39.7 | 39.2 | 1.104 | 697
868 | 2022-12-27 14:28 | 18.5 | 21 | 39.7 | 39.3 | 0.978 | 694
869 | 2022-12-27 14:29 | 18.4 | 20.9 | 39.7 | 38.3 | 0.976 | 692
870 | 2022-12-27 14:30 | 18.4 | 20.8 | 39.7 | 38.3 | 0.972 | 687
871 | 2022-12-27 14:31 | 18.3 | 20.8 | 39.7 | 38.4 | 0.972 | 685
872 | 2022-12-27 14:32 | 18.2 | 20.6 | 39.5 | 38.3 | 0.972 | 684
873 | 2022-12-27 14:33 | 18.2 | 20.7 | 39.4 | 38.1 | 0.973 | 679
874 | 2022-12-27 14:34 | 18.4 | 20.5 | 39.7 | 38.1 | 0.972 | 680
875 | 2022-12-27 14:35 | 18 | 20.4 | 40 | 38.3 | 1.444 | 678
876 | 2022-12-27 14:36 | 18.2 | 20.5 | 40.6 | 36.5 | 1.502 | 673
877 | 2022-12-27 14:37 | 18.3 | 20.5 | 40.9 | 38.7 | 1.502 | 667
878 | 2022-12-27 14:38 | 18.7 | 20.4 | 41.3 | 39 | 1.503 | 664
879 | 2022-12-27 14:39 | 18.8 | 20.3 | 41.6 | 39.4 | 1.584 | 662
880 | 2022-12-27 14:40 | 18.4 | 20.5 | 42.3 | 39.4 | 1.827 | 657
881 | 2022-12-27 14:41 | 18.3 | 20.6 | 42.4 | 39.3 | 1.829 | 653
882 | 2022-12-27 14:42 | 18.1 | 20.8 | 42 | 39.9 | 1.832 | 648
883 | 2022-12-27 14:43 | 17.7 | 21.3 | 41.8 | 39.7 | 1.827 | 649
884 | 2022-12-27 14:44 | 17.7 | 21.6 | 41.8 | 39.7 | 1.794 | 647
885 | 2022-12-27 14:45 | 18 | 21.8 | 41.7 | 39.6 | 1.624 | 645
886 | 2022-12-27 14:46 | 17.9 | 22.1 | 41.6 | 39.3 | 1.622 | 642
887 | 2022-12-27 14:47 | 17.6 | 22.2 | 41.5 | 39.3 | 1.624 | 641
888 | 2022-12-27 14:48 | 18.1 | 22 | 41.3 | 40.2 | 1.627 | 639
889 | 2022-12-27 14:49 | 18.2 | 21.8 | 41.2 | 40.1 | 1.613 | 631
890 | 2022-12-27 14:50 | 18.2 | 21.4 | 41.2 | 40 | 1.526 | 626
891 | 2022-12-27 14:51 | 18.3 | 21.2 | 41.2 | 39.9 | 1.086 | 622
892 | 2022-12-27 14:52 | 17.9 | 21.1 | 41.1 | 39.6 | 1.086 | 619
893 | 2022-12-27 14:53 | 17.7 | 20.9 | 41.1 | 39.5 | 1.091 | 616
894 | 2022-12-27 14:54 | 17.6 | 20.8 | 41 | 39.5 | 1.091 | 616
895 | 2022-12-27 14:55 | 17.3 | 20.8 | 40.8 | 39.4 | 1.09 | 616
896 | 2022-12-27 14:56 | 17.8 | 20.8 | 40.8 | 40.4 | 1.44 | 613
897 | 2022-12-27 14:57 | 17.6 | 20.7 | 40.7 | 40.2 | 1.511 | 607
898 | 2022-12-27 14:58 | 17.9 | 20.6 | 40.7 | 39.6 | 1.5 | 601
899 | 2022-12-27 14:59 | 18 | 20.6 | 40.7 | 39.6 | 1.469 | 600
900 | 2022-12-27 15:00 | 17.9 | 20.6 | 40.5 | 39.6 | 1.34 | 599
901 | 2022-12-27 15:01 | 17.7 | 20.5 | 40.5 | 39.4 | 1.008 | 595
902 | 2022-12-27 15:02 | 18.1 | 20.6 | 40.5 | 39.2 | 0.974 | 591
903 | 2022-12-27 15:03 | 18.1 | 20.4 | 40.4 | 39 | 0.973 | 588
904 | 2022-12-27 15:04 | 17.6 | 20.4 | 40.7 | 39 | 0.973 | 584
905 | 2022-12-27 15:05 | 17.5 | 20.4 | 41.1 | 39.2 | 0.978 | 582
906 | 2022-12-27 15:06 | 17.7 | 20.4 | 41.5 | 39.6 | 0.977 | 574
907 | 2022-12-27 15:07 | 17.9 | 20.4 | 41.9 | 40 | 1.684 | 570
908 | 2022-12-27 15:08 | 18 | 20.6 | 41.5 | 37.5 | 1.83 | 566
909 | 2022-12-27 15:09 | 17.8 | 20.5 | 41.3 | 39 | 1.827 | 561
910 | 2022-12-27 15:10 | 18 | 20.8 | 41.1 | 39.1 | 1.828 | 560
911 | 2022-12-27 15:11 | 18 | 21.1 | 40.9 | 38.9 | 1.825 | 556
912 | 2022-12-27 15:12 | 18 | 21.5 | 40.9 | 38.8 | 1.676 | 553
913 | 2022-12-27 15:13 | 18.3 | 21.7 | 40.8 | 38.6 | 1.613 | 549
914 | 2022-12-27 15:14 | 18.1 | 21.9 | 40.7 | 38.4 | 1.618 | 546
915 | 2022-12-27 15:15 | 18.2 | 22 | 40.5 | 38.3 | 1.624 | 544
916 | 2022-12-27 15:16 | 17.9 | 22.1 | 40.3 | 38.2 | 1.618 | 541
917 | 2022-12-27 15:17 | 18.1 | 21.9 | 40.1 | 39.1 | 1.621 | 535
918 | 2022-12-27 15:18 | 18.3 | 21.6 | 40.1 | 39 | 1.615 | 531
919 | 2022-12-27 15:19 | 18.1 | 21.4 | 40.1 | 38.9 | 1.525 | 528
920 | 2022-12-27 15:20 | 18 | 21.1 | 40 | 38.8 | 1.09 | 524
921 | 2022-12-27 15:21 | 18.1 | 21 | 40 | 38.5 | 1.085 | 520
922 | 2022-12-27 15:22 | 17.8 | 21 | 39.9 | 38.5 | 1.087 | 516
923 | 2022-12-27 15:23 | 17.7 | 20.8 | 39.8 | 38.4 | 1.469 | 510
924 | 2022-12-27 15:24 | 17.6 | 20.7 | 39.8 | 36.1 | 1.503 | 505
925 | 2022-12-27 15:25 | 17.3 | 20.7 | 39.6 | 37.8 | 1.502 | 502
926 | 2022-12-27 15:26 | 17.6 | 20.6 | 39.5 | 37.8 | 1.503 | 499
927 | 2022-12-27 15:27 | 17.4 | 20.6 | 39.3 | 38.4 | 1.503 | 494
928 | 2022-12-27 15:28 | 17.3 | 20.6 | 39.2 | 38.3 | 1.499 | 489
929 | 2022-12-27 15:29 | 17.2 | 20.6 | 39.1 | 38.2 | 1.5 | 487
930 | 2022-12-27 15:30 | 17.3 | 20.5 | 39.1 | 38.2 | 1.483 | 484
931 | 2022-12-27 15:31 | 17.5 | 20.5 | 39.1 | 38.1 | 1.408 | 481
932 | 2022-12-27 15:32 | 17.1 | 20.5 | 39 | 38.1 | 1.162 | 479
933 | 2022-12-27 15:33 | 17.3 | 20.3 | 39 | 37.9 | 0.973 | 476
934 | 2022-12-27 15:34 | 17.1 | 20.4 | 39.1 | 37.7 | 0.972 | 472
935 | 2022-12-27 15:35 | 17.3 | 20.4 | 39.5 | 37.8 | 0.971 | 469
936 | 2022-12-27 15:36 | 17.5 | 20.5 | 39.9 | 38.1 | 1.555 | 465
937 | 2022-12-27 15:37 | 17.6 | 20.6 | 40.3 | 38 | 1.553 | 461
938 | 2022-12-27 15:38 | 17.3 | 20.6 | 40.6 | 38.8 | 1.558 | 457
939 | 2022-12-27 15:39 | 17.4 | 20.9 | 40.9 | 39 | 1.451 | 453
940 | 2022-12-27 15:40 | 17.5 | 21.1 | 41.7 | 39.3 | 0.989 | 449
941 | 2022-12-27 15:41 | 17.7 | 21.4 | 41.3 | 39.3 | 1.599 | 446
942 | 2022-12-27 15:42 | 17.4 | 21.6 | 41.3 | 38.1 | 1.624 | 441
943 | 2022-12-27 15:43 | 17.6 | 21.8 | 41.1 | 38.9 | 1.623 | 437
944 | 2022-12-27 15:44 | 17.6 | 21.9 | 40.9 | 38.7 | 1.619 | 434
945 | 2022-12-27 15:45 | 17.9 | 22 | 40.8 | 38.5 | 1.617 | 429
946 | 2022-12-27 15:46 | 17.7 | 22.1 | 40.8 | 38.5 | 1.622 | 425
947 | 2022-12-27 15:47 | 17.4 | 22.1 | 40.6 | 39.5 | 1.626 | 421
948 | 2022-12-27 15:48 | 17.3 | 21.7 | 40.5 | 39.4 | 1.617 | 416
949 | 2022-12-27 15:49 | 17.3 | 21.4 | 40.5 | 39.3 | 1.569 | 411
950 | 2022-12-27 15:50 | 17.5 | 21.1 | 40.5 | 39.3 | 1.127 | 405
951 | 2022-12-27 15:51 | 17.1 | 21.1 | 40.4 | 39 | 1.406 | 401
952 | 2022-12-27 15:52 | 17 | 21 | 40.3 | 38.8 | 1.5 | 394
953 | 2022-12-27 15:53 | 17.2 | 20.8 | 40.2 | 38.3 | 1.507 | 391
954 | 2022-12-27 15:54 | 17 | 20.8 | 40.1 | 38.3 | 1.505 | 386
955 | 2022-12-27 15:55 | 17 | 20.8 | 39.9 | 38.2 | 1.501 | 381
956 | 2022-12-27 15:56 | 17.2 | 20.7 | 39.8 | 38 | 1.507 | 377
957 | 2022-12-27 15:57 | 17.2 | 20.6 | 39.7 | 37.9 | 1.503 | 372
958 | 2022-12-27 15:58 | 17.1 | 20.6 | 39.6 | 38.7 | 1.504 | 367
959 | 2022-12-27 15:59 | 16.6 | 20.6 | 39.4 | 38.5 | 1.499 | 364
960 | 2022-12-27 16:00 | 16.3 | 20.6 | 39.4 | 38.4 | 1.496 | 360
961 | 2022-12-27 16:01 | 16 | 20.6 | 39.4 | 38.4 | 1.462 | 355
962 | 2022-12-27 16:02 | 16.1 | 20.5 | 39.4 | 38.4 | 1.308 | 350
963 | 2022-12-27 16:03 | 16.1 | 20.4 | 39.4 | 38.3 | 0 | 346
964 | 2022-12-27 16:04 | 16.2 | 20.4 | 39.5 | 38.2 | 0 | 343
965 | 2022-12-27 16:05 | 16.3 | 20.4 | 39.3 | 38 | 0.978 | 338
966 | 2022-12-27 16:06 | 16.5 | 20.4 | 40.1 | 37.7 | 0.956 | 334
967 | 2022-12-27 16:07 | 16.5 | 20.3 | 41.2 | 39.6 | 0.217 | 328
968 | 2022-12-27 16:08 | 16.4 | 20.5 | 41.4 | 40.7 | 0.924 | 323
969 | 2022-12-27 16:09 | 16.3 | 20.5 | 41.9 | 37.8 | 0.956 | 317
970 | 2022-12-27 16:10 | 15.8 | 20.6 | 42.1 | 39.4 | 0.954 | 311
971 | 2022-12-27 16:11 | 15.5 | 20.7 | 42.4 | 39.5 | 0.955 | 306
972 | 2022-12-27 16:12 | 15.4 | 21.1 | 42.9 | 40.1 | 0.959 | 302
973 | 2022-12-27 16:13 | 15.1 | 21.4 | 43.3 | 40.3 | 0.954 | 297
974 | 2022-12-27 16:14 | 15 | 21.6 | 43.1 | 40.8 | 1.245 | 294
975 | 2022-12-27 16:15 | 15.1 | 21.7 | 43 | 40 | 1.615 | 289
976 | 2022-12-27 16:16 | 15.2 | 21.8 | 42.6 | 39.8 | 1.622 | 284
977 | 2022-12-27 16:17 | 15 | 21.9 | 42.6 | 40.1 | 1.622 | 279
978 | 2022-12-27 16:18 | 14.9 | 22.1 | 42.2 | 40 | 1.74 | 276
979 | 2022-12-27 16:19 | 14.9 | 22.1 | 42.3 | 39.1 | 1.826 | 270
980 | 2022-12-27 16:20 | 14.7 | 22.1 | 42.2 | 40.2 | 1.833 | 264
981 | 2022-12-27 16:21 | 14.7 | 21.9 | 42 | 40.3 | 1.832 | 260
982 | 2022-12-27 16:22 | 14.6 | 21.5 | 41.9 | 40.1 | 1.825 | 243
983 | 2022-12-27 16:23 | 14.2 | 21.3 | 41.8 | 40.1 | 1.715 | 241
984 | 2022-12-27 16:24 | 14.1 | 21.1 | 41.7 | 39.9 | 1.501 | 241
985 | 2022-12-27 16:25 | 14 | 21 | 41.6 | 39.7 | 1.507 | 235
986 | 2022-12-27 16:26 | 13.7 | 21 | 41.5 | 39.5 | 1.511 | 231
987 | 2022-12-27 16:27 | 13.5 | 20.8 | 41.3 | 39.4 | 1.506 | 225
988 | 2022-12-27 16:28 | 13.5 | 20.8 | 41.2 | 39.3 | 1.507 | 219
989 | 2022-12-27 16:29 | 13.3 | 20.7 | 41.2 | 39.3 | 1.507 | 214
990 | 2022-12-27 16:30 | 13 | 20.7 | 41 | 39.8 | 1.506 | 209
991 | 2022-12-27 16:31 | 13 | 20.6 | 40.9 | 39.7 | 0 | 202
992 | 2022-12-27 16:32 | 12.9 | 20.7 | 40.8 | 39.6 | 0 | 197
993 | 2022-12-27 16:33 | 13 | 20.6 | 40.6 | 39.4 | 0 | 191
994 | 2022-12-27 16:34 | 12.8 | 20.6 | 40.4 | 39 | 0 | 185
995 | 2022-12-27 16:35 | 12.6 | 20.5 | 40.2 | 38.6 | 0 | 179
996 | 2022-12-27 16:36 | 12.5 | 20.5 | 40 | 38.2 | 0 | 173
997 | 2022-12-27 16:37 | 12.5 | 20.5 | 39.8 | 37.9 | 0.779 | 167
998 | 2022-12-27 16:38 | 12.6 | 20.5 | 40.5 | 37.1 | 0 | 131
999 | 2022-12-27 16:39 | 12.4 | 20.4 | 40.5 | 38.8 | 0 | 84
1000 | 2022-12-27 16:40 | 12.4 | 20.4 | 40.4 | 39.2 | 0.916 | 43
1001 | 2022-12-27 16:41 | 12.3 | 20.3 | 40.5 | 30.5 | 1.4 | 24
1002 | 2022-12-27 16:42 | 12.2 | 20.4 | 40.2 | 36.5 | 1.545 | 18
1003 | 2022-12-27 16:43 | 12.1 | 20.5 | 40 | 37.4 | 1.55 | 17
1004 | 2022-12-27 16:44 | 11.9 | 20.7 | 39.5 | 37.1 | 1.545 | 16
1005 | 2022-12-27 16:45 | 12 | 21.1 | 39.4 | 36.8 | 1.845 | 14
1006 | 2022-12-27 16:46 | 12 | 21.4 | 39.4 | 35.3 | 1.895 | 14
1007 | 2022-12-27 16:47 | 12 | 21.6 | 39.2 | 36.6 | 1.992 | 14
1008 | 2022-12-27 16:48 | 11.9 | 21.8 | 38.8 | 36.7 | 2.003 | 12
1009 | 2022-12-27 16:49 | 11.7 | 21.9 | 38.7 | 36.5 | 1.993 | 11
1010 | 2022-12-27 16:50 | 11.9 | 22 | 38.6 | 36.4 | 1.828 | 10
1011 | 2022-12-27 16:51 | 11.7 | 22 | 38.5 | 36.4 | 1.827 | 10
1012 | 2022-12-27 16:52 | 11.8 | 21.8 | 38.3 | 36.9 | 1.827 | 9
1013 | 2022-12-27 16:53 | 11.6 | 21.5 | 38.2 | 36.8 | 1.82 | 9
1014 | 2022-12-27 16:54 | 11.6 | 21.2 | 38.1 | 36.7 | 1.712 | 9
1015 | 2022-12-27 16:55 | 11.5 | 21.1 | 38 | 36.5 | 1.502 | 9
1016 | 2022-12-27 16:56 | 11.5 | 20.9 | 38 | 36.3 | 1.5 | 8
1017 | 2022-12-27 16:57 | 11.4 | 20.8 | 37.8 | 36.2 | 1.494 | 7
1018 | 2022-12-27 16:58 | 11.4 | 20.8 | 37.7 | 36.1 | 1.501 | 7
1019 | 2022-12-27 16:59 | 11.3 | 20.7 | 37.6 | 36 | 1.498 | 6
1020 | 2022-12-27 17:00 | 11.3 | 20.6 | 37.5 | 35.9 | 1.496 | 5
1021 | 2022-12-27 17:01 | 11.3 | 20.6 | 37.4 | 35.8 | 1.499 | 5
1022 | 2022-12-27 17:02 | 11.2 | 20.5 | 37.3 | 36.1 | 1.499 | 4
1023 | 2022-12-27 17:03 | 11.2 | 20.5 | 37.2 | 36.2 | 1.495 | 4
1024 | 2022-12-27 17:04 | 11 | 20.5 | 37.4 | 36.3 | 1.491 | 3
1025 | 2022-12-27 17:05 | 11 | 20.4 | 37.7 | 36.4 | 1.297 | 3
1026 | 2022-12-27 17:06 | 11.1 | 20.4 | 38.2 | 36.7 | 1.087 | 2
1027 | 2022-12-27 17:07 | 11 | 20.4 | 38.5 | 36.8 | 1.083 | 2
1028 | 2022-12-27 17:08 | 11.3 | 20.4 | 38.9 | 37.1 | 1.088 | 2
1029 | 2022-12-27 17:09 | 11.4 | 20.4 | 39.3 | 37.4 | 1.091 | 1
1030 | 2022-12-27 17:10 | 11.1 | 20.4 | 39.7 | 37.9 | 1.086 | 1
1031 | 2022-12-27 17:11 | 11.3 | 20.3 | 40 | 38.2 | 1.085 | 1
1032 | 2022-12-27 17:12 | 10.9 | 20.5 | 40.5 | 38.5 | 1.581 | 0
1033 | 2022-12-27 17:13 | 10.9 | 20.6 | 40.8 | 35 | 1.619 | 0
1034 | 2022-12-27 17:14 | 11 | 20.5 | 41.2 | 38.4 | 1.617 | 0
1035 | 2022-12-27 17:15 | 11 | 20.8 | 41.7 | 38.9 | 1.622 | 0
1036 | 2022-12-27 17:16 | 10.8 | 21.1 | 41.3 | 39.2 | 1.794 | 0
1037 | 2022-12-27 17:17 | 10.6 | 21.4 | 41.2 | 38.7 | 1.836 | 0
1038 | 2022-12-27 17:18 | 11 | 21.6 | 41.1 | 39 | 1.835 | 0
1039 | 2022-12-27 17:19 | 10.9 | 21.8 | 40.9 | 39.1 | 1.834 | 0
1040 | 2022-12-27 17:20 | 10.7 | 21.9 | 40.8 | 38.8 | 1.828 | 0
1041 | 2022-12-27 17:21 | 10.8 | 21.9 | 40.7 | 38.7 | 1.818 | 0
1042 | 2022-12-27 17:22 | 10.8 | 21.9 | 40.6 | 38.6 | 1.757 | 0
1043 | 2022-12-27 17:23 | 10.5 | 21.9 | 40.4 | 38.5 | 1.565 | 0
1044 | 2022-12-27 17:24 | 10.5 | 21.9 | 40.3 | 39.2 | 1.556 | 0
1045 | 2022-12-27 17:25 | 10.3 | 21.6 | 40.2 | 39.2 | 1.562 | 0
1046 | 2022-12-27 17:26 | 10.5 | 21.4 | 40.1 | 39.1 | 1.539 | 0
1047 | 2022-12-27 17:27 | 10.3 | 21.1 | 40.1 | 39.1 | 1.314 | 0
1048 | 2022-12-27 17:28 | 10.2 | 20.9 | 40.1 | 38.9 | 0.971 | 0
1049 | 2022-12-27 17:29 | 10.2 | 20.8 | 40 | 38.7 | 0.074 | 0
1050 | 2022-12-27 17:30 | 10.2 | 20.6 | 40 | 38.6 | 0 | 0
1051 | 2022-12-27 17:31 | 10.2 | 20.5 | 39.8 | 38.4 | 0 | 0
1052 | 2022-12-27 17:32 | 10.2 | 20.4 | 39.6 | 38 | 0 | 0
1053 | 2022-12-27 17:33 | 10.1 | 20.3 | 39.3 | 37.7 | 0.808 | 0
1054 | 2022-12-27 17:34 | 10.4 | 20.3 | 39.9 | 38.5 | 0.463 | 0
1055 | 2022-12-27 17:35 | 10.2 | 20.2 | 40.3 | 39.1 | 1.08 | 0
1056 | 2022-12-27 17:36 | 10.6 | 20.2 | 40.7 | 38.4 | 1.089 | 0
1057 | 2022-12-27 17:37 | 10.3 | 20.3 | 41.2 | 39 | 1.612 | 0
1058 | 2022-12-27 17:38 | 10.3 | 20.3 | 40.5 | 37.5 | 1.629 | 0
1059 | 2022-12-27 17:39 | 10.3 | 20.3 | 40.5 | 38 | 1.855 | 0
1060 | 2022-12-27 17:40 | 10.4 | 20.5 | 40.2 | 35.9 | 1.891 | 0
1061 | 2022-12-27 17:41 | 10.2 | 20.7 | 40.2 | 37.2 | 1.886 | 0
1062 | 2022-12-27 17:42 | 10.2 | 20.9 | 39.9 | 37.2 | 1.887 | 0
1063 | 2022-12-27 17:43 | 10.2 | 21.3 | 39.7 | 37 | 1.893 | 0
1064 | 2022-12-27 17:44 | 10.1 | 21.5 | 39.6 | 36.8 | 1.888 | 0
1065 | 2022-12-27 17:45 | 10 | 21.8 | 39.3 | 37.4 | 1.985 | 0
1066 | 2022-12-27 17:46 | 10 | 21.9 | 39.2 | 37.3 | 1.999 | 0
1067 | 2022-12-27 17:47 | 10 | 22.1 | 39 | 36.8 | 1.982 | 0
1068 | 2022-12-27 17:48 | 9.9 | 21.9 | 38.9 | 37.5 | 1.828 | 0
1069 | 2022-12-27 17:49 | 9.9 | 21.6 | 38.7 | 37.2 | 1.83 | 0
1070 | 2022-12-27 17:50 | 10.1 | 21.3 | 38.7 | 37.2 | 1.709 | 0
1071 | 2022-12-27 17:51 | 10.1 | 21.1 | 38.6 | 37 | 1.507 | 0
1072 | 2022-12-27 17:52 | 10 | 21 | 38.5 | 36.8 | 1.498 | 0
1073 | 2022-12-27 17:53 | 10 | 20.9 | 38.3 | 36.7 | 1.499 | 0
1074 | 2022-12-27 17:54 | 10.1 | 20.7 | 38.3 | 36.6 | 1.497 | 0
1075 | 2022-12-27 17:55 | 10 | 20.7 | 38.1 | 36.5 | 1.502 | 0
1076 | 2022-12-27 17:56 | 10 | 20.6 | 38 | 37 | 1.497 | 0
1077 | 2022-12-27 17:57 | 10 | 20.6 | 37.9 | 37.1 | 1.502 | 0
1078 | 2022-12-27 17:58 | 9.9 | 20.6 | 37.9 | 37 | 1.503 | 0
1079 | 2022-12-27 17:59 | 10 | 20.5 | 37.9 | 36.9 | 1.488 | 0
1080 | 2022-12-27 18:00 | 10.2 | 20.5 | 37.8 | 36.9 | 1.412 | 0
1081 | 2022-12-27 18:01 | 9.8 | 20.4 | 37.8 | 36.8 | 1.272 | 0
1082 | 2022-12-27 18:02 | 10.1 | 20.3 | 37.7 | 36.7 | 0 | 0
1083 | 2022-12-27 18:03 | 10 | 20.2 | 37.6 | 36.5 | 0 | 0
1084 | 2022-12-27 18:04 | 10.1 | 20.2 | 37.5 | 36.3 | 0.974 | 0
1085 | 2022-12-27 18:05 | 9.7 | 20.2 | 38.1 | 36.7 | 0.955 | 0
1086 | 2022-12-27 18:06 | 9.9 | 20.3 | 38.4 | 37.7 | 0.922 | 0
1087 | 2022-12-27 18:07 | 9.9 | 20.4 | 39 | 34.9 | 0.944 | 0
1088 | 2022-12-27 18:08 | 9.7 | 20.4 | 39.3 | 36.9 | 0.951 | 0
1089 | 2022-12-27 18:09 | 9.6 | 20.6 | 39.6 | 37.1 | 1.54 | 0
1090 | 2022-12-27 18:10 | 9.8 | 20.9 | 39.9 | 35.9 | 1.621 | 0
1091 | 2022-12-27 18:11 | 10.1 | 21.1 | 40.2 | 37.5 | 1.621 | 0
1092 | 2022-12-27 18:12 | 9.9 | 21.4 | 40.7 | 38 | 1.626 | 0
1093 | 2022-12-27 18:13 | 9.9 | 21.5 | 41 | 38.3 | 1.624 | 0
1094 | 2022-12-27 18:14 | 9.6 | 21.7 | 41.4 | 38.7 | 1.622 | 0
1095 | 2022-12-27 18:15 | 9.6 | 21.8 | 41.7 | 39 | 1.62 | 0
1096 | 2022-12-27 18:16 | 9.6 | 21.9 | 42 | 39.3 | 1.623 | 0
1097 | 2022-12-27 18:17 | 9.8 | 22 | 42.1 | 39.6 | 1.626 | 0
1098 | 2022-12-27 18:18 | 9.8 | 22.1 | 41.8 | 39.5 | 1.784 | 0
1099 | 2022-12-27 18:19 | 9.7 | 21.9 | 41.7 | 40.2 | 1.831 | 0
1100 | 2022-12-27 18:20 | 9.6 | 21.6 | 41.7 | 39.8 | 1.829 | 0
1101 | 2022-12-27 18:21 | 9.6 | 21.3 | 41.5 | 39.9 | 1.779 | 0
1102 | 2022-12-27 18:22 | 9.9 | 21.1 | 41.3 | 39.6 | 1.505 | 0
1103 | 2022-12-27 18:23 | 9.6 | 21 | 41.3 | 39.2 | 1.501 | 0
1104 | 2022-12-27 18:24 | 9.7 | 20.9 | 41.2 | 39.3 | 1.511 | 0
1105 | 2022-12-27 18:25 | 9.6 | 20.8 | 41 | 39.1 | 1.499 | 0
1106 | 2022-12-27 18:26 | 9.5 | 20.7 | 40.9 | 39 | 1.504 | 0
1107 | 2022-12-27 18:27 | 9.6 | 20.8 | 40.9 | 38.9 | 1.508 | 0
1108 | 2022-12-27 18:28 | 9.4 | 20.6 | 40.7 | 38.8 | 1.502 | 0
1109 | 2022-12-27 18:29 | 9.5 | 20.6 | 40.6 | 38.7 | 1.508 | 0
1110 | 2022-12-27 18:30 | 9.4 | 20.6 | 40.4 | 38.6 | 1.507 | 0
1111 | 2022-12-27 18:31 | 9.6 | 20.5 | 40.3 | 39.3 | 1.504 | 0
1112 | 2022-12-27 18:32 | 9.4 | 20.5 | 40.2 | 39.2 | 1.788 | 0
1113 | 2022-12-27 18:33 | 9.5 | 20.5 | 40.2 | 35.9 | 1.83 | 0
1114 | 2022-12-27 18:34 | 9.5 | 20.4 | 40.1 | 38.7 | 1.819 | 0
1115 | 2022-12-27 18:35 | 9.4 | 20.4 | 39.8 | 38.7 | 1.682 | 0
1116 | 2022-12-27 18:36 | 9.3 | 20.4 | 39.8 | 38.3 | 0.978 | 0
1117 | 2022-12-27 18:37 | 9.3 | 20.4 | 39.7 | 37.8 | 0.976 | 0
1118 | 2022-12-27 18:38 | 9.3 | 20.4 | 39.7 | 37.6 | 0.977 | 0
1119 | 2022-12-27 18:39 | 9.3 | 20.5 | 39.6 | 37.5 | 0 | 0
1120 | 2022-12-27 18:40 | 9.3 | 20.6 | 39.5 | 37.4 | 0 | 0
1121 | 2022-12-27 18:41 | 9.3 | 20.6 | 39.4 | 37.2 | 0.979 | 0
1122 | 2022-12-27 18:42 | 9.2 | 20.6 | 39.3 | 38.8 | 0.938 | 0
1123 | 2022-12-27 18:43 | 9.2 | 20.7 | 39.2 | 38.8 | 0.924 | 0
1124 | 2022-12-27 18:44 | 9.2 | 20.7 | 39.1 | 32.9 | 1.467 | 0
1125 | 2022-12-27 18:45 | 9.4 | 20.7 | 39 | 36.9 | 1.618 | 0
1126 | 2022-12-27 18:46 | 9.4 | 20.8 | 39 | 36.6 | 1.619 | 0
1127 | 2022-12-27 18:47 | 9.3 | 21 | 38.7 | 36.7 | 1.762 | 0
1128 | 2022-12-27 18:48 | 9.2 | 21.3 | 38.5 | 36.5 | 1.82 | 0
1129 | 2022-12-27 18:49 | 9.1 | 21.6 | 38.4 | 35.9 | 1.821 | 0
1130 | 2022-12-27 18:50 | 9.2 | 21.7 | 38.1 | 35.9 | 1.826 | 0
1131 | 2022-12-27 18:51 | 9.1 | 21.7 | 38 | 35.7 | 1.825 | 0
1132 | 2022-12-27 18:52 | 9.2 | 21.8 | 37.8 | 35.5 | 1.822 | 0
1133 | 2022-12-27 18:53 | 9 | 21.8 | 37.6 | 35.4 | 1.828 | 0
1134 | 2022-12-27 18:54 | 9 | 21.8 | 37.5 | 35.3 | 1.831 | 0
1135 | 2022-12-27 18:55 | 8.9 | 21.8 | 37.3 | 36 | 1.828 | 0
1136 | 2022-12-27 18:56 | 9.1 | 21.4 | 37.2 | 35.9 | 1.823 | 0
1137 | 2022-12-27 18:57 | 8.9 | 21.2 | 37.2 | 35.8 | 1.755 | 0
1138 | 2022-12-27 18:58 | 8.9 | 21 | 37.1 | 35.7 | 1.502 | 0
1139 | 2022-12-27 18:59 | 9 | 20.9 | 37 | 35.4 | 1.497 | 0
1140 | 2022-12-27 19:00 | 9.3 | 20.9 | 36.8 | 35.4 | 1.503 | 0
1141 | 2022-12-27 19:01 | 9.7 | 20.7 | 36.8 | 35.2 | 1.503 | 0
1142 | 2022-12-27 19:02 | 9.7 | 20.7 | 37 | 35.2 | 1.497 | 0
1143 | 2022-12-27 19:03 | 9.6 | 20.7 | 37.6 | 35.5 | 1.498 | 0
1144 | 2022-12-27 19:04 | 9.8 | 20.6 | 38 | 36 | 1.499 | 0
1145 | 2022-12-27 19:05 | 9.7 | 20.6 | 38.2 | 36.4 | 1.504 | 0
1146 | 2022-12-27 19:06 | 10 | 20.5 | 38.7 | 36.5 | 1.505 | 0
1147 | 2022-12-27 19:07 | 9.7 | 20.5 | 38.4 | 36.8 | 1.5 | 0
1148 | 2022-12-27 19:08 | 10 | 20.4 | 38.5 | 36.7 | 1.504 | 0
1149 | 2022-12-27 19:09 | 10.3 | 20.5 | 38.3 | 37.2 | 1.496 | 0
1150 | 2022-12-27 19:10 | 10.1 | 20.4 | 38.3 | 37.1 | 1.502 | 0
1151 | 2022-12-27 19:11 | 9.8 | 20.4 | 38.2 | 37.1 | 1.665 | 0
1152 | 2022-12-27 19:12 | 9.7 | 20.4 | 38.1 | 35.6 | 1.636 | 0
1153 | 2022-12-27 19:13 | 9.7 | 20.4 | 38 | 36 | 1.777 | 0
1154 | 2022-12-27 19:14 | 9.9 | 20.6 | 37.9 | 35.6 | 1.885 | 0
1155 | 2022-12-27 19:15 | 10 | 20.6 | 37.6 | 35 | 1.885 | 0
1156 | 2022-12-27 19:16 | 10.4 | 20.8 | 37.4 | 35 | 1.885 | 0
1157 | 2022-12-27 19:17 | 10 | 21 | 37.2 | 34.8 | 1.875 | 0
1158 | 2022-12-27 19:18 | 10.1 | 21.3 | 37 | 34.6 | 1.89 | 0
1159 | 2022-12-27 19:19 | 10.4 | 21.6 | 36.9 | 34.8 | 1.886 | 0
1160 | 2022-12-27 19:20 | 9.8 | 21.6 | 36.7 | 34.9 | 1.882 | 0
1161 | 2022-12-27 19:21 | 9.7 | 21.9 | 36.6 | 35.5 | 1.891 | 0
1162 | 2022-12-27 19:22 | 9.5 | 22 | 36.9 | 35.5 | 1.885 | 0
1163 | 2022-12-27 19:23 | 9.5 | 21.8 | 37.2 | 36.4 | 1.81 | 0
1164 | 2022-12-27 19:24 | 9.6 | 21.6 | 37.2 | 36.8 | 1.677 | 0
1165 | 2022-12-27 19:25 | 9.8 | 21.3 | 37.2 | 35.6 | 1.486 | 0
1166 | 2022-12-27 19:26 | 10.3 | 21.1 | 37.2 | 36.3 | 1.004 | 0
1167 | 2022-12-27 19:27 | 10.1 | 20.9 | 37.1 | 36 | 0.967 | 0
1168 | 2022-12-27 19:28 | 9.8 | 20.7 | 37 | 35.9 | 0.965 | 0
1169 | 2022-12-27 19:29 | 9.7 | 20.5 | 37 | 35.8 | 0.97 | 0
1170 | 2022-12-27 19:30 | 9.8 | 20.4 | 36.9 | 35.7 | 0.963 | 0
1171 | 2022-12-27 19:31 | 9.8 | 20.4 | 37 | 35.7 | 0.968 | 0
1172 | 2022-12-27 19:32 | 9.7 | 20.3 | 37.2 | 35.7 | 0.965 | 0
1173 | 2022-12-27 19:33 | 9.5 | 20.3 | 37.8 | 35.9 | 0.97 | 0
1174 | 2022-12-27 19:34 | 9.5 | 20.1 | 38.2 | 36.4 | 1.394 | 0
1175 | 2022-12-27 19:35 | 9.6 | 20.1 | 38.6 | 34.5 | 1.5 | 0
1176 | 2022-12-27 19:36 | 9.4 | 20.2 | 39 | 36.7 | 1.5 | 0
1177 | 2022-12-27 19:37 | 9.6 | 20.3 | 38.8 | 37.3 | 1.808 | 0
1178 | 2022-12-27 19:38 | 9.5 | 20.4 | 38.7 | 35 | 1.811 | 0
1179 | 2022-12-27 19:39 | 9.4 | 20.5 | 38.6 | 36.1 | 1.823 | 0
1180 | 2022-12-27 19:40 | 9.5 | 20.7 | 38.3 | 36.1 | 1.82 | 0
1181 | 2022-12-27 19:41 | 9.5 | 20.9 | 38.1 | 35.8 | 1.815 | 0
1182 | 2022-12-27 19:42 | 9.5 | 21.2 | 37.9 | 35.7 | 1.824 | 0
1183 | 2022-12-27 19:43 | 9.6 | 21.4 | 37.8 | 36 | 1.815 | 0
1184 | 2022-12-27 19:44 | 9.6 | 21.6 | 37.7 | 35.9 | 1.82 | 0
1185 | 2022-12-27 19:45 | 9.7 | 21.7 | 37.6 | 35.8 | 1.804 | 0
1186 | 2022-12-27 19:46 | 9.4 | 21.8 | 37.5 | 35.8 | 1.615 | 0
1187 | 2022-12-27 19:47 | 9.4 | 21.9 | 37.4 | 35.5 | 1.617 | 0
1188 | 2022-12-27 19:48 | 9.5 | 21.8 | 37.3 | 35.4 | 1.614 | 0
1189 | 2022-12-27 19:49 | 9.6 | 21.7 | 37.2 | 36.2 | 1.61 | 0
1190 | 2022-12-27 19:50 | 10.2 | 21.4 | 37 | 36.1 | 1.612 | 0
1191 | 2022-12-27 19:51 | 9.9 | 21.2 | 37 | 36 | 1.528 | 0
1192 | 2022-12-27 19:52 | 10 | 21 | 37 | 35.9 | 1.077 | 0
1193 | 2022-12-27 19:53 | 9.8 | 20.9 | 37.2 | 35.7 | 1.085 | 0
1194 | 2022-12-27 19:54 | 10.4 | 20.8 | 37.5 | 35.9 | 1.084 | 0
1195 | 2022-12-27 19:55 | 10.2 | 20.7 | 37.7 | 36.1 | 1.09 | 0
1196 | 2022-12-27 19:56 | 9.9 | 20.6 | 37.4 | 36.2 | 1.087 | 0
1197 | 2022-12-27 19:57 | 9.8 | 20.5 | 37.3 | 36 | 1.083 | 0
1198 | 2022-12-27 19:58 | 9.7 | 20.5 | 37.3 | 35.9 | 1.462 | 0
1199 | 2022-12-27 19:59 | 9.4 | 20.5 | 37.2 | 34 | 1.498 | 0
1200 | 2022-12-27 20:00 | 9.5 | 20.5 | 37.1 | 35.4 | 1.695 | 0
1201 | 2022-12-27 20:01 | 9.4 | 20.4 | 37 | 34.7 | 1.816 | 0
1202 | 2022-12-27 20:02 | 9.3 | 20.4 | 36.9 | 34.5 | 1.828 | 0
1203 | 2022-12-27 20:03 | 9.3 | 20.4 | 37.2 | 34.8 | 1.826 | 0
1204 | 2022-12-27 20:04 | 9.3 | 20.4 | 36.9 | 34.8 | 1.824 | 0
1205 | 2022-12-27 20:05 | 9.3 | 20.5 | 36.9 | 34.7 | 1.824 | 0
1206 | 2022-12-27 20:06 | 9.1 | 20.5 | 36.8 | 34.6 | 1.831 | 0
1207 | 2022-12-27 20:07 | 9 | 20.5 | 36.8 | 34.6 | 1.824 | 0
1208 | 2022-12-27 20:08 | 9.5 | 20.6 | 37.1 | 34.7 | 1.827 | 0
1209 | 2022-12-27 20:09 | 9.6 | 20.9 | 37.6 | 34.9 | 1.978 | 0
1210 | 2022-12-27 20:10 | 9.7 | 20.9 | 38 | 33.6 | 1.993 | 0
1211 | 2022-12-27 20:11 | 9.8 | 21 | 38.2 | 35.5 | 1.991 | 0
1212 | 2022-12-27 20:12 | 9.5 | 21.1 | 38.3 | 35.9 | 1.992 | 0
1213 | 2022-12-27 20:13 | 9.9 | 21.3 | 38.9 | 36.1 | 1.992 | 0
1214 | 2022-12-27 20:14 | 10.3 | 21.6 | 39 | 36.5 | 1.832 | 0
1215 | 2022-12-27 20:15 | 9.5 | 21.6 | 39 | 36.3 | 1.826 | 0
1216 | 2022-12-27 20:16 | 9.3 | 21.8 | 38.9 | 37.2 | 1.822 | 0
1217 | 2022-12-27 20:17 | 9.4 | 21.8 | 38.9 | 37.1 | 1.818 | 0
1218 | 2022-12-27 20:18 | 9.9 | 22 | 38.8 | 37 | 0 | 0
1219 | 2022-12-27 20:19 | 10 | 21.8 | 38.7 | 36.9 | 0 | 0
1220 | 2022-12-27 20:20 | 9.9 | 21.5 | 38.6 | 36.6 | 0 | 0
1221 | 2022-12-27 20:21 | 10.1 | 21.2 | 38.3 | 36.2 | 0 | 0
1222 | 2022-12-27 20:22 | 10.4 | 21 | 38 | 35.7 | 0 | 0
1223 | 2022-12-27 20:23 | 10.5 | 20.8 | 37.8 | 35.2 | 0 | 0
1224 | 2022-12-27 20:24 | 10.5 | 20.6 | 37.6 | 34.8 | 0 | 0
1225 | 2022-12-27 20:25 | 10.2 | 20.5 | 37.3 | 34.4 | 0 | 0
1226 | 2022-12-27 20:26 | 10.3 | 20.4 | 37.1 | 34 | 0 | 0
1227 | 2022-12-27 20:27 | 11.2 | 20.4 | 36.8 | 33.7 | 0 | 0
1228 | 2022-12-27 20:28 | 10.5 | 20.3 | 36.6 | 33.3 | 0.076 | 0
1229 | 2022-12-27 20:29 | 10.6 | 20.2 | 36.4 | 34.7 | 0 | 0
1230 | 2022-12-27 20:30 | 10.5 | 20.2 | 36.2 | 34.7 | 1.031 | 0
1231 | 2022-12-27 20:31 | 11.2 | 20.2 | 38.3 | 32.4 | 1.09 | 0
1232 | 2022-12-27 20:32 | 11 | 20.2 | 37.9 | 36.7 | 1.086 | 0
1233 | 2022-12-27 20:33 | 11.2 | 20.1 | 37.7 | 36.2 | 1.61 | 0
1234 | 2022-12-27 20:34 | 10.9 | 20.3 | 38.1 | 35.3 | 1.811 | 0
1235 | 2022-12-27 20:35 | 10.5 | 20.4 | 38.7 | 35.6 | 1.832 | 0
1236 | 2022-12-27 20:36 | 10.7 | 20.6 | 39 | 36.2 | 1.826 | 0
1237 | 2022-12-27 20:37 | 11.6 | 20.9 | 39.3 | 36.5 | 1.83 | 0
1238 | 2022-12-27 20:38 | 11.7 | 21.2 | 39.7 | 36.8 | 1.827 | 0
1239 | 2022-12-27 20:39 | 11.6 | 21.5 | 39.9 | 37.1 | 1.827 | 0
1240 | 2022-12-27 20:40 | 11.6 | 21.6 | 40.2 | 37.3 | 1.83 | 0
1241 | 2022-12-27 20:41 | 11.1 | 21.8 | 40 | 37.5 | 1.827 | 0
1242 | 2022-12-27 20:42 | 10.9 | 21.8 | 40 | 37.4 | 1.823 | 0
1243 | 2022-12-27 20:43 | 11.2 | 21.9 | 39.8 | 37.3 | 1.829 | 0
1244 | 2022-12-27 20:44 | 11.5 | 21.9 | 39.6 | 37.2 | 1.829 | 0
1245 | 2022-12-27 20:45 | 11.4 | 21.9 | 39.4 | 37.9 | 1.828 | 0
1246 | 2022-12-27 20:46 | 11.5 | 21.6 | 39.3 | 37.8 | 1.828 | 0
1247 | 2022-12-27 20:47 | 11.8 | 21.4 | 39.3 | 37.7 | 1.805 | 0
1248 | 2022-12-27 20:48 | 11.6 | 21.2 | 39.2 | 37.7 | 1.523 | 0
1249 | 2022-12-27 20:49 | 11.3 | 21 | 39.2 | 37.3 | 1.501 | 0
1250 | 2022-12-27 20:50 | 11.6 | 20.9 | 39 | 37.3 | 1.497 | 0
1251 | 2022-12-27 20:51 | 11.9 | 20.8 | 38.9 | 37.3 | 1.502 | 0
1252 | 2022-12-27 20:52 | 11.8 | 20.8 | 38.8 | 37.7 | 1.503 | 0
1253 | 2022-12-27 20:53 | 11.6 | 20.6 | 38.7 | 37.6 | 1.499 | 0
1254 | 2022-12-27 20:54 | 12.2 | 20.7 | 38.7 | 37.6 | 1.375 | 0
1255 | 2022-12-27 20:55 | 12.2 | 20.6 | 38.6 | 37.5 | 1.306 | 0
1256 | 2022-12-27 20:56 | 12.1 | 20.5 | 38.6 | 36.8 | 1.624 | 0
1257 | 2022-12-27 20:57 | 11.8 | 20.5 | 38.5 | 36.1 | 1.626 | 0
1258 | 2022-12-27 20:58 | 11.8 | 20.5 | 38.3 | 36.3 | 1.627 | 0
1259 | 2022-12-27 20:59 | 11.5 | 20.6 | 37.9 | 36.1 | 0 | 0
1260 | 2022-12-27 21:00 | 11.3 | 20.6 | 37.9 | 36.3 | 0 | 0
1261 | 2022-12-27 21:01 | 11 | 20.6 | 37.7 | 36 | 0 | 0
1262 | 2022-12-27 21:02 | 10.9 | 20.5 | 37.5 | 35.5 | 0 | 0
1263 | 2022-12-27 21:03 | 10.6 | 20.5 | 37.3 | 35.1 | 0 | 0
1264 | 2022-12-27 21:04 | 10.3 | 20.5 | 37.1 | 34.7 | 0 | 0
1265 | 2022-12-27 21:05 | 10 | 20.4 | 36.8 | 34.3 | 0 | 0
1266 | 2022-12-27 21:06 | 10 | 20.3 | 36.6 | 34 | 0 | 0
1267 | 2022-12-27 21:07 | 10.4 | 20.2 | 36.4 | 33.6 | 0 | 0
1268 | 2022-12-27 21:08 | 10.3 | 20.2 | 36.2 | 33.3 | 0 | 0
1269 | 2022-12-27 21:09 | 10.1 | 20.1 | 36 | 32.9 | 0 | 0
1270 | 2022-12-27 21:10 | 10 | 20.1 | 35.8 | 32.6 | 0 | 0
1271 | 2022-12-27 21:11 | 10 | 20.1 | 35.6 | 32.3 | 0 | 0
1272 | 2022-12-27 21:12 | 9.9 | 20.1 | 35.3 | 32 | 0 | 0
1273 | 2022-12-27 21:13 | 10.4 | 20.1 | 35.1 | 31.7 | 0 | 0
1274 | 2022-12-27 21:14 | 10.3 | 20 | 34.9 | 31.4 | 0 | 0
1275 | 2022-12-27 21:15 | 10.2 | 20 | 34.7 | 31.1 | 0 | 0
1276 | 2022-12-27 21:16 | 10 | 20 | 34.5 | 30.8 | 0 | 0
1277 | 2022-12-27 21:17 | 10 | 20 | 34.3 | 30.6 | 0 | 0
1278 | 2022-12-27 21:18 | 9.7 | 20 | 34.1 | 30.3 | 0 | 0
1279 | 2022-12-27 21:19 | 9.8 | 20.1 | 33.9 | 30.1 | 0 | 0
1280 | 2022-12-27 21:20 | 9.6 | 20 | 33.7 | 29.8 | 0 | 0
1281 | 2022-12-27 21:21 | 9.6 | 20 | 33.5 | 29.6 | 0 | 0
1282 | 2022-12-27 21:22 | 9.4 | 19.9 | 33.3 | 29.4 | 0 | 0
1283 | 2022-12-27 21:23 | 9.3 | 20 | 33.1 | 29.2 | 0 | 0
1284 | 2022-12-27 21:24 | 9.4 | 20 | 32.9 | 28.9 | 0 | 0
1285 | 2022-12-27 21:25 | 9.2 | 19.9 | 32.7 | 28.7 | 0 | 0
1286 | 2022-12-27 21:26 | 9.1 | 19.9 | 32.5 | 28.5 | 0 | 0
1287 | 2022-12-27 21:27 | 9 | 19.9 | 32.3 | 28.3 | 0 | 0
1288 | 2022-12-27 21:28 | 9 | 19.9 | 32.2 | 28.1 | 0 | 0
1289 | 2022-12-27 21:29 | 9 | 19.9 | 32 | 27.9 | 0 | 0
1290 | 2022-12-27 21:30 | 8.9 | 19.8 | 31.8 | 27.7 | 0 | 0
1291 | 2022-12-27 21:31 | 9 | 19.8 | 31.6 | 27.5 | 0 | 0
1292 | 2022-12-27 21:32 | 8.9 | 19.8 | 31.4 | 27.3 | 0 | 0
1293 | 2022-12-27 21:33 | 8.7 | 19.9 | 31.2 | 27.1 | 0 | 0
1294 | 2022-12-27 21:34 | 8.9 | 19.7 | 31.1 | 26.9 | 0 | 0
1295 | 2022-12-27 21:35 | 8.7 | 19.9 | 30.9 | 26.8 | 0 | 0
1296 | 2022-12-27 21:36 | 9 | 19.8 | 30.7 | 26.6 | 0 | 0
1297 | 2022-12-27 21:37 | 9 | 19.8 | 30.5 | 26.4 | 0 | 0
1298 | 2022-12-27 21:38 | 8.9 | 19.8 | 30.4 | 26.2 | 0 | 0
1299 | 2022-12-27 21:39 | 8.9 | 19.8 | 30.2 | 26.1 | 0 | 0
1300 | 2022-12-27 21:40 | 8.8 | 19.8 | 30 | 25.9 | 0 | 0
1301 | 2022-12-27 21:41 | 8.7 | 19.7 | 29.8 | 25.8 | 0 | 0
1302 | 2022-12-27 21:42 | 8.7 | 19.7 | 29.7 | 25.6 | 0 | 0
1303 | 2022-12-27 21:43 | 8.7 | 19.7 | 29.5 | 25.5 | 0 | 0
1304 | 2022-12-27 21:44 | 8.7 | 19.7 | 29.4 | 25.3 | 0 | 0
1305 | 2022-12-27 21:45 | 8.7 | 19.7 | 29.2 | 25.2 | 0 | 0
1306 | 2022-12-27 21:46 | 8.6 | 19.7 | 29 | 25 | 0 | 0
1307 | 2022-12-27 21:47 | 8.7 | 19.7 | 28.9 | 24.9 | 0 | 0
1308 | 2022-12-27 21:48 | 8.6 | 19.7 | 28.7 | 24.7 | 0 | 0
1309 | 2022-12-27 21:49 | 8.4 | 19.6 | 28.5 | 24.6 | 0 | 0
1310 | 2022-12-27 21:50 | 8.4 | 19.7 | 28.4 | 24.4 | 0 | 0
1311 | 2022-12-27 21:51 | 8.5 | 19.6 | 28.2 | 24.3 | 0 | 0
1312 | 2022-12-27 21:52 | 8.4 | 19.6 | 28.1 | 24.1 | 0 | 0
1313 | 2022-12-27 21:53 | 8.5 | 19.6 | 27.9 | 24 | 0 | 0
1314 | 2022-12-27 21:54 | 8.6 | 19.6 | 27.7 | 23.8 | 0 | 0
1315 | 2022-12-27 21:55 | 8.5 | 19.6 | 27.6 | 23.7 | 0 | 0
1316 | 2022-12-27 21:56 | 8.3 | 19.6 | 27.4 | 23.6 | 0 | 0
1317 | 2022-12-27 21:57 | 8.2 | 19.6 | 27.3 | 23.4 | 0 | 0
1318 | 2022-12-27 21:58 | 8.2 | 19.6 | 27.1 | 23.3 | 0 | 0
1319 | 2022-12-27 21:59 | 8.2 | 19.6 | 27 | 23.2 | 0 | 0
1320 | 2022-12-27 22:00 | 8.2 | 19.6 | 26.8 | 23 | 0 | 0
1321 | 2022-12-27 22:01 | 8.2 | 19.6 | 26.7 | 22.9 | 0 | 0
1322 | 2022-12-27 22:02 | 8.3 | 19.5 | 26.5 | 22.8 | 0 | 0
1323 | 2022-12-27 22:03 | 8.1 | 19.5 | 26.4 | 22.7 | 0 | 0
1324 | 2022-12-27 22:04 | 8.1 | 19.5 | 26.2 | 22.5 | 0 | 0
1325 | 2022-12-27 22:05 | 8.1 | 19.5 | 26.1 | 22.4 | 0 | 0
1326 | 2022-12-27 22:06 | 8.1 | 19.5 | 25.9 | 22.3 | 0 | 0
1327 | 2022-12-27 22:07 | 8.2 | 19.5 | 25.8 | 22.2 | 0 | 0
1328 | 2022-12-27 22:08 | 8.2 | 19.5 | 25.6 | 22.1 | 0 | 0
1329 | 2022-12-27 22:09 | 8 | 19.5 | 25.5 | 22 | 0 | 0
1330 | 2022-12-27 22:10 | 8.2 | 19.5 | 25.3 | 21.9 | 0 | 0
1331 | 2022-12-27 22:11 | 8.1 | 19.6 | 25.2 | 21.8 | 0 | 0
1332 | 2022-12-27 22:12 | 8 | 19.5 | 25.1 | 21.6 | 0 | 0
1333 | 2022-12-27 22:13 | 8 | 19.5 | 24.9 | 21.5 | 0 | 0
1334 | 2022-12-27 22:14 | 7.9 | 19.5 | 24.8 | 21.4 | 0 | 0
1335 | 2022-12-27 22:15 | 8.1 | 19.5 | 24.6 | 21.3 | 0 | 0
1336 | 2022-12-27 22:16 | 8 | 19.5 | 24.5 | 21.2 | 0 | 0
1337 | 2022-12-27 22:17 | 7.9 | 19.5 | 24.4 | 21.1 | 0 | 0
1338 | 2022-12-27 22:18 | 7.8 | 19.4 | 24.2 | 21 | 0 | 0
1339 | 2022-12-27 22:19 | 7.8 | 19.5 | 24.1 | 20.9 | 0 | 0
1340 | 2022-12-27 22:20 | 7.7 | 19.5 | 24 | 20.8 | 0 | 0
1341 | 2022-12-27 22:21 | 7.7 | 19.5 | 23.8 | 20.7 | 0 | 0
1342 | 2022-12-27 22:22 | 7.8 | 19.4 | 23.7 | 20.6 | 0 | 0
1343 | 2022-12-27 22:23 | 7.7 | 19.4 | 23.6 | 20.5 | 0 | 0
1344 | 2022-12-27 22:24 | 7.7 | 19.4 | 23.4 | 20.4 | 0 | 0
1345 | 2022-12-27 22:25 | 7.6 | 19.4 | 23.3 | 20.3 | 0 | 0
1346 | 2022-12-27 22:26 | 7.8 | 19.4 | 23.2 | 20.2 | 0 | 0
1347 | 2022-12-27 22:27 | 7.6 | 19.5 | 23.1 | 20.1 | 0 | 0
1348 | 2022-12-27 22:28 | 7.7 | 19.4 | 23 | 20 | 0 | 0
1349 | 2022-12-27 22:29 | 7.6 | 19.4 | 22.9 | 19.9 | 0 | 0
1350 | 2022-12-27 22:30 | 7.7 | 19.4 | 22.8 | 19.8 | 0 | 0
1351 | 2022-12-27 22:31 | 7.5 | 19.4 | 22.6 | 19.7 | 0 | 0
1352 | 2022-12-27 22:32 | 7.5 | 19.4 | 22.5 | 19.6 | 0 | 0
1353 | 2022-12-27 22:33 | 7.7 | 19.4 | 22.4 | 19.6 | 0 | 0
1354 | 2022-12-27 22:34 | 7.5 | 19.4 | 22.3 | 19.5 | 0 | 0
1355 | 2022-12-27 22:35 | 7.5 | 19.4 | 22.2 | 19.4 | 0 | 0
1356 | 2022-12-27 22:36 | 7.4 | 19.4 | 22.1 | 19.3 | 0 | 0
1357 | 2022-12-27 22:37 | 7.5 | 19.3 | 22 | 19.2 | 0 | 0
1358 | 2022-12-27 22:38 | 7.6 | 19.4 | 21.9 | 19.1 | 0 | 0
1359 | 2022-12-27 22:39 | 7.5 | 19.4 | 21.8 | 19 | 0 | 0
1360 | 2022-12-27 22:40 | 7.6 | 19.3 | 21.7 | 18.9 | 0 | 0
1361 | 2022-12-27 22:41 | 7.5 | 19.3 | 21.6 | 18.9 | 0 | 0
1362 | 2022-12-27 22:42 | 7.4 | 19.3 | 21.5 | 18.8 | 0 | 0
1363 | 2022-12-27 22:43 | 7.4 | 19.3 | 21.4 | 18.7 | 0 | 0
1364 | 2022-12-27 22:44 | 7.4 | 19.4 | 21.3 | 18.6 | 0 | 0
1365 | 2022-12-27 22:45 | 7.5 | 19.4 | 21.2 | 18.5 | 0 | 0
1366 | 2022-12-27 22:46 | 7.5 | 19.4 | 21.1 | 18.5 | 0 | 0
1367 | 2022-12-27 22:47 | 7.3 | 19.3 | 21 | 18.4 | 0 | 0
1368 | 2022-12-27 22:48 | 7.5 | 19.3 | 21 | 18.3 | 0 | 0
1369 | 2022-12-27 22:49 | 7.3 | 19.3 | 20.9 | 18.2 | 0 | 0
1370 | 2022-12-27 22:50 | 7.4 | 19.3 | 20.8 | 18.2 | 0 | 0
1371 | 2022-12-27 22:51 | 7.4 | 19.3 | 20.7 | 18.1 | 0 | 0
1372 | 2022-12-27 22:52 | 7.4 | 19.3 | 20.6 | 18 | 0 | 0
1373 | 2022-12-27 22:53 | 7.4 | 19.3 | 20.5 | 17.9 | 0 | 0
1374 | 2022-12-27 22:54 | 7.4 | 19.2 | 20.4 | 17.9 | 0 | 0
1375 | 2022-12-27 22:55 | 7.3 | 19.3 | 20.4 | 17.8 | 0 | 0
1376 | 2022-12-27 22:56 | 7.5 | 19.3 | 20.3 | 17.7 | 0 | 0
1377 | 2022-12-27 22:57 | 7.6 | 19.3 | 20.2 | 17.7 | 0 | 0
1378 | 2022-12-27 22:58 | 7.4 | 19.3 | 20.1 | 17.6 | 0 | 0
1379 | 2022-12-27 22:59 | 7.3 | 19.3 | 20 | 17.5 | 0 | 0
1380 | 2022-12-27 23:00 | 7.4 | 19.2 | 20 | 17.5 | 0 | 0
1381 | 2022-12-27 23:01 | 7.5 | 19.2 | 19.9 | 17.4 | 0 | 0
1382 | 2022-12-27 23:02 | 7.6 | 19.2 | 19.8 | 17.3 | 0 | 0
1383 | 2022-12-27 23:03 | 7.5 | 19.2 | 19.7 | 17.3 | 0 | 0
1384 | 2022-12-27 23:04 | 7.6 | 19.2 | 19.7 | 17.2 | 0 | 0
1385 | 2022-12-27 23:05 | 7.5 | 19.2 | 19.6 | 17.1 | 0 | 0
1386 | 2022-12-27 23:06 | 7.7 | 19.2 | 19.5 | 17.1 | 0 | 0
1387 | 2022-12-27 23:07 | 7.5 | 19.2 | 19.5 | 17 | 0 | 0
1388 | 2022-12-27 23:08 | 7.6 | 19.2 | 19.4 | 16.9 | 0 | 0
1389 | 2022-12-27 23:09 | 7.6 | 19.2 | 19.3 | 16.9 | 0 | 0
1390 | 2022-12-27 23:10 | 7.6 | 19.2 | 19.3 | 16.8 | 0 | 0
1391 | 2022-12-27 23:11 | 7.7 | 19.3 | 19.2 | 16.8 | 0 | 0
1392 | 2022-12-27 23:12 | 7.9 | 19.2 | 19.1 | 16.7 | 0 | 0
1393 | 2022-12-27 23:13 | 8.1 | 19.2 | 19.1 | 16.7 | 0 | 0
1394 | 2022-12-27 23:14 | 8.2 | 19.1 | 19 | 16.6 | 0 | 0
1395 | 2022-12-27 23:15 | 8.3 | 19.2 | 19 | 16.5 | 0 | 0
1396 | 2022-12-27 23:16 | 8.2 | 19.2 | 18.9 | 16.5 | 0 | 0
1397 | 2022-12-27 23:17 | 8.5 | 19.2 | 18.9 | 16.4 | 0 | 0
1398 | 2022-12-27 23:18 | 9.4 | 19.1 | 18.8 | 16.4 | 0 | 0
1399 | 2022-12-27 23:19 | 8.9 | 19.1 | 18.7 | 16.3 | 0 | 0
1400 | 2022-12-27 23:20 | 10.3 | 19.1 | 18.6 | 16.3 | 0 | 0
1401 | 2022-12-27 23:21 | 10.3 | 19.2 | 18.6 | 16.2 | 0 | 0
1402 | 2022-12-27 23:22 | 10.3 | 19.1 | 18.6 | 16.2 | 0 | 0
1403 | 2022-12-27 23:23 | 10.2 | 19.1 | 18.5 | 16.1 | 0 | 0
1404 | 2022-12-27 23:24 | 10.7 | 19.1 | 18.5 | 16.1 | 0 | 0
1405 | 2022-12-27 23:25 | 10.7 | 19.1 | 18.4 | 16 | 0 | 0
1406 | 2022-12-27 23:26 | 10.6 | 19.1 | 18.4 | 16 | 0 | 0
1407 | 2022-12-27 23:27 | 11.2 | 19.1 | 18.4 | 15.9 | 0 | 0
1408 | 2022-12-27 23:28 | 11 | 19.1 | 18.4 | 15.9 | 0 | 0
1409 | 2022-12-27 23:29 | 10.2 | 19.1 | 18.3 | 15.8 | 0 | 0
1410 | 2022-12-27 23:30 | 10.4 | 19.1 | 18.3 | 15.8 | 0 | 0
1411 | 2022-12-27 23:31 | 11 | 19.1 | 18.3 | 15.8 | 0 | 0
1412 | 2022-12-27 23:32 | 10.3 | 19.1 | 18.3 | 15.7 | 0 | 0
1413 | 2022-12-27 23:33 | 9.9 | 19.2 | 18.2 | 15.7 | 0 | 0
1414 | 2022-12-27 23:34 | 9.4 | 19.1 | 18.2 | 15.6 | 0 | 0
1415 | 2022-12-27 23:35 | 9.6 | 19.2 | 18.2 | 15.6 | 0 | 0
1416 | 2022-12-27 23:36 | 10.2 | 19.1 | 18.2 | 15.6 | 0 | 0
1417 | 2022-12-27 23:37 | 10.4 | 19 | 18.1 | 15.5 | 0 | 0
1418 | 2022-12-27 23:38 | 10.1 | 19 | 18.1 | 15.5 | 0 | 0
1419 | 2022-12-27 23:39 | 10.5 | 19.1 | 18.1 | 15.5 | 0 | 0
1420 | 2022-12-27 23:40 | 10.7 | 19 | 18 | 15.4 | 0 | 0
1421 | 2022-12-27 23:41 | 10.4 | 19.1 | 18 | 15.4 | 0 | 0
1422 | 2022-12-27 23:42 | 10.6 | 19 | 18 | 15.4 | 0 | 0
1423 | 2022-12-27 23:43 | 10.9 | 19 | 17.9 | 15.3 | 0 | 0
1424 | 2022-12-27 23:44 | 10.6 | 19 | 17.9 | 15.3 | 0 | 0
1425 | 2022-12-27 23:45 | 10.4 | 19 | 17.9 | 15.3 | 0 | 0
1426 | 2022-12-27 23:46 | 10.7 | 19.1 | 17.8 | 15.2 | 0 | 0
1427 | 2022-12-27 23:47 | 10.7 | 19.1 | 17.8 | 15.2 | 0 | 0
1428 | 2022-12-27 23:48 | 11 | 19.1 | 17.8 | 15.2 | 0 | 0
1429 | 2022-12-27 23:49 | 11.1 | 19 | 17.8 | 15.1 | 0 | 0
1430 | 2022-12-27 23:50 | 10.7 | 19 | 17.8 | 15.1 | 0 | 0
1431 | 2022-12-27 23:51 | 10.7 | 19 | 17.7 | 15.1 | 0 | 0
1432 | 2022-12-27 23:52 | 10.7 | 19 | 17.7 | 15 | 0 | 0
1433 | 2022-12-27 23:53 | 10.7 | 19 | 17.7 | 15 | 0 | 0
1434 | 2022-12-27 23:54 | 10.4 | 19 | 17.7 | 15 | 0 | 0
1435 | 2022-12-27 23:55 | 10 | 19 | 17.6 | 15 | 0 | 0
1436 | 2022-12-27 23:56 | 9.6 | 19 | 17.6 | 14.9 | 0 | 0
1437 | 2022-12-27 23:57 | 9.4 | 19 | 17.6 | 14.9 | 0 | 0
1438 | 2022-12-27 23:58 | 10.1 | 19 | 17.6 | 14.9 | 0 | 0
1439 | 2022-12-27 23:59 | 9.7 | 19 | 17.6 | 14.8 | 0 | 0